## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2773-27_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2773-27_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2773-27_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2773-27_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_2773-27_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_2773-27_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2773-27_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2773-27_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2773-27_0_4_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_2773-27_0_4_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_2773-27_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_2773-27_0_4_node_50 | 0.4 | n |  | TRUE
12 | bus_LV_2773-27_0_4_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_2773-27_0_4_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_2773-27_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_2773-27_0_4_node_109 | 0.4 | n |  | TRUE
16 | bus_LV_2773-27_0_4_node_107 | 0.4 | n |  | TRUE
17 | bus_LV_2773-27_0_4_node_54 | 0.4 | n |  | TRUE
18 | bus_LV_2773-27_0_4_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_2773-27_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_2773-27_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_2773-27_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_2773-27_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_2773-27_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_2773-27_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_2773-27_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2773-27_0_4_node_111 | 0.4 | n |  | TRUE
27 | bus_LV_2773-27_0_4_node_98 | 0.4 | n |  | TRUE
28 | bus_LV_2773-27_0_4_node_105 | 0.4 | n |  | TRUE
29 | bus_LV_2773-27_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2773-27_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_2773-27_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_2773-27_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2773-27_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_2773-27_0_4_node_120 | 0.4 | n |  | TRUE
35 | bus_LV_2773-27_0_4_node_119 | 0.4 | n |  | TRUE
36 | bus_LV_2773-27_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_2773-27_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_2773-27_0_4_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_2773-27_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_2773-27_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_2773-27_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_2773-27_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_2773-27_0_4_node_223 | 0.4 | n |  | TRUE
44 | bus_LV_2773-27_0_4_node_222 | 0.4 | n |  | TRUE
45 | bus_LV_2773-27_0_4_node_135 | 0.4 | n |  | TRUE
46 | bus_LV_2773-27_0_4_node_131 | 0.4 | n |  | TRUE
47 | bus_LV_2773-27_0_4_node_217 | 0.4 | n |  | TRUE
48 | bus_LV_2773-27_0_4_node_221 | 0.4 | n |  | TRUE
49 | bus_LV_2773-27_0_4_node_129 | 0.4 | n |  | TRUE
50 | bus_LV_2773-27_0_4_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_2773-27_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_2773-27_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_2773-27_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_2773-27_0_4_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_2773-27_0_4_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_2773-27_0_4_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_2773-27_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_2773-27_0_4_node_152 | 0.4 | n |  | TRUE
59 | bus_LV_2773-27_0_4_node_149 | 0.4 | n |  | TRUE
60 | bus_LV_2773-27_0_4_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_2773-27_0_4_node_90 | 0.4 | n |  | TRUE
62 | bus_LV_2773-27_0_4_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_2773-27_0_4_node_151 | 0.4 | n |  | TRUE
64 | bus_LV_2773-27_0_4_node_150 | 0.4 | n |  | TRUE
65 | bus_LV_2773-27_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2773-27_0_4_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_2773-27_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_2773-27_0_4_node_51 | 0.4 | n |  | TRUE
69 | bus_LV_2773-27_0_4_node_52 | 0.4 | n |  | TRUE
70 | bus_LV_2773-27_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_2773-27_0_4_node_58 | 0.4 | n |  | TRUE
72 | bus_LV_2773-27_0_4_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_2773-27_0_4_node_224 | 0.4 | n |  | TRUE
74 | bus_LV_2773-27_0_4_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_2773-27_0_4_node_59 | 0.4 | n |  | TRUE
76 | bus_LV_2773-27_0_4_node_56 | 0.4 | n |  | TRUE
77 | bus_LV_2773-27_0_4_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_2773-27_0_4_node_225 | 0.4 | n |  | TRUE
79 | bus_LV_2773-27_0_4_node_226 | 0.4 | n |  | TRUE
80 | bus_LV_2773-27_0_4_node_62 | 0.4 | n |  | TRUE
81 | bus_LV_2773-27_0_4_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_2773-27_0_4_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_2773-27_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_2773-27_0_4_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_2773-27_0_4_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_2773-27_0_4_node_66 | 0.4 | n |  | TRUE
87 | bus_LV_2773-27_0_4_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_2773-27_0_4_node_115 | 0.4 | n |  | TRUE
89 | bus_LV_2773-27_0_4_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2773-27_0_4_node_112 | 0.4 | n |  | TRUE
91 | bus_LV_2773-27_0_4_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_2773-27_0_4_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_2773-27_0_4_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_2773-27_0_4_node_116 | 0.4 | n |  | TRUE
95 | bus_LV_2773-27_0_4_node_117 | 0.4 | n |  | TRUE
96 | bus_LV_2773-27_0_4_node_72 | 0.4 | n |  | TRUE
97 | bus_LV_2773-27_0_4_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_2773-27_0_4_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_2773-27_0_4_node_71 | 0.4 | n |  | TRUE
100 | bus_LV_2773-27_0_4_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_2773-27_0_4_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_2773-27_0_4_node_81 | 0.4 | n |  | TRUE
103 | bus_LV_2773-27_0_4_node_99 | 0.4 | n |  | TRUE
104 | bus_LV_2773-27_0_4_node_100 | 0.4 | n |  | TRUE
105 | bus_LV_2773-27_0_4_node_87 | 0.4 | n |  | TRUE
106 | bus_LV_2773-27_0_4_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_2773-27_0_4_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_2773-27_0_4_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_2773-27_0_4_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_2773-27_0_4_node_191 | 0.4 | n |  | TRUE
111 | bus_LV_2773-27_0_4_node_194 | 0.4 | n |  | TRUE
112 | bus_LV_2773-27_0_4_node_197 | 0.4 | n |  | TRUE
113 | bus_LV_2773-27_0_4_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_2773-27_0_4_node_195 | 0.4 | n |  | TRUE
115 | bus_LV_2773-27_0_4_node_198 | 0.4 | n |  | TRUE
116 | bus_LV_2773-27_0_4_node_192 | 0.4 | n |  | TRUE
117 | bus_LV_2773-27_0_4_node_193 | 0.4 | n |  | TRUE
118 | bus_LV_2773-27_0_4_node_103 | 0.4 | n |  | TRUE
119 | bus_LV_2773-27_0_4_node_106 | 0.4 | n |  | TRUE
120 | bus_LV_2773-27_0_4_node_108 | 0.4 | n |  | TRUE
121 | bus_LV_2773-27_0_4_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_2773-27_0_4_node_101 | 0.4 | n |  | TRUE
123 | bus_LV_2773-27_0_4_node_110 | 0.4 | n |  | TRUE
124 | bus_LV_2773-27_0_4_node_114 | 0.4 | n |  | TRUE
125 | bus_LV_2773-27_0_4_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_2773-27_0_4_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_2773-27_0_4_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_2773-27_0_4_node_188 | 0.4 | n |  | TRUE
129 | bus_LV_2773-27_0_4_node_130 | 0.4 | n |  | TRUE
130 | bus_LV_2773-27_0_4_node_132 | 0.4 | n |  | TRUE
131 | bus_LV_2773-27_0_4_node_133 | 0.4 | n |  | TRUE
132 | bus_LV_2773-27_0_4_node_134 | 0.4 | n |  | TRUE
133 | bus_LV_2773-27_0_4_node_139 | 0.4 | n |  | TRUE
134 | bus_LV_2773-27_0_4_node_140 | 0.4 | n |  | TRUE
135 | bus_LV_2773-27_0_4_node_136 | 0.4 | n |  | TRUE
136 | bus_LV_2773-27_0_4_node_153 | 0.4 | n |  | TRUE
137 | bus_LV_2773-27_0_4_node_137 | 0.4 | n |  | TRUE
138 | bus_LV_2773-27_0_4_node_220 | 0.4 | n |  | TRUE
139 | bus_LV_2773-27_0_4_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_2773-27_0_4_node_141 | 0.4 | n |  | TRUE
141 | bus_LV_2773-27_0_4_node_142 | 0.4 | n |  | TRUE
142 | bus_LV_2773-27_0_4_node_199 | 0.4 | n |  | TRUE
143 | bus_LV_2773-27_0_4_node_143 | 0.4 | n |  | TRUE
144 | bus_LV_2773-27_0_4_node_144 | 0.4 | n |  | TRUE
145 | bus_LV_2773-27_0_4_node_145 | 0.4 | n |  | TRUE
146 | bus_LV_2773-27_0_4_node_146 | 0.4 | n |  | TRUE
147 | bus_LV_2773-27_0_4_node_147 | 0.4 | n |  | TRUE
148 | bus_LV_2773-27_0_4_node_148 | 0.4 | n |  | TRUE
149 | bus_LV_2773-27_0_4_node_200 | 0.4 | n |  | TRUE
150 | bus_LV_2773-27_0_4_node_196 | 0.4 | n |  | TRUE
151 | bus_LV_2773-27_0_4_node_218 | 0.4 | n |  | TRUE
152 | bus_LV_2773-27_0_4_node_215 | 0.4 | n |  | TRUE
153 | bus_LV_2773-27_0_4_node_211 | 0.4 | n |  | TRUE
154 | bus_LV_2773-27_0_4_node_210 | 0.4 | n |  | TRUE
155 | bus_LV_2773-27_0_4_node_201 | 0.4 | n |  | TRUE
156 | bus_LV_2773-27_0_4_node_202 | 0.4 | n |  | TRUE
157 | bus_LV_2773-27_0_4_node_203 | 0.4 | n |  | TRUE
158 | bus_LV_2773-27_0_4_node_204 | 0.4 | n |  | TRUE
159 | bus_LV_2773-27_0_4_node_205 | 0.4 | n |  | TRUE
160 | bus_LV_2773-27_0_4_node_212 | 0.4 | n |  | TRUE
161 | bus_LV_2773-27_0_4_node_206 | 0.4 | n |  | TRUE
162 | bus_LV_2773-27_0_4_node_213 | 0.4 | n |  | TRUE
163 | bus_LV_2773-27_0_4_node_207 | 0.4 | n |  | TRUE
164 | bus_LV_2773-27_0_4_node_208 | 0.4 | n |  | TRUE
165 | bus_LV_2773-27_0_4_node_209 | 0.4 | n |  | TRUE
166 | bus_LV_2773-27_0_4_node_214 | 0.4 | n |  | TRUE
167 | bus_LV_2773-27_0_4_node_216 | 0.4 | n |  | TRUE
168 | bus_LV_2773-27_0_4_node_219 | 0.4 | n |  | TRUE
169 | bus_LV_2773-27_0_4_node_228 | 0.4 | n |  | TRUE
170 | bus_LV_2773-27_0_4_node_227 | 0.4 | n |  | TRUE
171 | bus_LV_2773-27_0_4_node_230 | 0.4 | n |  | TRUE
172 | bus_LV_2773-27_0_4_node_229 | 0.4 | n |  | TRUE
173 | bus_LV_2773-27_0_4_node_231 | 0.4 | n |  | TRUE
174 | bus_MV_573_0_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2773-27_0_4_load_0 | 0 | 0.013691 | 0.0034312 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2773-27_0_4_load_1 | 1 | 0.0068637 | 0.0017202 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2773-27_0_4_load_4 | 3 | 0.011798 | 0.0029568 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2773-27_0_4_load_6 | 6 | 0.0014145 | 0.0003545 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2773-27_0_4_load_13 | 8 | 0.0011697 | 0.00029316 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2773-27_0_4_load_10 | 9 | 0.0023039 | 0.00057742 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2773-27_0_4_load_50 | 11 | 0.001876 | 0.00047016 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2773-27_0_4_load_46 | 12 | 0.0021332 | 0.00053463 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2773-27_0_4_load_8 | 14 | 0.0011708 | 0.00029344 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2773-27_0_4_load_107 | 16 | 0.0014984 | 0.00037554 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2773-27_0_4_load_54 | 17 | 0.0011646 | 0.00029188 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2773-27_0_4_load_45 | 18 | 0.018231 | 0.0045692 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2773-27_0_4_load_9 | 19 | 0.0011697 | 0.00029316 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2773-27_0_4_load_11 | 20 | 0.0011704 | 0.00029333 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2773-27_0_4_load_12 | 21 | 0.0011697 | 0.00029316 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2773-27_0_4_load_14 | 22 | 0.0011697 | 0.00029316 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2773-27_0_4_load_15 | 23 | 0.002342 | 0.00058696 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2773-27_0_4_load_24 | 24 | 0.0085272 | 0.0021371 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2773-27_0_4_load_21 | 25 | 0.0011697 | 0.00029316 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2773-27_0_4_load_111 | 26 | 0.0054226 | 0.001359 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2773-27_0_4_load_105 | 28 | 0.0018308 | 0.00045883 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2773-27_0_4_load_19 | 29 | 0.0011716 | 0.00029363 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2773-27_0_4_load_18 | 30 | 0.0011693 | 0.00029305 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2773-27_0_4_load_20 | 31 | 0.0017788 | 0.00044581 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2773-27_0_4_load_22 | 32 | 0.0067164 | 0.0016833 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2773-27_0_4_load_23 | 33 | 0.0013539 | 0.00033933 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2773-27_0_4_load_120 | 34 | 0.001935 | 0.00048495 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2773-27_0_4_load_119 | 35 | 0.0017361 | 0.00043511 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2773-27_0_4_load_26 | 36 | 0.0021671 | 0.00054312 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2773-27_0_4_load_30 | 38 | 0.0012817 | 0.00032123 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2773-27_0_4_load_31 | 40 | 0.0014029 | 0.00035161 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2773-27_0_4_load_32 | 41 | 0.0014026 | 0.00035152 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2773-27_0_4_load_223 | 43 | 0.0014029 | 0.00035161 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2773-27_0_4_load_222 | 44 | 0.0012696 | 0.00031819 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2773-27_0_4_load_135 | 45 | 0.0012805 | 0.00032093 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2773-27_0_4_load_217 | 47 | 0.0014025 | 0.00035151 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2773-27_0_4_load_221 | 48 | 0.0014675 | 0.0003678 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2773-27_0_4_load_129 | 49 | 0.0064261 | 0.0016105 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2773-27_0_4_load_34 | 50 | 0.012857 | 0.0032222 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2773-27_0_4_load_37 | 52 | 0.0056562 | 0.0014176 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2773-27_0_4_load_38 | 53 | 0.0058308 | 0.0014613 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2773-27_0_4_load_39 | 54 | 0.0013937 | 0.00034929 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2773-27_0_4_load_43 | 55 | 0.0013953 | 0.00034969 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2773-27_0_4_load_40 | 56 | 0.0011658 | 0.00029217 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2773-27_0_4_load_152 | 58 | 0.001177 | 0.00029499 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2773-27_0_4_load_149 | 59 | 0.0015442 | 0.00038701 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2773-27_0_4_load_90 | 61 | 0.0017896 | 0.00044852 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2773-27_0_4_load_86 | 62 | 0.0019464 | 0.00048782 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2773-27_0_4_load_151 | 63 | 0.001177 | 0.00029499 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2773-27_0_4_load_150 | 64 | 0.0011656 | 0.00029213 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2773-27_0_4_load_49 | 67 | 0.0025998 | 0.00065157 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2773-27_0_4_load_51 | 68 | 0.0029435 | 0.00073771 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2773-27_0_4_load_52 | 69 | 0.0029465 | 0.00073847 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2773-27_0_4_load_58 | 71 | 0.0018535 | 0.00046454 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2773-27_0_4_load_57 | 72 | 0.011638 | 0.0029167 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2773-27_0_4_load_224 | 73 | 0.0039663 | 0.00099404 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2773-27_0_4_load_55 | 74 | 0.0011637 | 0.00029166 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2773-27_0_4_load_59 | 75 | 0.0011539 | 0.00028919 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2773-27_0_4_load_56 | 76 | 0.001578 | 0.00039549 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2773-27_0_4_load_226 | 79 | 0.0011536 | 0.00028911 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2773-27_0_4_load_62 | 80 | 0.0024315 | 0.0006094 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2773-27_0_4_load_63 | 81 | 0.0027201 | 0.00068172 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2773-27_0_4_load_65 | 83 | 0.00258 | 0.00064661 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2773-27_0_4_load_69 | 85 | 0.0014196 | 0.00035579 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2773-27_0_4_load_66 | 86 | 0.0042608 | 0.0010679 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2773-27_0_4_load_70 | 87 | 0.0018865 | 0.0004728 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2773-27_0_4_load_112 | 90 | 0.0038798 | 0.00097237 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2773-27_0_4_load_74 | 91 | 0.0024047 | 0.00060268 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2773-27_0_4_load_79 | 92 | 0.00094832 | 0.00023767 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2773-27_0_4_load_96 | 93 | 0.0027442 | 0.00068776 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2773-27_0_4_load_116 | 94 | 0.0093571 | 0.0023451 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2773-27_0_4_load_117 | 95 | 0.01217 | 0.0030502 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2773-27_0_4_load_72 | 96 | 0.00070274 | 0.00017612 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2773-27_0_4_load_97 | 98 | 0.0023399 | 0.00058645 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2773-27_0_4_load_71 | 99 | 0.0024045 | 0.00060263 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2773-27_0_4_load_75 | 100 | 0.0014143 | 0.00035445 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2773-27_0_4_load_80 | 101 | 0.0053955 | 0.0013522 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2773-27_0_4_load_81 | 102 | 0.0056191 | 0.0014083 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2773-27_0_4_load_99 | 103 | 0.0018661 | 0.00046768 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2773-27_0_4_load_100 | 104 | 0.018785 | 0.0047081 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2773-27_0_4_load_87 | 105 | 0.0019469 | 0.00048793 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2773-27_0_4_load_91 | 107 | 0.0014026 | 0.00035152 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2773-27_0_4_load_92 | 108 | 0.0013345 | 0.00033445 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2773-27_0_4_load_95 | 109 | 0.0014679 | 0.00036789 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2773-27_0_4_load_191 | 110 | 0.0014045 | 0.000352 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2773-27_0_4_load_194 | 111 | 0.0014029 | 0.00035161 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2773-27_0_4_load_197 | 112 | 0.0014669 | 0.00036763 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2773-27_0_4_load_102 | 113 | 0.0072363 | 0.0018136 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2773-27_0_4_load_195 | 114 | 0.0014029 | 0.00035161 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2773-27_0_4_load_198 | 115 | 0.0014669 | 0.00036763 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2773-27_0_4_load_193 | 117 | 0.0014031 | 0.00035165 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2773-27_0_4_load_103 | 118 | 0.001402 | 0.00035138 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2773-27_0_4_load_108 | 120 | 0.0097236 | 0.002437 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2773-27_0_4_load_104 | 121 | 0.0019972 | 0.00050056 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2773-27_0_4_load_110 | 123 | 0.0018453 | 0.00046248 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2773-27_0_4_load_114 | 124 | 0.003058 | 0.00076641 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2773-27_0_4_load_113 | 125 | 0.003441 | 0.00086239 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2773-27_0_4_load_121 | 126 | 0.0013782 | 0.0003454 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2773-27_0_4_load_118 | 127 | 0.0018382 | 0.0004607 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2773-27_0_4_load_188 | 128 | 0.0039898 | 0.00099994 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2773-27_0_4_load_130 | 129 | 0.0014262 | 0.00035744 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2773-27_0_4_load_134 | 132 | 0.0011652 | 0.00029202 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2773-27_0_4_load_139 | 133 | 0.0016177 | 0.00040545 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2773-27_0_4_load_140 | 134 | 0.001177 | 0.00029499 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2773-27_0_4_load_136 | 135 | 0.0011781 | 0.00029525 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2773-27_0_4_load_153 | 136 | 0.0013956 | 0.00034976 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2773-27_0_4_load_137 | 137 | 0.001166 | 0.00029223 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2773-27_0_4_load_220 | 138 | 0.0012723 | 0.00031887 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2773-27_0_4_load_138 | 139 | 0.0011661 | 0.00029225 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2773-27_0_4_load_141 | 140 | 0.0011641 | 0.00029176 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2773-27_0_4_load_142 | 141 | 0.0011643 | 0.00029179 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2773-27_0_4_load_199 | 142 | 0.0013953 | 0.00034969 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2773-27_0_4_load_144 | 144 | 0.0015445 | 0.00038709 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2773-27_0_4_load_145 | 145 | 0.0023308 | 0.00058416 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2773-27_0_4_load_146 | 146 | 0.0017143 | 0.00042966 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2773-27_0_4_load_147 | 147 | 0.0011656 | 0.00029213 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2773-27_0_4_load_148 | 148 | 0.0015454 | 0.00038732 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2773-27_0_4_load_196 | 150 | 0.0016188 | 0.00040571 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2773-27_0_4_load_218 | 151 | 0.0016192 | 0.00040581 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2773-27_0_4_load_211 | 153 | 0.0014689 | 0.00036814 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2773-27_0_4_load_210 | 154 | 0.0014673 | 0.00036775 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2773-27_0_4_load_201 | 155 | 0.0014689 | 0.00036814 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2773-27_0_4_load_202 | 156 | 0.0016188 | 0.00040571 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2773-27_0_4_load_203 | 157 | 0.0014669 | 0.00036763 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2773-27_0_4_load_204 | 158 | 0.0016184 | 0.0004056 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2773-27_0_4_load_205 | 159 | 0.0014682 | 0.00036797 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2773-27_0_4_load_212 | 160 | 0.0016206 | 0.00040616 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2773-27_0_4_load_206 | 161 | 0.0014669 | 0.00036763 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2773-27_0_4_load_213 | 162 | 0.0016188 | 0.00040571 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2773-27_0_4_load_207 | 163 | 0.001467 | 0.00036766 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2773-27_0_4_load_208 | 164 | 0.0014687 | 0.00036809 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2773-27_0_4_load_209 | 165 | 0.0014668 | 0.00036762 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2773-27_0_4_load_216 | 167 | 0.0012725 | 0.00031891 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2773-27_0_4_load_219 | 168 | 0.0016177 | 0.00040545 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2773-27_0_4_load_228 | 169 | 0.0011536 | 0.00028911 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2773-27_0_4_load_230 | 171 | 0.0018514 | 0.000464 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2773-27_0_4_load_229 | 172 | 0.0011522 | 0.00028877 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2773-27_0_4_load_231 | 173 | 0.0018517 | 0.00046409 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 27 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2773-27_0_4_line_0 |  | 0 | 1 | 0.0034861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2773-27_0_4_line_1 |  | 0 | 2 | 0.039794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2773-27_0_4_line_2 |  | 2 | 3 | 0.033175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2773-27_0_4_line_3 |  | 3 | 7 | 0.0041209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2773-27_0_4_line_4 |  | 4 | 5 | 0.004829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2773-27_0_4_line_5 |  | 4 | 6 | 0.02795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2773-27_0_4_line_6 |  | 5 | 8 | 0.034125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2773-27_0_4_line_7 |  | 5 | 9 | 0.010129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2773-27_0_4_line_8 |  | 6 | 10 | 0.014931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_2773-27_0_4_line_9 |  | 7 | 11 | 0.014064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2773-27_0_4_line_10 |  | 7 | 12 | 0.024597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2773-27_0_4_line_11 |  | 8 | 13 | 0.011587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2773-27_0_4_line_12 |  | 9 | 14 | 4.8522e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2773-27_0_4_line_13 |  | 10 | 15 | 0.009319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2773-27_0_4_line_14 |  | 10 | 16 | 0.022105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2773-27_0_4_line_15 |  | 11 | 17 | 0.0061039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2773-27_0_4_line_16 |  | 12 | 18 | 0.024254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2773-27_0_4_line_17 |  | 13 | 24 | 0.036646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2773-27_0_4_line_18 |  | 13 | 25 | 0.016044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2773-27_0_4_line_19 |  | 14 | 19 | 0.0067215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2773-27_0_4_line_20 |  | 15 | 26 | 0.024001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2773-27_0_4_line_21 |  | 15 | 27 | 0.024349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_2773-27_0_4_line_22 |  | 16 | 28 | 0.007755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2773-27_0_4_line_23 |  | 17 | 74 | 0.0060991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2773-27_0_4_line_24 |  | 18 | 65 | 0.014392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2773-27_0_4_line_25 |  | 19 | 20 | 4.2885e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2773-27_0_4_line_26 |  | 20 | 21 | 0.0067217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2773-27_0_4_line_27 |  | 21 | 22 | 4.3777e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2773-27_0_4_line_28 |  | 22 | 23 | 0.0064367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2773-27_0_4_line_29 |  | 25 | 29 | 0.0067699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2773-27_0_4_line_30 |  | 26 | 73 | 0.015724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2773-27_0_4_line_31 |  | 27 | 116 | 0.009945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2773-27_0_4_line_32 |  | 27 | 98 | 0.021183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2773-27_0_4_line_33 |  | 28 | 121 | 0.01466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2773-27_0_4_line_34 |  | 29 | 30 | 0.0067697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2773-27_0_4_line_35 |  | 30 | 31 | 0.013906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2773-27_0_4_line_36 |  | 31 | 32 | 0.0065116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2773-27_0_4_line_37 |  | 32 | 33 | 0.018303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2773-27_0_4_line_38 |  | 33 | 34 | 0.0085348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2773-27_0_4_line_39 |  | 34 | 35 | 0.010342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2773-27_0_4_line_40 |  | 35 | 127 | 0.001211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2773-27_0_4_line_41 |  | 36 | 37 | 0.051171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2773-27_0_4_line_42 |  | 37 | 38 | 0.019658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2773-27_0_4_line_43 |  | 38 | 42 | 0.0084363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2773-27_0_4_line_44 |  | 39 | 40 | 0.014782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2773-27_0_4_line_45 |  | 39 | 41 | 0.019459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2773-27_0_4_line_46 |  | 40 | 43 | 0.00071067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2773-27_0_4_line_47 |  | 41 | 44 | 0.0036694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2773-27_0_4_line_48 |  | 42 | 45 | 0.013224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2773-27_0_4_line_49 |  | 42 | 46 | 0.002271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2773-27_0_4_line_50 |  | 44 | 47 | 0.0016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2773-27_0_4_line_51 |  | 45 | 48 | 0.0053475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2773-27_0_4_line_52 |  | 46 | 49 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2773-27_0_4_line_53 |  | 47 | 152 | 0.01717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2773-27_0_4_line_54 |  | 48 | 138 | 0.0053531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2773-27_0_4_line_55 |  | 49 | 129 | 0.030988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2773-27_0_4_line_56 |  | 50 | 51 | 0.02784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2773-27_0_4_line_57 |  | 51 | 52 | 0.0411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2773-27_0_4_line_58 |  | 51 | 53 | 0.021878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2773-27_0_4_line_59 |  | 51 | 54 | 0.017665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2773-27_0_4_line_60 |  | 54 | 55 | 0.00068131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2773-27_0_4_line_61 |  | 55 | 58 | 0.0038266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2773-27_0_4_line_62 |  | 56 | 57 | 0.01476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2773-27_0_4_line_63 |  | 57 | 59 | 0.017388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2773-27_0_4_line_64 |  | 58 | 63 | 0.0059004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2773-27_0_4_line_65 |  | 59 | 64 | 0.0017613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2773-27_0_4_line_66 |  | 60 | 61 | 0.01234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2773-27_0_4_line_67 |  | 60 | 62 | 0.0076089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2773-27_0_4_line_68 |  | 61 | 109 | 0.00567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2773-27_0_4_line_69 |  | 62 | 105 | 0.01449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2773-27_0_4_line_70 |  | 63 | 134 | 0.0058999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2773-27_0_4_line_71 |  | 64 | 147 | 0.0058962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2773-27_0_4_line_72 |  | 65 | 66 | 0.048918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2773-27_0_4_line_73 |  | 65 | 67 | 0.028802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2773-27_0_4_line_74 |  | 66 | 68 | 0.013549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2773-27_0_4_line_75 |  | 66 | 69 | 0.0093751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2773-27_0_4_line_76 |  | 67 | 70 | 0.0092633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2773-27_0_4_line_77 |  | 68 | 71 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2773-27_0_4_line_78 |  | 69 | 72 | 0.022075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2773-27_0_4_line_79 |  | 70 | 73 | 0.019326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2773-27_0_4_line_80 |  | 71 | 75 | 0.0052397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2773-27_0_4_line_81 |  | 74 | 76 | 0.0072759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2773-27_0_4_line_82 |  | 75 | 77 | 0.028058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2773-27_0_4_line_83 |  | 77 | 78 | 0.021612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2773-27_0_4_line_84 |  | 78 | 79 | 0.01316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2773-27_0_4_line_85 |  | 79 | 169 | 6.2503e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2773-27_0_4_line_86 |  | 80 | 81 | 0.019829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2773-27_0_4_line_87 |  | 80 | 82 | 0.010146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2773-27_0_4_line_88 |  | 81 | 83 | 0.0067171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2773-27_0_4_line_89 |  | 82 | 84 | 0.018614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2773-27_0_4_line_90 |  | 83 | 85 | 0.012157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2773-27_0_4_line_91 |  | 84 | 88 | 0.033467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2773-27_0_4_line_92 |  | 84 | 89 | 0.05323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2773-27_0_4_line_93 |  | 84 | 90 | 0.018769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2773-27_0_4_line_94 |  | 85 | 92 | 0.01525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2773-27_0_4_line_95 |  | 86 | 87 | 0.045947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2773-27_0_4_line_96 |  | 87 | 93 | 0.01824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2773-27_0_4_line_97 |  | 88 | 94 | 0.03754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2773-27_0_4_line_98 |  | 88 | 95 | 0.026234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2773-27_0_4_line_99 |  | 89 | 91 | 0.054955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2773-27_0_4_line_100 |  | 91 | 96 | 0.022553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2773-27_0_4_line_101 |  | 92 | 97 | 0.011264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2773-27_0_4_line_102 |  | 93 | 98 | 0.013041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2773-27_0_4_line_103 |  | 94 | 126 | 0.017296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2773-27_0_4_line_104 |  | 95 | 127 | 0.018542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2773-27_0_4_line_105 |  | 96 | 99 | 0.0077278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2773-27_0_4_line_106 |  | 97 | 101 | 0.024835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2773-27_0_4_line_107 |  | 97 | 100 | 0.016598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2773-27_0_4_line_108 |  | 101 | 102 | 0.012661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2773-27_0_4_line_109 |  | 102 | 103 | 0.015563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2773-27_0_4_line_110 |  | 103 | 104 | 0.021138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2773-27_0_4_line_111 |  | 105 | 106 | 0.0058131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2773-27_0_4_line_112 |  | 106 | 107 | 0.017095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2773-27_0_4_line_113 |  | 106 | 108 | 0.013922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2773-27_0_4_line_114 |  | 107 | 110 | 0.003054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2773-27_0_4_line_115 |  | 108 | 111 | 0.0019907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2773-27_0_4_line_116 |  | 109 | 112 | 0.0019933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2773-27_0_4_line_117 |  | 110 | 113 | 0.0059188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2773-27_0_4_line_118 |  | 111 | 114 | 5.0346e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2773-27_0_4_line_119 |  | 112 | 115 | 0.0033577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2773-27_0_4_line_120 |  | 113 | 122 | 0.0033556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2773-27_0_4_line_121 |  | 115 | 153 | 0.0019927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2773-27_0_4_line_122 |  | 116 | 117 | 0.016276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2773-27_0_4_line_123 |  | 116 | 118 | 0.014303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2773-27_0_4_line_124 |  | 118 | 122 | 0.0090159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2773-27_0_4_line_125 |  | 119 | 120 | 0.023931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2773-27_0_4_line_126 |  | 119 | 121 | 0.0058241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2773-27_0_4_line_127 |  | 120 | 123 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2773-27_0_4_line_128 |  | 123 | 124 | 0.0058273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2773-27_0_4_line_129 |  | 124 | 125 | 0.0062895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2773-27_0_4_line_130 |  | 126 | 128 | 0.015775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2773-27_0_4_line_131 |  | 130 | 131 | 0.01216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2773-27_0_4_line_132 |  | 130 | 132 | 0.010851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2773-27_0_4_line_133 |  | 131 | 133 | 0.017578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2773-27_0_4_line_134 |  | 131 | 134 | 0.0027242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2773-27_0_4_line_135 |  | 132 | 135 | 0.0016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_2773-27_0_4_line_136 |  | 133 | 136 | 0.0045301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2773-27_0_4_line_137 |  | 135 | 137 | 0.0042284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_2773-27_0_4_line_138 |  | 136 | 142 | 0.0051664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_2773-27_0_4_line_139 |  | 137 | 139 | 0.0058943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_2773-27_0_4_line_140 |  | 138 | 168 | 0.00035313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_2773-27_0_4_line_141 |  | 139 | 140 | 0.0058973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2773-27_0_4_line_142 |  | 140 | 141 | 0.0058881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2773-27_0_4_line_143 |  | 141 | 143 | 0.010471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2773-27_0_4_line_144 |  | 142 | 149 | 0.00078048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2773-27_0_4_line_145 |  | 143 | 144 | 0.005345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_2773-27_0_4_line_146 |  | 143 | 145 | 0.0077269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2773-27_0_4_line_147 |  | 144 | 146 | 0.0067985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2773-27_0_4_line_148 |  | 145 | 147 | 0.0010507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_2773-27_0_4_line_149 |  | 146 | 148 | 0.0023285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_2773-27_0_4_line_150 |  | 149 | 155 | 0.0064486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2773-27_0_4_line_151 |  | 149 | 156 | 0.012891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2773-27_0_4_line_152 |  | 150 | 151 | 7.3922e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2773-27_0_4_line_153 |  | 151 | 152 | 0.015633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2773-27_0_4_line_154 |  | 152 | 166 | 0.006507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2773-27_0_4_line_155 |  | 153 | 154 | 0.0033544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_2773-27_0_4_line_156 |  | 154 | 165 | 0.001996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2773-27_0_4_line_157 |  | 155 | 157 | 0.016689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_2773-27_0_4_line_158 |  | 156 | 158 | 0.0052901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2773-27_0_4_line_159 |  | 157 | 159 | 0.0033548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2773-27_0_4_line_160 |  | 158 | 160 | 0.0052929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2773-27_0_4_line_161 |  | 159 | 161 | 0.0019933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2773-27_0_4_line_162 |  | 160 | 162 | 0.0052936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2773-27_0_4_line_163 |  | 161 | 163 | 0.003358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2773-27_0_4_line_164 |  | 162 | 166 | 0.0039336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2773-27_0_4_line_165 |  | 163 | 164 | 0.0019921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2773-27_0_4_line_166 |  | 164 | 165 | 0.0033567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2773-27_0_4_line_167 |  | 166 | 167 | 0.012354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2773-27_0_4_line_168 |  | 167 | 168 | 0.004999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_2773-27_0_4_line_169 |  | 169 | 172 | 0.026123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2773-27_0_4_line_170 |  | 170 | 171 | 0.018339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_2773-27_0_4_line_171 |  | 170 | 172 | 0.013162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2773-27_0_4_line_172 |  | 171 | 173 | 0.0060604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2773-27_0_4_trafo_98 | 0.63 MVA 20/0.4 kV | 174 | 27 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2611364.9197 | 1259745.5612 | 2611365.5713 | 1259748.9859
1 | 2611357.4816 | 1259706.4686 | 2611364.9197 | 1259745.5612
2 | 2611357.4816 | 1259706.4686 | 2611389.8014 | 1259698.9843
3 | 2611393.816 | 1259698.0546 | 2611389.8014 | 1259698.9843
4 | 2611368.5353 | 1259790.4688 | 2611373.2776 | 1259789.4883
5 | 2611373.2776 | 1259789.4883 | 2611400.7324 | 1259784.2515
6 | 2611368.5353 | 1259790.4688 | 2611335.1257 | 1259797.4188
7 | 2611368.5353 | 1259790.4688 | 2611370.4358 | 1259800.4177
8 | 2611415.4954 | 1259782.1197 | 2611407.9048 | 1259782.8834 | 2611400.7324 | 1259784.2515
9 | 2611393.816 | 1259698.0546 | 2611390.7767 | 1259684.3232
10 | 2611393.816 | 1259698.0546 | 2611417.7153 | 1259692.2376
11 | 2611323.7817 | 1259799.7786 | 2611335.1257 | 1259797.4188
12 | 2611370.4449 | 1259800.4654 | 2611370.4358 | 1259800.4177
13 | 2611422.4107 | 1259775.8509 | 2611415.4954 | 1259782.1197
14 | 2611415.4954 | 1259782.1197 | 2611418.4948 | 1259793.9001 | 2611417.7717 | 1259803.8221
15 | 2611390.7767 | 1259684.3232 | 2611389.4576 | 1259678.3636
16 | 2611417.7153 | 1259692.2376 | 2611441.2809 | 1259686.5018
17 | 2611323.7817 | 1259799.7786 | 2611288.0384 | 1259807.8626
18 | 2611323.7817 | 1259799.7786 | 2611326.7144 | 1259815.5525
19 | 2611370.4449 | 1259800.4654 | 2611371.7061 | 1259807.0676
20 | 2611422.4107 | 1259775.8509 | 2611430.7215 | 1259753.3344
21 | 2611422.4107 | 1259775.8509 | 2611426.2375 | 1259776.7589 | 2611428.5884 | 1259776.9858 | 2611431.6868 | 1259776.5025 | 2611433.7599 | 1259776.1841 | 2611438.1439 | 1259773.3906 | 2611445.7196 | 1259772.549
22 | 2611417.7717 | 1259803.8221 | 2611417.208 | 1259811.5566
23 | 2611389.4576 | 1259678.3636 | 2611388.1395 | 1259672.4086
24 | 2611455.4829 | 1259684.5417 | 2611447.2521 | 1259685.0484 | 2611441.2809 | 1259686.5018
25 | 2611371.7141 | 1259807.1097 | 2611371.7061 | 1259807.0676
26 | 2611372.9753 | 1259813.712 | 2611371.7141 | 1259807.1097
27 | 2611372.9835 | 1259813.755 | 2611372.9753 | 1259813.712
28 | 2611374.1913 | 1259820.0774 | 2611372.9835 | 1259813.755
29 | 2611327.9518 | 1259822.2083 | 2611326.7144 | 1259815.5525
30 | 2611430.7215 | 1259753.3344 | 2611436.1661 | 1259738.5833
31 | 2611445.7196 | 1259772.549 | 2611455.4372 | 1259774.7915
32 | 2611445.7196 | 1259772.549 | 2611437.8284 | 1259792.2069
33 | 2611416.1446 | 1259826.1783 | 2611416.5365 | 1259820.77 | 2611417.208 | 1259811.5566
34 | 2611329.1893 | 1259828.8639 | 2611327.9518 | 1259822.2083
35 | 2611331.7311 | 1259842.5357 | 2611329.1893 | 1259828.8639
36 | 2611331.7311 | 1259842.5357 | 2611332.9213 | 1259848.9376
37 | 2611336.2668 | 1259866.9318 | 2611332.9213 | 1259848.9376
38 | 2611336.2668 | 1259866.9318 | 2611337.8269 | 1259875.3228
39 | 2611339.7172 | 1259885.49 | 2611337.8269 | 1259875.3228
40 | 2611339.7172 | 1259885.49 | 2611339.9385 | 1259886.6806
41 | 2611487.2414 | 1259676.8977 | 2611498.6104 | 1259643.675 | 2611498.3777 | 1259631.533 | 2611500.5148 | 1259628.2553
42 | 2611487.2414 | 1259676.8977 | 2611505.9561 | 1259682.9158
43 | 2611513.9869 | 1259685.4997 | 2611506.4777 | 1259683.0835 | 2611505.9561 | 1259682.9158
44 | 2611473.6023 | 1259718.8776 | 2611469.035 | 1259732.9362
45 | 2611473.6023 | 1259718.8776 | 2611492.7559 | 1259722.3106
46 | 2611468.8154 | 1259733.6121 | 2611469.035 | 1259732.9362
47 | 2611496.3677 | 1259722.958 | 2611492.7559 | 1259722.3106
48 | 2611513.9869 | 1259685.4997 | 2611511.6142 | 1259698.5092
49 | 2611516.1561 | 1259686.1932 | 2611513.9869 | 1259685.4997
50 | 2611496.3677 | 1259722.958 | 2611497.9646 | 1259723.2442
51 | 2611511.6142 | 1259698.5092 | 2611510.6547 | 1259703.7699
52 | 2611516.1561 | 1259686.1932 | 2611522.4072 | 1259667.3389
53 | 2611514.8651 | 1259726.2734 | 2611497.9646 | 1259723.2442
54 | 2611510.6547 | 1259703.7699 | 2611509.6942 | 1259709.0362
55 | 2611532.1592 | 1259637.9249 | 2611522.4072 | 1259667.3389
56 | 2611588.1298 | 1259709.3153 | 2611592.2056 | 1259681.7757
57 | 2611588.1298 | 1259709.3153 | 2611580.384 | 1259749.6784
58 | 2611588.1298 | 1259709.3153 | 2611609.793 | 1259712.3727
59 | 2611588.1298 | 1259709.3153 | 2611571.3109 | 1259703.9143
60 | 2611571.3109 | 1259703.9143 | 2611570.6622 | 1259703.706
61 | 2611570.6622 | 1259703.706 | 2611567.0188 | 1259702.5361
62 | 2611571.2002 | 1259629.3838 | 2611585.2485 | 1259633.9117
63 | 2611571.2002 | 1259629.3838 | 2611565.7446 | 1259645.8941
64 | 2611561.401 | 1259700.732 | 2611567.0188 | 1259702.5361
65 | 2611565.7446 | 1259645.8941 | 2611565.192 | 1259647.5664
66 | 2611532.1116 | 1259786.8255 | 2611534.3239 | 1259774.6853
67 | 2611532.1116 | 1259786.8255 | 2611524.5427 | 1259786.0471
68 | 2611534.3239 | 1259774.6853 | 2611535.3403 | 1259769.1071
69 | 2611510.1282 | 1259784.5646 | 2611524.5427 | 1259786.0471
70 | 2611555.7837 | 1259698.9282 | 2611561.401 | 1259700.732
71 | 2611563.3421 | 1259653.1648 | 2611565.192 | 1259647.5664
72 | 2611470.4197 | 1259637.9501 | 2611455.4829 | 1259684.5417
73 | 2611455.4829 | 1259684.5417 | 2611445.9303 | 1259711.7138
74 | 2611470.4197 | 1259637.9501 | 2611474.5545 | 1259625.0476
75 | 2611470.4197 | 1259637.9501 | 2611461.2685 | 1259639.9866
76 | 2611442.858 | 1259720.4528 | 2611445.9303 | 1259711.7138
77 | 2611479.9035 | 1259608.3562 | 2611474.5545 | 1259625.0476
78 | 2611439.6907 | 1259643.15 | 2611443.7213 | 1259643.8916 | 2611461.2685 | 1259639.9866
79 | 2611442.858 | 1259720.4528 | 2611436.1661 | 1259738.5833
80 | 2611479.9035 | 1259608.3562 | 2611481.5026 | 1259603.3664
81 | 2611388.1395 | 1259672.4086 | 2611386.5671 | 1259665.3047
82 | 2611490.0654 | 1259576.6465 | 2611481.5026 | 1259603.3664
83 | 2611490.0654 | 1259576.6465 | 2611469.3064 | 1259570.4245
84 | 2611469.3064 | 1259570.4245 | 2611465.8198 | 1259580.6803 | 2611463.5407 | 1259581.1535
85 | 2611463.5407 | 1259581.1535 | 2611463.4795 | 1259581.1662
86 | 2611399.9328 | 1259935.2207 | 2611419.3798 | 1259931.3487
87 | 2611389.9073 | 1259936.6641 | 2611394.4824 | 1259936.3059 | 2611399.9328 | 1259935.2207
88 | 2611425.9677 | 1259930.037 | 2611419.3798 | 1259931.3487
89 | 2611379.1325 | 1259943.5148 | 2611382.0545 | 1259944.5877 | 2611384.5924 | 1259945.5154 | 2611387.0701 | 1259946.4208 | 2611389.9073 | 1259936.6641
90 | 2611425.9677 | 1259930.037 | 2611437.8909 | 1259927.663
91 | 2611348.123 | 1259930.7024 | 2611379.1325 | 1259943.5148
92 | 2611378.302 | 1259987.6319 | 2611375.7034 | 1259986.9265 | 2611378.0162 | 1259979.4481 | 2611379.1304 | 1259976.1035 | 2611383.4591 | 1259958.8334 | 2611387.0701 | 1259946.4208 | 2611384.5924 | 1259945.5154 | 2611382.0545 | 1259944.5877 | 2611379.1325 | 1259943.5148
93 | 2611379.1325 | 1259943.5148 | 2611384.9827 | 1259925.6805
94 | 2611452.8471 | 1259924.6851 | 2611437.8909 | 1259927.663
95 | 2611427.4616 | 1259821.7028 | 2611413.2186 | 1259865.3862
96 | 2611433.1157 | 1259804.3617 | 2611427.4616 | 1259821.7028
97 | 2611348.123 | 1259930.7024 | 2611328.9656 | 1259922.994 | 2611314.368 | 1259914.4976
98 | 2611348.123 | 1259930.7024 | 2611343.3278 | 1259904.9106
99 | 2611378.302 | 1259987.6319 | 2611380.5919 | 1259980.3314 | 2611416.1983 | 1259973.406 | 2611427.0791 | 1259971.5952
100 | 2611427.0791 | 1259971.5952 | 2611449.3257 | 1259967.893
101 | 2611463.8947 | 1259922.4855 | 2611452.8471 | 1259924.6851
102 | 2611437.8284 | 1259792.2069 | 2611434.9891 | 1259799.2798 | 2611433.8381 | 1259802.1462 | 2611433.1157 | 1259804.3617
103 | 2611314.368 | 1259914.4976 | 2611299.4197 | 1259905.7971
104 | 2611339.9385 | 1259886.6806 | 2611343.3278 | 1259904.9106
105 | 2611456.9351 | 1259966.5469 | 2611452.1948 | 1259967.4155 | 2611449.3257 | 1259967.893
106 | 2611463.8947 | 1259922.4855 | 2611460.8713 | 1259897.8355
107 | 2611463.8947 | 1259922.4855 | 2611467.3069 | 1259938.729
108 | 2611460.8713 | 1259897.8355 | 2611460.6523 | 1259896.0502 | 2611460.4679 | 1259885.189
109 | 2611460.2038 | 1259869.6279 | 2611460.4679 | 1259885.189
110 | 2611460.2038 | 1259869.6279 | 2611460.0093 | 1259858.1678 | 2611459.8741 | 1259848.4922
111 | 2611504.3456 | 1259783.9698 | 2611510.1282 | 1259784.5646
112 | 2611504.3456 | 1259783.9698 | 2611487.3408 | 1259782.2201
113 | 2611504.3456 | 1259783.9698 | 2611506.8428 | 1259770.2736
114 | 2611487.3408 | 1259782.2201 | 2611484.3029 | 1259781.9075 | 2611484.3029 | 1259781.9075
115 | 2611506.8428 | 1259770.2736 | 2611507.1999 | 1259768.3152
116 | 2611535.6977 | 1259767.1461 | 2611535.3403 | 1259769.1071
117 | 2611478.5002 | 1259783.0742 | 2611484.3029 | 1259781.9075
118 | 2611507.2008 | 1259768.3102 | 2611507.1999 | 1259768.3152
119 | 2611535.6977 | 1259767.1461 | 2611536.2996 | 1259763.8427
120 | 2611475.2105 | 1259783.7356 | 2611478.5002 | 1259783.0742
121 | 2611536.6569 | 1259761.8823 | 2611536.2996 | 1259763.8427
122 | 2611455.4372 | 1259774.7915 | 2611460.4662 | 1259759.3118
123 | 2611455.4372 | 1259774.7915 | 2611469.6171 | 1259776.6645
124 | 2611475.2105 | 1259783.7356 | 2611469.6171 | 1259776.6645
125 | 2611415.7237 | 1259831.9872 | 2611408.263 | 1259854.7252
126 | 2611415.7237 | 1259831.9872 | 2611416.1446 | 1259826.1783
127 | 2611408.263 | 1259854.7252 | 2611402.4541 | 1259872.4291
128 | 2611400.6374 | 1259877.966 | 2611402.4541 | 1259872.4291
129 | 2611400.6374 | 1259877.966 | 2611398.6766 | 1259883.9421
130 | 2611285.7857 | 1259897.8617 | 2611299.4197 | 1259905.7971
131 | 2611541.5835 | 1259694.3591 | 2611553.1899 | 1259698.0953
132 | 2611541.5835 | 1259694.3591 | 2611544.9899 | 1259684.0565
133 | 2611553.1899 | 1259698.0953 | 2611550.0681 | 1259715.3939
134 | 2611553.1899 | 1259698.0953 | 2611555.7837 | 1259698.9282
135 | 2611544.9899 | 1259684.0565 | 2611545.5118 | 1259682.478
136 | 2611549.2636 | 1259719.8519 | 2611550.0681 | 1259715.3939
137 | 2611546.8392 | 1259678.4634 | 2611545.5118 | 1259682.478
138 | 2611548.3461 | 1259724.9362 | 2611549.2636 | 1259719.8519
139 | 2611546.8392 | 1259678.4634 | 2611548.6896 | 1259672.8671
140 | 2611509.6308 | 1259709.3836 | 2611509.6942 | 1259709.0362
141 | 2611548.6896 | 1259672.8671 | 2611550.5409 | 1259667.268
142 | 2611550.5409 | 1259667.268 | 2611552.3894 | 1259661.6775
143 | 2611555.6766 | 1259651.7355 | 2611552.3894 | 1259661.6775
144 | 2611548.2074 | 1259725.7043 | 2611548.3461 | 1259724.9362
145 | 2611555.6766 | 1259651.7355 | 2611550.628 | 1259649.9804
146 | 2611555.6766 | 1259651.7355 | 2611563.0125 | 1259654.1625
147 | 2611544.2065 | 1259647.7481 | 2611550.628 | 1259649.9804
148 | 2611563.0125 | 1259654.1625 | 2611563.3421 | 1259653.1648
149 | 2611542.007 | 1259646.9835 | 2611544.2065 | 1259647.7481
150 | 2611548.2074 | 1259725.7043 | 2611547.0646 | 1259732.0508 | 2611547.0646 | 1259732.0508
151 | 2611548.2074 | 1259725.7043 | 2611535.5231 | 1259723.4049
152 | 2611512.061 | 1259741.653 | 2611512.0597 | 1259741.6602
153 | 2611514.8651 | 1259726.2734 | 2611512.061 | 1259741.653
154 | 2611516.0306 | 1259719.8713 | 2611514.8651 | 1259726.2734
155 | 2611536.6569 | 1259761.8823 | 2611537.2582 | 1259758.5822
156 | 2611537.616 | 1259756.6186 | 2611537.2582 | 1259758.5822
157 | 2611547.0646 | 1259732.0508 | 2611542.2505 | 1259731.1853 | 2611540.1356 | 1259742.7914
158 | 2611535.5231 | 1259723.4049 | 2611530.3179 | 1259722.4613
159 | 2611539.5342 | 1259746.0918 | 2611540.1356 | 1259742.7914
160 | 2611530.3179 | 1259722.4613 | 2611525.1098 | 1259721.5172
161 | 2611539.5342 | 1259746.0918 | 2611539.1769 | 1259748.0528
162 | 2611525.1098 | 1259721.5172 | 2611519.9011 | 1259720.573
163 | 2611538.5749 | 1259751.3564 | 2611539.1769 | 1259748.0528
164 | 2611516.0306 | 1259719.8713 | 2611519.9011 | 1259720.573
165 | 2611538.5749 | 1259751.3564 | 2611538.2178 | 1259753.3163
166 | 2611537.616 | 1259756.6186 | 2611538.2178 | 1259753.3163
167 | 2611516.0306 | 1259719.8713 | 2611507.9845 | 1259718.4103 | 2611508.7339 | 1259714.3015
168 | 2611509.6308 | 1259709.3836 | 2611508.7339 | 1259714.3015
169 | 2611463.4795 | 1259581.1662 | 2611437.9024 | 1259586.4764
170 | 2611425.0153 | 1259589.152 | 2611428.8098 | 1259607.0945
171 | 2611425.0153 | 1259589.152 | 2611437.9024 | 1259586.4764
172 | 2611428.8098 | 1259607.0945 | 2611430.0637 | 1259613.0237

## bus_geodata
| x | y | coords
0 | 2611364.9197 | 1259745.5612
1 | 2611365.5713 | 1259748.9859
2 | 2611357.4816 | 1259706.4686
3 | 2611389.8014 | 1259698.9843
4 | 2611373.2776 | 1259789.4883
5 | 2611368.5353 | 1259790.4688
6 | 2611400.7324 | 1259784.2515
7 | 2611393.816 | 1259698.0546
8 | 2611335.1257 | 1259797.4188
9 | 2611370.4358 | 1259800.4177
10 | 2611415.4954 | 1259782.1197
11 | 2611390.7767 | 1259684.3232
12 | 2611417.7153 | 1259692.2376
13 | 2611323.7817 | 1259799.7786
14 | 2611370.4449 | 1259800.4654
15 | 2611422.4107 | 1259775.8509
16 | 2611417.7717 | 1259803.8221
17 | 2611389.4576 | 1259678.3636
18 | 2611441.2809 | 1259686.5018
19 | 2611371.7061 | 1259807.0676
20 | 2611371.7141 | 1259807.1097
21 | 2611372.9753 | 1259813.712
22 | 2611372.9835 | 1259813.755
23 | 2611374.1913 | 1259820.0774
24 | 2611288.0384 | 1259807.8626
25 | 2611326.7144 | 1259815.5525
26 | 2611430.7215 | 1259753.3344
27 | 2611445.7196 | 1259772.549
28 | 2611417.208 | 1259811.5566
29 | 2611327.9518 | 1259822.2083
30 | 2611329.1893 | 1259828.8639
31 | 2611331.7311 | 1259842.5357
32 | 2611332.9213 | 1259848.9376
33 | 2611336.2668 | 1259866.9318
34 | 2611337.8269 | 1259875.3228
35 | 2611339.7172 | 1259885.49
36 | 2611500.5148 | 1259628.2553
37 | 2611487.2414 | 1259676.8977
38 | 2611505.9561 | 1259682.9158
39 | 2611473.6023 | 1259718.8776
40 | 2611469.035 | 1259732.9362
41 | 2611492.7559 | 1259722.3106
42 | 2611513.9869 | 1259685.4997
43 | 2611468.8154 | 1259733.6121
44 | 2611496.3677 | 1259722.958
45 | 2611511.6142 | 1259698.5092
46 | 2611516.1561 | 1259686.1932
47 | 2611497.9646 | 1259723.2442
48 | 2611510.6547 | 1259703.7699
49 | 2611522.4072 | 1259667.3389
50 | 2611592.2056 | 1259681.7757
51 | 2611588.1298 | 1259709.3153
52 | 2611580.384 | 1259749.6784
53 | 2611609.793 | 1259712.3727
54 | 2611571.3109 | 1259703.9143
55 | 2611570.6622 | 1259703.706
56 | 2611585.2485 | 1259633.9117
57 | 2611571.2002 | 1259629.3838
58 | 2611567.0188 | 1259702.5361
59 | 2611565.7446 | 1259645.8941
60 | 2611532.1116 | 1259786.8255
61 | 2611534.3239 | 1259774.6853
62 | 2611524.5427 | 1259786.0471
63 | 2611561.401 | 1259700.732
64 | 2611565.192 | 1259647.5664
65 | 2611455.4829 | 1259684.5417
66 | 2611470.4197 | 1259637.9501
67 | 2611445.9303 | 1259711.7138
68 | 2611474.5545 | 1259625.0476
69 | 2611461.2685 | 1259639.9866
70 | 2611442.858 | 1259720.4528
71 | 2611479.9035 | 1259608.3562
72 | 2611439.6907 | 1259643.15
73 | 2611436.1661 | 1259738.5833
74 | 2611388.1395 | 1259672.4086
75 | 2611481.5026 | 1259603.3664
76 | 2611386.5671 | 1259665.3047
77 | 2611490.0654 | 1259576.6465
78 | 2611469.3064 | 1259570.4245
79 | 2611463.5407 | 1259581.1535
80 | 2611399.9328 | 1259935.2207
81 | 2611419.3798 | 1259931.3487
82 | 2611389.9073 | 1259936.6641
83 | 2611425.9677 | 1259930.037
84 | 2611379.1325 | 1259943.5148
85 | 2611437.8909 | 1259927.663
86 | 2611413.2186 | 1259865.3862
87 | 2611427.4616 | 1259821.7028
88 | 2611348.123 | 1259930.7024
89 | 2611378.302 | 1259987.6319
90 | 2611384.9827 | 1259925.6805
91 | 2611427.0791 | 1259971.5952
92 | 2611452.8471 | 1259924.6851
93 | 2611433.1157 | 1259804.3617
94 | 2611314.368 | 1259914.4976
95 | 2611343.3278 | 1259904.9106
96 | 2611449.3257 | 1259967.893
97 | 2611463.8946 | 1259922.4855
98 | 2611437.8284 | 1259792.2069
99 | 2611456.9351 | 1259966.5469
100 | 2611467.3069 | 1259938.729
101 | 2611460.8713 | 1259897.8355
102 | 2611460.4679 | 1259885.189
103 | 2611460.2038 | 1259869.6279
104 | 2611459.8741 | 1259848.4922
105 | 2611510.1282 | 1259784.5646
106 | 2611504.3456 | 1259783.9698
107 | 2611487.3408 | 1259782.2201
108 | 2611506.8428 | 1259770.2736
109 | 2611535.3403 | 1259769.1071
110 | 2611484.3029 | 1259781.9075
111 | 2611507.1999 | 1259768.3152
112 | 2611535.6977 | 1259767.1461
113 | 2611478.5002 | 1259783.0742
114 | 2611507.2008 | 1259768.3102
115 | 2611536.2996 | 1259763.8427
116 | 2611455.4372 | 1259774.7915
117 | 2611460.4662 | 1259759.3118
118 | 2611469.6171 | 1259776.6645
119 | 2611415.7237 | 1259831.9872
120 | 2611408.263 | 1259854.7252
121 | 2611416.1446 | 1259826.1783
122 | 2611475.2105 | 1259783.7356
123 | 2611402.4541 | 1259872.4291
124 | 2611400.6374 | 1259877.966
125 | 2611398.6766 | 1259883.9421
126 | 2611299.4197 | 1259905.7971
127 | 2611339.9385 | 1259886.6806
128 | 2611285.7857 | 1259897.8617
129 | 2611532.1592 | 1259637.9249
130 | 2611541.5835 | 1259694.3591
131 | 2611553.1899 | 1259698.0953
132 | 2611544.9899 | 1259684.0565
133 | 2611550.0681 | 1259715.3939
134 | 2611555.7837 | 1259698.9282
135 | 2611545.5118 | 1259682.478
136 | 2611549.2636 | 1259719.8519
137 | 2611546.8392 | 1259678.4634
138 | 2611509.6942 | 1259709.0362
139 | 2611548.6896 | 1259672.8671
140 | 2611550.5409 | 1259667.268
141 | 2611552.3894 | 1259661.6775
142 | 2611548.3461 | 1259724.9362
143 | 2611555.6766 | 1259651.7355
144 | 2611550.628 | 1259649.9804
145 | 2611563.0125 | 1259654.1625
146 | 2611544.2065 | 1259647.7481
147 | 2611563.3421 | 1259653.1648
148 | 2611542.007 | 1259646.9835
149 | 2611548.2074 | 1259725.7043
150 | 2611512.0597 | 1259741.6602
151 | 2611512.061 | 1259741.653
152 | 2611514.8651 | 1259726.2734
153 | 2611536.6569 | 1259761.8823
154 | 2611537.2582 | 1259758.5822
155 | 2611547.0646 | 1259732.0508
156 | 2611535.5231 | 1259723.4049
157 | 2611540.1356 | 1259742.7914
158 | 2611530.3179 | 1259722.4613
159 | 2611539.5342 | 1259746.0918
160 | 2611525.1098 | 1259721.5172
161 | 2611539.1769 | 1259748.0528
162 | 2611519.9011 | 1259720.573
163 | 2611538.5749 | 1259751.3564
164 | 2611538.2178 | 1259753.3163
165 | 2611537.616 | 1259756.6186
166 | 2611516.0306 | 1259719.8713
167 | 2611508.7339 | 1259714.3015
168 | 2611509.6308 | 1259709.3836
169 | 2611463.4795 | 1259581.1662
170 | 2611425.0153 | 1259589.152
171 | 2611428.8098 | 1259607.0945
172 | 2611437.9024 | 1259586.4764
173 | 2611430.0637 | 1259613.0237
174 | 2611438.1439 | 1259773.3906

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1