## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2939-37_0_10_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2939-37_0_10_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2939-37_0_10_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2939-37_0_10_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2939-37_0_10_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2939-37_0_10_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2939-37_0_10_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_2939-37_0_10_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_2939-37_0_10_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_2939-37_0_10_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_2939-37_0_10_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_2939-37_0_10_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_2939-37_0_10_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_2939-37_0_10_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_2939-37_0_10_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_2939-37_0_10_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_2939-37_0_10_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_2939-37_0_10_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_2939-37_0_10_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_2939-37_0_10_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_2939-37_0_10_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_2939-37_0_10_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_2939-37_0_10_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_2939-37_0_10_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_2939-37_0_10_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_2939-37_0_10_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_2939-37_0_10_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_2939-37_0_10_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_2939-37_0_10_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_2939-37_0_10_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_2939-37_0_10_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_2939-37_0_10_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_2939-37_0_10_node_42 | 0.4 | n |  | TRUE
33 | bus_LV_2939-37_0_10_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_2939-37_0_10_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_2939-37_0_10_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_2939-37_0_10_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_2939-37_0_10_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_2939-37_0_10_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_2939-37_0_10_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_2939-37_0_10_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_2939-37_0_10_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_2939-37_0_10_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_2939-37_0_10_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2939-37_0_10_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_2939-37_0_10_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_2939-37_0_10_node_56 | 0.4 | n |  | TRUE
47 | bus_LV_2939-37_0_10_node_68 | 0.4 | n |  | TRUE
48 | bus_LV_2939-37_0_10_node_69 | 0.4 | n |  | TRUE
49 | bus_LV_2939-37_0_10_node_61 | 0.4 | n |  | TRUE
50 | bus_LV_2939-37_0_10_node_78 | 0.4 | n |  | TRUE
51 | bus_LV_2939-37_0_10_node_60 | 0.4 | n |  | TRUE
52 | bus_LV_2939-37_0_10_node_77 | 0.4 | n |  | TRUE
53 | bus_LV_2939-37_0_10_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_2939-37_0_10_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_2939-37_0_10_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_2939-37_0_10_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_2939-37_0_10_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_2939-37_0_10_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_2939-37_0_10_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_2939-37_0_10_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_2939-37_0_10_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_2939-37_0_10_node_63 | 0.4 | n |  | TRUE
63 | bus_LV_2939-37_0_10_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_2939-37_0_10_node_85 | 0.4 | n |  | TRUE
65 | bus_LV_2939-37_0_10_node_95 | 0.4 | n |  | TRUE
66 | bus_LV_2939-37_0_10_node_83 | 0.4 | n |  | TRUE
67 | bus_LV_2939-37_0_10_node_162 | 0.4 | n |  | TRUE
68 | bus_LV_2939-37_0_10_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_2939-37_0_10_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_2939-37_0_10_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_2939-37_0_10_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_2939-37_0_10_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_2939-37_0_10_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_2939-37_0_10_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_2939-37_0_10_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_2939-37_0_10_node_74 | 0.4 | n |  | TRUE
77 | bus_LV_2939-37_0_10_node_76 | 0.4 | n |  | TRUE
78 | bus_LV_2939-37_0_10_node_75 | 0.4 | n |  | TRUE
79 | bus_LV_2939-37_0_10_node_148 | 0.4 | n |  | TRUE
80 | bus_LV_2939-37_0_10_node_123 | 0.4 | n |  | TRUE
81 | bus_LV_2939-37_0_10_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_2939-37_0_10_node_112 | 0.4 | n |  | TRUE
83 | bus_LV_2939-37_0_10_node_178 | 0.4 | n |  | TRUE
84 | bus_LV_2939-37_0_10_node_121 | 0.4 | n |  | TRUE
85 | bus_LV_2939-37_0_10_node_115 | 0.4 | n |  | TRUE
86 | bus_LV_2939-37_0_10_node_113 | 0.4 | n |  | TRUE
87 | bus_LV_2939-37_0_10_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_2939-37_0_10_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_2939-37_0_10_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_2939-37_0_10_node_96 | 0.4 | n |  | TRUE
91 | bus_LV_2939-37_0_10_node_97 | 0.4 | n |  | TRUE
92 | bus_LV_2939-37_0_10_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_2939-37_0_10_node_84 | 0.4 | n |  | TRUE
94 | bus_LV_2939-37_0_10_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_2939-37_0_10_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_2939-37_0_10_node_99 | 0.4 | n |  | TRUE
97 | bus_LV_2939-37_0_10_node_98 | 0.4 | n |  | TRUE
98 | bus_LV_2939-37_0_10_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_2939-37_0_10_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_2939-37_0_10_node_89 | 0.4 | n |  | TRUE
101 | bus_LV_2939-37_0_10_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_2939-37_0_10_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_2939-37_0_10_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_2939-37_0_10_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_2939-37_0_10_node_184 | 0.4 | n |  | TRUE
106 | bus_LV_2939-37_0_10_node_159 | 0.4 | n |  | TRUE
107 | bus_LV_2939-37_0_10_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_2939-37_0_10_node_109 | 0.4 | n |  | TRUE
109 | bus_LV_2939-37_0_10_node_110 | 0.4 | n |  | TRUE
110 | bus_LV_2939-37_0_10_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_2939-37_0_10_node_102 | 0.4 | n |  | TRUE
112 | bus_LV_2939-37_0_10_node_103 | 0.4 | n |  | TRUE
113 | bus_LV_2939-37_0_10_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_2939-37_0_10_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_2939-37_0_10_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_2939-37_0_10_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_2939-37_0_10_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_2939-37_0_10_node_116 | 0.4 | n |  | TRUE
119 | bus_LV_2939-37_0_10_node_136 | 0.4 | n |  | TRUE
120 | bus_LV_2939-37_0_10_node_132 | 0.4 | n |  | TRUE
121 | bus_LV_2939-37_0_10_node_137 | 0.4 | n |  | TRUE
122 | bus_LV_2939-37_0_10_node_138 | 0.4 | n |  | TRUE
123 | bus_LV_2939-37_0_10_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_2939-37_0_10_node_124 | 0.4 | n |  | TRUE
125 | bus_LV_2939-37_0_10_node_128 | 0.4 | n |  | TRUE
126 | bus_LV_2939-37_0_10_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_2939-37_0_10_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_2939-37_0_10_node_126 | 0.4 | n |  | TRUE
129 | bus_LV_2939-37_0_10_node_133 | 0.4 | n |  | TRUE
130 | bus_LV_2939-37_0_10_node_117 | 0.4 | n |  | TRUE
131 | bus_LV_2939-37_0_10_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_2939-37_0_10_node_119 | 0.4 | n |  | TRUE
133 | bus_LV_2939-37_0_10_node_120 | 0.4 | n |  | TRUE
134 | bus_LV_2939-37_0_10_node_122 | 0.4 | n |  | TRUE
135 | bus_LV_2939-37_0_10_node_131 | 0.4 | n |  | TRUE
136 | bus_LV_2939-37_0_10_node_146 | 0.4 | n |  | TRUE
137 | bus_LV_2939-37_0_10_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_2939-37_0_10_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_2939-37_0_10_node_134 | 0.4 | n |  | TRUE
140 | bus_LV_2939-37_0_10_node_135 | 0.4 | n |  | TRUE
141 | bus_LV_2939-37_0_10_node_147 | 0.4 | n |  | TRUE
142 | bus_LV_2939-37_0_10_node_141 | 0.4 | n |  | TRUE
143 | bus_LV_2939-37_0_10_node_139 | 0.4 | n |  | TRUE
144 | bus_LV_2939-37_0_10_node_168 | 0.4 | n |  | TRUE
145 | bus_LV_2939-37_0_10_node_145 | 0.4 | n |  | TRUE
146 | bus_LV_2939-37_0_10_node_181 | 0.4 | n |  | TRUE
147 | bus_LV_2939-37_0_10_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_2939-37_0_10_node_144 | 0.4 | n |  | TRUE
149 | bus_LV_2939-37_0_10_node_175 | 0.4 | n |  | TRUE
150 | bus_LV_2939-37_0_10_node_169 | 0.4 | n |  | TRUE
151 | bus_LV_2939-37_0_10_node_170 | 0.4 | n |  | TRUE
152 | bus_LV_2939-37_0_10_node_173 | 0.4 | n |  | TRUE
153 | bus_LV_2939-37_0_10_node_176 | 0.4 | n |  | TRUE
154 | bus_LV_2939-37_0_10_node_182 | 0.4 | n |  | TRUE
155 | bus_LV_2939-37_0_10_node_179 | 0.4 | n |  | TRUE
156 | bus_LV_2939-37_0_10_node_149 | 0.4 | n |  | TRUE
157 | bus_LV_2939-37_0_10_node_150 | 0.4 | n |  | TRUE
158 | bus_LV_2939-37_0_10_node_151 | 0.4 | n |  | TRUE
159 | bus_LV_2939-37_0_10_node_152 | 0.4 | n |  | TRUE
160 | bus_LV_2939-37_0_10_node_153 | 0.4 | n |  | TRUE
161 | bus_LV_2939-37_0_10_node_154 | 0.4 | n |  | TRUE
162 | bus_LV_2939-37_0_10_node_155 | 0.4 | n |  | TRUE
163 | bus_LV_2939-37_0_10_node_163 | 0.4 | n |  | TRUE
164 | bus_LV_2939-37_0_10_node_167 | 0.4 | n |  | TRUE
165 | bus_LV_2939-37_0_10_node_160 | 0.4 | n |  | TRUE
166 | bus_LV_2939-37_0_10_node_156 | 0.4 | n |  | TRUE
167 | bus_LV_2939-37_0_10_node_157 | 0.4 | n |  | TRUE
168 | bus_LV_2939-37_0_10_node_158 | 0.4 | n |  | TRUE
169 | bus_LV_2939-37_0_10_node_161 | 0.4 | n |  | TRUE
170 | bus_LV_2939-37_0_10_node_174 | 0.4 | n |  | TRUE
171 | bus_LV_2939-37_0_10_node_171 | 0.4 | n |  | TRUE
172 | bus_LV_2939-37_0_10_node_164 | 0.4 | n |  | TRUE
173 | bus_LV_2939-37_0_10_node_177 | 0.4 | n |  | TRUE
174 | bus_LV_2939-37_0_10_node_180 | 0.4 | n |  | TRUE
175 | bus_LV_2939-37_0_10_node_183 | 0.4 | n |  | TRUE
176 | bus_MV_391_0_node_110 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2939-37_0_10_load_0 | 0 | 0.0024876 | 0.00062345 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2939-37_0_10_load_1 | 1 | 0.005997 | 0.001503 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2939-37_0_10_load_2 | 2 | 0.002217 | 0.00055564 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2939-37_0_10_load_4 | 4 | 0.0047291 | 0.0011852 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2939-37_0_10_load_5 | 5 | 0.0019924 | 0.00049934 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2939-37_0_10_load_6 | 6 | 0.002577 | 0.00064586 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2939-37_0_10_load_7 | 7 | 0.0017718 | 0.00044406 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2939-37_0_10_load_30 | 8 | 0.0026157 | 0.00065555 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2939-37_0_10_load_8 | 9 | 0.0027077 | 0.0006786 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2939-37_0_10_load_26 | 10 | 0.002071 | 0.00051905 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2939-37_0_10_load_9 | 11 | 0.0022124 | 0.00055448 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2939-37_0_10_load_10 | 12 | 0.00051961 | 0.00013023 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2939-37_0_10_load_11 | 13 | 0.0014367 | 0.00036007 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2939-37_0_10_load_17 | 14 | 0.0032394 | 0.00081187 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2939-37_0_10_load_15 | 15 | 0.0024792 | 0.00062135 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2939-37_0_10_load_12 | 16 | 0.0021732 | 0.00054465 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2939-37_0_10_load_13 | 17 | 0.0027273 | 0.00068354 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2939-37_0_10_load_14 | 18 | 0.0044054 | 0.0011041 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2939-37_0_10_load_18 | 20 | 0.0012099 | 0.00030324 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2939-37_0_10_load_19 | 21 | 0.0028554 | 0.00071563 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2939-37_0_10_load_20 | 24 | 0.0041651 | 0.0010439 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2939-37_0_10_load_21 | 25 | 0.003458 | 0.00086667 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2939-37_0_10_load_22 | 26 | 0.0030894 | 0.00077428 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2939-37_0_10_load_23 | 27 | 0.0013661 | 0.00034238 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2939-37_0_10_load_25 | 29 | 0.0031284 | 0.00078405 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2939-37_0_10_load_27 | 30 | 0.0022002 | 0.00055141 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2939-37_0_10_load_28 | 31 | 0.0046045 | 0.001154 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2939-37_0_10_load_42 | 32 | 0.0022027 | 0.00055206 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2939-37_0_10_load_29 | 33 | 0.0024668 | 0.00061823 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2939-37_0_10_load_41 | 34 | 0.0022979 | 0.00057592 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2939-37_0_10_load_45 | 35 | 0.0053912 | 0.0013512 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2939-37_0_10_load_46 | 36 | 0.0021752 | 0.00054517 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2939-37_0_10_load_33 | 37 | 0.0038579 | 0.00096689 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2939-37_0_10_load_34 | 38 | 0.0032451 | 0.00081329 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2939-37_0_10_load_36 | 39 | 0.0033631 | 0.00084288 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2939-37_0_10_load_38 | 40 | 0.002379 | 0.00059623 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2939-37_0_10_load_39 | 42 | 0.0030063 | 0.00075345 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2939-37_0_10_load_43 | 43 | 0.0036852 | 0.00092359 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2939-37_0_10_load_40 | 44 | 0.0021488 | 0.00053853 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2939-37_0_10_load_55 | 45 | 0.0019292 | 0.00048351 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2939-37_0_10_load_56 | 46 | 0.0019555 | 0.0004901 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2939-37_0_10_load_68 | 47 | 0.0026593 | 0.00066647 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2939-37_0_10_load_69 | 48 | 0.0058845 | 0.0014748 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2939-37_0_10_load_61 | 49 | 0.001007 | 0.00025239 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2939-37_0_10_load_78 | 50 | 0.0018321 | 0.00045917 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2939-37_0_10_load_60 | 51 | 0.00092671 | 0.00023226 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2939-37_0_10_load_77 | 52 | 0.0019595 | 0.00049109 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2939-37_0_10_load_47 | 53 | 0.0011839 | 0.00029671 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2939-37_0_10_load_48 | 54 | 0.0015715 | 0.00039385 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2939-37_0_10_load_49 | 55 | 0.0016759 | 0.00042002 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2939-37_0_10_load_50 | 56 | 0.00096474 | 0.00024179 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2939-37_0_10_load_51 | 57 | 0.0023273 | 0.00058329 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2939-37_0_10_load_52 | 58 | 0.0036426 | 0.00091292 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2939-37_0_10_load_53 | 59 | 0.00091771 | 0.00023 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2939-37_0_10_load_62 | 60 | 0.0030723 | 0.00076999 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2939-37_0_10_load_59 | 61 | 0.00090889 | 0.00022779 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2939-37_0_10_load_63 | 62 | 0.0039474 | 0.00098932 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2939-37_0_10_load_57 | 63 | 0.0014402 | 0.00036095 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2939-37_0_10_load_85 | 64 | 0.0021881 | 0.00054839 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2939-37_0_10_load_95 | 65 | 0.0021242 | 0.00053237 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2939-37_0_10_load_83 | 66 | 0.0019883 | 0.00049831 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2939-37_0_10_load_58 | 68 | 0.00076565 | 0.00019189 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2939-37_0_10_load_64 | 69 | 0.0056084 | 0.0014056 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2939-37_0_10_load_65 | 70 | 0.0027506 | 0.00068936 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2939-37_0_10_load_66 | 71 | 0.0043339 | 0.0010862 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2939-37_0_10_load_67 | 72 | 0.005001 | 0.0012534 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2939-37_0_10_load_70 | 73 | 0.0026597 | 0.00066658 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2939-37_0_10_load_71 | 74 | 0.0018999 | 0.00047616 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2939-37_0_10_load_72 | 75 | 0.0033208 | 0.00083228 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2939-37_0_10_load_74 | 76 | 0.0024724 | 0.00061963 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2939-37_0_10_load_76 | 77 | 0.0025926 | 0.00064977 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2939-37_0_10_load_127 | 81 | 0.0029345 | 0.00073545 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2939-37_0_10_load_112 | 82 | 0.0026452 | 0.00066294 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2939-37_0_10_load_178 | 83 | 0.0091455 | 0.0022921 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2939-37_0_10_load_121 | 84 | 0.011593 | 0.0029056 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2939-37_0_10_load_113 | 86 | 0.002699 | 0.00067643 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2939-37_0_10_load_79 | 87 | 0.0019929 | 0.00049946 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2939-37_0_10_load_80 | 88 | 0.0014637 | 0.00036685 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2939-37_0_10_load_81 | 89 | 0.0022593 | 0.00056624 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2939-37_0_10_load_96 | 90 | 0.0013592 | 0.00034066 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2939-37_0_10_load_97 | 91 | 0.0061565 | 0.001543 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2939-37_0_10_load_82 | 92 | 0.0023478 | 0.00058841 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2939-37_0_10_load_84 | 93 | 0.0029978 | 0.00075132 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2939-37_0_10_load_86 | 94 | 0.0024111 | 0.00060428 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2939-37_0_10_load_99 | 96 | 0.0019563 | 0.00049029 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2939-37_0_10_load_98 | 97 | 0.0024276 | 0.00060842 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2939-37_0_10_load_93 | 98 | 0.0031484 | 0.00078906 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2939-37_0_10_load_88 | 99 | 0.0021277 | 0.00053325 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2939-37_0_10_load_89 | 100 | 0.0025851 | 0.00064789 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2939-37_0_10_load_90 | 101 | 0.0047708 | 0.0011957 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2939-37_0_10_load_91 | 102 | 0.0022451 | 0.00056266 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2939-37_0_10_load_92 | 103 | 0.0026088 | 0.00065384 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2939-37_0_10_load_94 | 104 | 0.0019112 | 0.000479 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2939-37_0_10_load_184 | 105 | 0.0013368 | 0.00033503 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2939-37_0_10_load_100 | 107 | 0.011958 | 0.0029971 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2939-37_0_10_load_109 | 108 | 0.0018113 | 0.00045396 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2939-37_0_10_load_110 | 109 | 0.001919 | 0.00048096 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2939-37_0_10_load_101 | 110 | 0.0023312 | 0.00058426 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2939-37_0_10_load_102 | 111 | 0.0018151 | 0.0004549 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2939-37_0_10_load_103 | 112 | 0.0049461 | 0.0012396 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2939-37_0_10_load_104 | 113 | 0.0017447 | 0.00043727 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2939-37_0_10_load_105 | 114 | 0.0051434 | 0.0012891 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2939-37_0_10_load_106 | 115 | 0.0046246 | 0.001159 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2939-37_0_10_load_107 | 116 | 0.0025278 | 0.00063353 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2939-37_0_10_load_108 | 117 | 0.010776 | 0.0027007 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2939-37_0_10_load_116 | 118 | 0.0048938 | 0.0012265 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2939-37_0_10_load_132 | 120 | 0.0057304 | 0.0014362 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2939-37_0_10_load_138 | 122 | 0.0027675 | 0.0006936 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2939-37_0_10_load_111 | 123 | 0.0019461 | 0.00048774 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2939-37_0_10_load_124 | 124 | 0.0043596 | 0.0010926 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2939-37_0_10_load_128 | 125 | 0.0018058 | 0.00045257 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2939-37_0_10_load_114 | 126 | 0.0026541 | 0.00066517 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2939-37_0_10_load_125 | 127 | 0.0079668 | 0.0019967 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2939-37_0_10_load_126 | 128 | 0.0074681 | 0.0018717 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2939-37_0_10_load_117 | 130 | 0.0023584 | 0.00059107 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_2939-37_0_10_load_118 | 131 | 0.003195 | 0.00080073 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_2939-37_0_10_load_119 | 132 | 0.002564 | 0.0006426 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_2939-37_0_10_load_120 | 133 | 0.002605 | 0.00065287 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_2939-37_0_10_load_131 | 135 | 0.0045714 | 0.0011457 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_2939-37_0_10_load_146 | 136 | 0.0030759 | 0.0007709 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_2939-37_0_10_load_130 | 137 | 0.0019511 | 0.000489 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_2939-37_0_10_load_129 | 138 | 0.0020029 | 0.00050197 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_2939-37_0_10_load_134 | 139 | 0.0019383 | 0.00048578 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_2939-37_0_10_load_147 | 141 | 0.0014325 | 0.00035902 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_2939-37_0_10_load_141 | 142 | 0.0051742 | 0.0012968 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_2939-37_0_10_load_139 | 143 | 0.0042449 | 0.0010639 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_2939-37_0_10_load_168 | 144 | 0.001562 | 0.00039146 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_2939-37_0_10_load_145 | 145 | 0.0027673 | 0.00069356 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_2939-37_0_10_load_181 | 146 | 0.012489 | 0.0031299 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_2939-37_0_10_load_144 | 148 | 0.0022851 | 0.00057271 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_2939-37_0_10_load_175 | 149 | 0.0095039 | 0.0023819 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_2939-37_0_10_load_170 | 151 | 0.0028053 | 0.00070309 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_2939-37_0_10_load_173 | 152 | 0.0047266 | 0.0011846 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_2939-37_0_10_load_182 | 154 | 0.0032571 | 0.00081632 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_2939-37_0_10_load_179 | 155 | 0.004731 | 0.0011857 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_2939-37_0_10_load_149 | 156 | 0.0024743 | 0.00062011 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_2939-37_0_10_load_150 | 157 | 0.0019666 | 0.00049288 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_2939-37_0_10_load_151 | 158 | 0.0024161 | 0.00060552 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_2939-37_0_10_load_152 | 159 | 0.0036816 | 0.00092268 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_2939-37_0_10_load_153 | 160 | 0.0023897 | 0.0005989 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_2939-37_0_10_load_154 | 161 | 0.0015487 | 0.00038814 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_2939-37_0_10_load_155 | 162 | 0.0016265 | 0.00040763 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_2939-37_0_10_load_163 | 163 | 0.0035142 | 0.00088075 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_2939-37_0_10_load_167 | 164 | 0.0036835 | 0.00092317 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_2939-37_0_10_load_160 | 165 | 0.0016314 | 0.00040887 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_2939-37_0_10_load_156 | 166 | 0.0017723 | 0.00044417 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_2939-37_0_10_load_157 | 167 | 0.0019716 | 0.00049413 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_2939-37_0_10_load_158 | 168 | 0.0018408 | 0.00046134 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_2939-37_0_10_load_161 | 169 | 0.0041676 | 0.0010445 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_2939-37_0_10_load_174 | 170 | 0.0023183 | 0.00058102 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_2939-37_0_10_load_171 | 171 | 0.0024807 | 0.00062173 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_2939-37_0_10_load_164 | 172 | 0.0025086 | 0.00062872 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_2939-37_0_10_load_177 | 173 | 0.0019699 | 0.00049371 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_2939-37_0_10_load_180 | 174 | 0.0033886 | 0.00084928 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_2939-37_0_10_load_183 | 175 | 0.0035998 | 0.0009022 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 102 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2939-37_0_10_line_0 |  | 0 | 1 | 0.0013009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2939-37_0_10_line_1 |  | 1 | 2 | 0.0028229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2939-37_0_10_line_2 |  | 2 | 3 | 0.021795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2939-37_0_10_line_3 |  | 3 | 4 | 0.01769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2939-37_0_10_line_4 |  | 3 | 5 | 0.010835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2939-37_0_10_line_5 |  | 4 | 6 | 0.012194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2939-37_0_10_line_6 |  | 5 | 7 | 0.033857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2939-37_0_10_line_7 |  | 6 | 8 | 0.024095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2939-37_0_10_line_8 |  | 7 | 9 | 0.00088508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2939-37_0_10_line_9 |  | 8 | 10 | 0.0075402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2939-37_0_10_line_10 |  | 9 | 11 | 0.0019171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2939-37_0_10_line_11 |  | 10 | 28 | 0.0071537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2939-37_0_10_line_12 |  | 11 | 12 | 0.0085715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2939-37_0_10_line_13 |  | 12 | 13 | 0.01755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2939-37_0_10_line_14 |  | 13 | 14 | 0.0045893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2939-37_0_10_line_15 |  | 14 | 15 | 0.016706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2939-37_0_10_line_16 |  | 15 | 17 | 0.0090674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2939-37_0_10_line_17 |  | 16 | 17 | 0.0042858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2939-37_0_10_line_18 |  | 16 | 18 | 0.023131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2939-37_0_10_line_19 |  | 18 | 19 | 0.019632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2939-37_0_10_line_20 |  | 19 | 20 | 0.054093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2939-37_0_10_line_21 |  | 19 | 21 | 0.0031638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2939-37_0_10_line_22 |  | 20 | 22 | 0.010668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2939-37_0_10_line_23 |  | 22 | 23 | 0.009956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2939-37_0_10_line_24 |  | 23 | 35 | 0.028398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2939-37_0_10_line_25 |  | 23 | 36 | 0.03825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2939-37_0_10_line_26 |  | 24 | 25 | 0.01241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2939-37_0_10_line_27 |  | 24 | 26 | 0.0092789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2939-37_0_10_line_28 |  | 25 | 27 | 0.010251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2939-37_0_10_line_29 |  | 26 | 28 | 0.022542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2939-37_0_10_line_30 |  | 27 | 29 | 0.0091473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2939-37_0_10_line_31 |  | 28 | 30 | 0.006879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2939-37_0_10_line_32 |  | 29 | 31 | 0.012631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2939-37_0_10_line_33 |  | 30 | 32 | 0.006761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2939-37_0_10_line_34 |  | 31 | 33 | 0.04397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2939-37_0_10_line_35 |  | 32 | 34 | 0.0098191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2939-37_0_10_line_36 |  | 34 | 44 | 0.0069888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2939-37_0_10_line_37 |  | 35 | 49 | 0.026983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2939-37_0_10_line_38 |  | 36 | 50 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_2939-37_0_10_line_39 |  | 37 | 38 | 0.013873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2939-37_0_10_line_40 |  | 38 | 39 | 0.024721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2939-37_0_10_line_41 |  | 39 | 40 | 0.036534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2939-37_0_10_line_42 |  | 40 | 41 | 0.0044684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2939-37_0_10_line_43 |  | 41 | 45 | 0.01884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_2939-37_0_10_line_44 |  | 41 | 46 | 0.0056201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_2939-37_0_10_line_45 |  | 42 | 43 | 0.022439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2939-37_0_10_line_46 |  | 43 | 47 | 0.029223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2939-37_0_10_line_47 |  | 45 | 64 | 0.012939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_2939-37_0_10_line_48 |  | 46 | 65 | 0.020398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_2939-37_0_10_line_49 |  | 47 | 48 | 0.0017623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2939-37_0_10_line_50 |  | 48 | 72 | 0.030573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2939-37_0_10_line_51 |  | 49 | 51 | 0.0037129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2939-37_0_10_line_52 |  | 50 | 52 | 0.0012686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_2939-37_0_10_line_53 |  | 51 | 68 | 0.0082075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2939-37_0_10_line_54 |  | 52 | 87 | 0.019564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_2939-37_0_10_line_55 |  | 53 | 54 | 0.00087024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2939-37_0_10_line_56 |  | 53 | 55 | 0.0034418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2939-37_0_10_line_57 |  | 54 | 56 | 0.01159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2939-37_0_10_line_58 |  | 55 | 57 | 0.0062244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2939-37_0_10_line_59 |  | 56 | 58 | 0.01599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2939-37_0_10_line_60 |  | 57 | 59 | 0.020609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2939-37_0_10_line_61 |  | 58 | 60 | 0.0035316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2939-37_0_10_line_62 |  | 59 | 61 | 0.0082744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2939-37_0_10_line_63 |  | 60 | 62 | 0.024697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2939-37_0_10_line_64 |  | 61 | 63 | 0.0058683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2939-37_0_10_line_65 |  | 62 | 69 | 0.0033455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2939-37_0_10_line_66 |  | 63 | 68 | 0.0021804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2939-37_0_10_line_67 |  | 64 | 66 | 0.0062001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_2939-37_0_10_line_68 |  | 65 | 67 | 0.022982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_2939-37_0_10_line_69 |  | 66 | 92 | 0.019524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_2939-37_0_10_line_70 |  | 67 | 105 | 0.11966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2939-37_0_10_line_71 |  | 67 | 106 | 0.048064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_2939-37_0_10_line_72 |  | 69 | 70 | 0.0075696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2939-37_0_10_line_73 |  | 70 | 71 | 0.017376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2939-37_0_10_line_74 |  | 71 | 72 | 0.00061028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2939-37_0_10_line_75 |  | 73 | 74 | 0.019446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2939-37_0_10_line_76 |  | 73 | 75 | 0.0076186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2939-37_0_10_line_77 |  | 75 | 76 | 0.0099112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2939-37_0_10_line_78 |  | 76 | 77 | 7.8483e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2939-37_0_10_line_79 |  | 77 | 82 | 0.0056692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2939-37_0_10_line_80 |  | 78 | 79 | 0.097887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2939-37_0_10_line_81 |  | 78 | 80 | 0.040043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_2939-37_0_10_line_82 |  | 78 | 81 | 0.029813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2939-37_0_10_line_83 |  | 79 | 83 | 0.099723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2939-37_0_10_line_84 |  | 80 | 84 | 0.03647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_2939-37_0_10_line_85 |  | 81 | 85 | 0.0056866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2939-37_0_10_line_86 |  | 82 | 86 | 0.0010848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2939-37_0_10_line_87 |  | 83 | 155 | 0.03217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2939-37_0_10_line_88 |  | 84 | 132 | 0.0044259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_2939-37_0_10_line_89 |  | 85 | 127 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2939-37_0_10_line_90 |  | 85 | 126 | 0.012466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2939-37_0_10_line_91 |  | 86 | 126 | 0.0199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2939-37_0_10_line_92 |  | 87 | 88 | 0.0052292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_2939-37_0_10_line_93 |  | 88 | 89 | 0.017076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
94 | LV_2939-37_0_10_line_94 |  | 89 | 90 | 0.00072202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_2939-37_0_10_line_95 |  | 90 | 91 | 0.025836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_2939-37_0_10_line_96 |  | 91 | 104 | 0.0039643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_2939-37_0_10_line_97 |  | 92 | 93 | 0.0056636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_2939-37_0_10_line_98 |  | 93 | 94 | 0.019344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_2939-37_0_10_line_99 |  | 94 | 95 | 0.010454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_2939-37_0_10_line_100 |  | 95 | 96 | 0.0093266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2939-37_0_10_line_101 |  | 95 | 97 | 0.011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_2939-37_0_10_line_102 |  | 97 | 98 | 0.0077812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_2939-37_0_10_line_103 |  | 98 | 102 | 0.014797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_2939-37_0_10_line_104 |  | 99 | 100 | 0.016967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
105 | LV_2939-37_0_10_line_105 |  | 99 | 101 | 0.0052525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_2939-37_0_10_line_106 |  | 100 | 102 | 0.010659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_2939-37_0_10_line_107 |  | 101 | 103 | 0.0020576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_2939-37_0_10_line_108 |  | 103 | 104 | 0.016865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_2939-37_0_10_line_109 |  | 105 | 172 | 0.07344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2939-37_0_10_line_110 |  | 106 | 169 | 0.0067733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_2939-37_0_10_line_111 |  | 106 | 167 | 0.017304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2939-37_0_10_line_112 |  | 107 | 108 | 0.0072234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2939-37_0_10_line_113 |  | 108 | 109 | 0.0032604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2939-37_0_10_line_114 |  | 109 | 123 | 0.0042407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2939-37_0_10_line_115 |  | 110 | 111 | 0.0018949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_2939-37_0_10_line_116 |  | 110 | 112 | 0.0032804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_2939-37_0_10_line_117 |  | 111 | 113 | 0.0018221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_2939-37_0_10_line_118 |  | 112 | 114 | 0.021357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_2939-37_0_10_line_119 |  | 113 | 115 | 0.0063261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_2939-37_0_10_line_120 |  | 114 | 116 | 0.0030669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_2939-37_0_10_line_121 |  | 115 | 117 | 0.0047164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_2939-37_0_10_line_122 |  | 116 | 118 | 0.0019002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
123 | LV_2939-37_0_10_line_123 |  | 117 | 119 | 0.021718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_2939-37_0_10_line_124 |  | 118 | 120 | 0.020249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_2939-37_0_10_line_125 |  | 119 | 121 | 0.012234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_2939-37_0_10_line_126 |  | 119 | 122 | 0.012635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2939-37_0_10_line_127 |  | 120 | 129 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_2939-37_0_10_line_128 |  | 121 | 136 | 0.012731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2939-37_0_10_line_129 |  | 121 | 134 | 0.014412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_2939-37_0_10_line_130 |  | 122 | 145 | 0.01619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2939-37_0_10_line_131 |  | 123 | 124 | 0.039503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2939-37_0_10_line_132 |  | 124 | 125 | 0.00258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2939-37_0_10_line_133 |  | 125 | 138 | 0.0056978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2939-37_0_10_line_134 |  | 127 | 128 | 0.0013591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_2939-37_0_10_line_135 |  | 129 | 139 | 0.019829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_2939-37_0_10_line_136 |  | 129 | 140 | 0.005963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_2939-37_0_10_line_137 |  | 130 | 131 | 0.0029455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_2939-37_0_10_line_138 |  | 130 | 132 | 0.0046197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_2939-37_0_10_line_139 |  | 131 | 133 | 0.0099072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_2939-37_0_10_line_140 |  | 133 | 134 | 0.032525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
141 | LV_2939-37_0_10_line_141 |  | 134 | 135 | 0.028062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_2939-37_0_10_line_142 |  | 135 | 137 | 0.0078084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_2939-37_0_10_line_143 |  | 136 | 146 | 0.018144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_2939-37_0_10_line_144 |  | 137 | 138 | 0.0052265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_2939-37_0_10_line_145 |  | 139 | 141 | 0.013457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
146 | LV_2939-37_0_10_line_146 |  | 140 | 142 | 0.02189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_2939-37_0_10_line_147 |  | 140 | 143 | 0.013137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_2939-37_0_10_line_148 |  | 141 | 144 | 0.0053261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
149 | LV_2939-37_0_10_line_149 |  | 144 | 150 | 0.040807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
150 | LV_2939-37_0_10_line_150 |  | 145 | 147 | 0.036481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_2939-37_0_10_line_151 |  | 146 | 154 | 0.0060743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_2939-37_0_10_line_152 |  | 147 | 148 | 0.020614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_2939-37_0_10_line_153 |  | 148 | 149 | 0.0079808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_2939-37_0_10_line_154 |  | 149 | 153 | 0.020163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_2939-37_0_10_line_155 |  | 150 | 151 | 0.041881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
156 | LV_2939-37_0_10_line_156 |  | 150 | 152 | 0.056573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_2939-37_0_10_line_157 |  | 151 | 171 | 0.0033335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
158 | LV_2939-37_0_10_line_158 |  | 153 | 173 | 0.020552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_2939-37_0_10_line_159 |  | 154 | 175 | 0.00067595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_2939-37_0_10_line_160 |  | 155 | 174 | 0.019015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_2939-37_0_10_line_161 |  | 156 | 157 | 0.0071375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_2939-37_0_10_line_162 |  | 156 | 158 | 0.0012146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_2939-37_0_10_line_163 |  | 157 | 159 | 0.00908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_2939-37_0_10_line_164 |  | 158 | 160 | 0.0029482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_2939-37_0_10_line_165 |  | 159 | 161 | 0.0057037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_2939-37_0_10_line_166 |  | 160 | 162 | 0.027628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_2939-37_0_10_line_167 |  | 161 | 163 | 0.014902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_2939-37_0_10_line_168 |  | 162 | 164 | 0.001545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_2939-37_0_10_line_169 |  | 163 | 165 | 0.023018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_2939-37_0_10_line_170 |  | 165 | 168 | 0.0027869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_2939-37_0_10_line_171 |  | 166 | 167 | 0.0039734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_2939-37_0_10_line_172 |  | 166 | 168 | 0.034854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_2939-37_0_10_line_173 |  | 169 | 170 | 0.017759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
174 | LV_2939-37_0_10_line_174 |  | 170 | 171 | 0.033883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2939-37_0_10_trafo_91 | 0.63 MVA 20/0.4 kV | 176 | 102 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2691464.1255 | 1283394.413 | 2691462.8247 | 1283394.3996
1 | 2691460.0019 | 1283394.3704 | 2691462.8247 | 1283394.3996
2 | 2691438.5576 | 1283396.6205 | 2691446.5307 | 1283394.231 | 2691460.0019 | 1283394.3704
3 | 2691438.5576 | 1283396.6205 | 2691431.6102 | 1283380.3514
4 | 2691438.5576 | 1283396.6205 | 2691440.3994 | 1283407.2975
5 | 2691426.8212 | 1283369.1367 | 2691426.8212 | 1283369.1367 | 2691431.6102 | 1283380.3514
6 | 2691440.3994 | 1283407.2975 | 2691441.5814 | 1283414.1494 | 2691443.1325 | 1283441.0085
7 | 2691426.8212 | 1283369.1367 | 2691413.8583 | 1283348.8262
8 | 2691443.1325 | 1283441.0085 | 2691443.1836 | 1283441.8921
9 | 2691413.8583 | 1283348.8262 | 2691409.8018 | 1283342.4703
10 | 2691443.2941 | 1283443.8061 | 2691443.1836 | 1283441.8921
11 | 2691405.9531 | 1283336.4401 | 2691409.8018 | 1283342.4703
12 | 2691443.7883 | 1283452.3633 | 2691443.2941 | 1283443.8061
13 | 2691443.7883 | 1283452.3633 | 2691444.4927 | 1283464.5607 | 2691445.8466 | 1283469.7187
14 | 2691445.8466 | 1283469.7187 | 2691447.0118 | 1283474.1576
15 | 2691447.0118 | 1283474.1576 | 2691451.2533 | 1283490.3157
16 | 2691453.5554 | 1283499.086 | 2691451.2533 | 1283490.3157
17 | 2691454.6436 | 1283503.2313 | 2691453.5554 | 1283499.086
18 | 2691464.013 | 1283524.3288 | 2691455.4375 | 1283506.2558 | 2691454.6436 | 1283503.2313
19 | 2691474.548 | 1283540.8714 | 2691464.9902 | 1283526.3882 | 2691464.013 | 1283524.3288
20 | 2691474.548 | 1283540.8714 | 2691467.7804 | 1283543.0016 | 2691439.0892 | 1283550.9745 | 2691425.9832 | 1283552.2501 | 2691421.9564 | 1283551.805
21 | 2691474.548 | 1283540.8714 | 2691476.6664 | 1283543.2213
22 | 2691411.353 | 1283550.6329 | 2691421.9564 | 1283551.805
23 | 2691411.353 | 1283550.6329 | 2691403.6048 | 1283544.3517
24 | 2691403.6048 | 1283544.3517 | 2691407.0938 | 1283537.2329 | 2691406.7496 | 1283527.4858 | 2691403.1902 | 1283517.3775
25 | 2691403.6048 | 1283544.3517 | 2691366.0929 | 1283536.8722
26 | 2691432.2833 | 1283318.5711 | 2691442.5519 | 1283311.6023
27 | 2691424.6055 | 1283323.7817 | 2691432.2833 | 1283318.5711
28 | 2691451.0339 | 1283305.846 | 2691451.0339 | 1283305.846 | 2691442.5519 | 1283311.6023
29 | 2691405.9531 | 1283336.4401 | 2691424.6055 | 1283323.7817
30 | 2691451.0339 | 1283305.846 | 2691456.7714 | 1283298.7218
31 | 2691405.9531 | 1283336.4401 | 2691401.0577 | 1283331.6074
32 | 2691456.7714 | 1283298.7218 | 2691464.6941 | 1283288.8841
33 | 2691396.2462 | 1283326.8576 | 2691401.0577 | 1283331.6074
34 | 2691464.6941 | 1283288.8841 | 2691492.2737 | 1283254.6384
35 | 2691396.2462 | 1283326.8576 | 2691391.2004 | 1283321.8765 | 2691389.0639 | 1283320.1788
36 | 2691383.5922 | 1283315.8309 | 2691389.0639 | 1283320.1788
37 | 2691391.9234 | 1283492.9278 | 2691400.0836 | 1283508.5548 | 2691403.1902 | 1283517.3775
38 | 2691366.0929 | 1283536.8722 | 2691355.523 | 1283534.7646 | 2691350.6575 | 1283530.8166
39 | 2691270.2462 | 1283259.029 | 2691257.1376 | 1283263.5709 | 2691257.1376 | 1283263.5709
40 | 2691238.4321 | 1283279.7331 | 2691257.1376 | 1283263.5709
41 | 2691238.4321 | 1283279.7331 | 2691227.816 | 1283288.9058 | 2691222.5917 | 1283300.9354 | 2691223.4542 | 1283310.2843
42 | 2691223.8646 | 1283314.7338 | 2691223.4542 | 1283310.2843
43 | 2691223.8646 | 1283314.7338 | 2691233.2001 | 1283331.0986
44 | 2691223.8646 | 1283314.7338 | 2691219.4031 | 1283311.3161
45 | 2691303.988 | 1283308.1797 | 2691308.4972 | 1283293.8593 | 2691312.7228 | 1283287.7533
46 | 2691303.988 | 1283308.1797 | 2691303.988 | 1283308.1797 | 2691304.979 | 1283322.2295 | 2691311.7506 | 1283335.7683
47 | 2691233.2001 | 1283331.0986 | 2691239.6115 | 1283342.3375
48 | 2691219.4031 | 1283311.3161 | 2691219.1677 | 1283311.1358 | 2691206.4863 | 1283295.5394
49 | 2691312.5389 | 1283337.3445 | 2691311.7506 | 1283335.7683
50 | 2691312.5389 | 1283337.3445 | 2691326.2151 | 1283364.688
51 | 2691391.9234 | 1283492.9278 | 2691390.2048 | 1283489.6366
52 | 2691349.6724 | 1283530.0173 | 2691350.6575 | 1283530.8166
53 | 2691390.2048 | 1283489.6366 | 2691386.4058 | 1283482.3613
54 | 2691349.6724 | 1283530.0173 | 2691334.4805 | 1283517.6903
55 | 2691364.4339 | 1283440.2841 | 2691364.8367 | 1283441.0555
56 | 2691364.8367 | 1283441.0555 | 2691366.4298 | 1283444.1064
57 | 2691364.4339 | 1283440.2841 | 2691359.069 | 1283430.0102
58 | 2691369.3109 | 1283449.6239 | 2691366.4298 | 1283444.1064
59 | 2691351.7709 | 1283415.7831 | 2691354.7462 | 1283421.7318 | 2691359.069 | 1283430.0102
60 | 2691378.8503 | 1283467.8923 | 2691369.3109 | 1283449.6239
61 | 2691350.1911 | 1283412.6245 | 2691351.7709 | 1283415.7831
62 | 2691378.8503 | 1283467.8923 | 2691382.6803 | 1283475.2268
63 | 2691350.1911 | 1283412.6245 | 2691339.1433 | 1283390.536
64 | 2691385.3966 | 1283480.4286 | 2691382.6803 | 1283475.2268
65 | 2691337.6467 | 1283387.5439 | 2691339.1433 | 1283390.536
66 | 2691385.3966 | 1283480.4286 | 2691386.4058 | 1283482.3613
67 | 2691242.6837 | 1283347.7229 | 2691239.6115 | 1283342.3375
68 | 2691191.9877 | 1283277.7083 | 2691206.4863 | 1283295.5394
69 | 2691242.6837 | 1283347.7229 | 2691252.3581 | 1283364.6818
70 | 2691191.9877 | 1283277.7083 | 2691172.2059 | 1283159.6996
71 | 2691166.2365 | 1283318.3343 | 2691170.5529 | 1283311.1059 | 2691191.9877 | 1283277.7083
72 | 2691337.6467 | 1283387.5439 | 2691334.2606 | 1283380.7739
73 | 2691326.4881 | 1283365.2338 | 2691334.2606 | 1283380.7739
74 | 2691326.2151 | 1283364.688 | 2691326.4881 | 1283365.2338
75 | 2691293.3418 | 1283548.4085 | 2691304.4551 | 1283564.3666
76 | 2691293.3418 | 1283548.4085 | 2691288.9879 | 1283542.1565
77 | 2691288.9879 | 1283542.1565 | 2691283.3239 | 1283534.0232 | 2691283.3239 | 1283534.0232
78 | 2691283.2674 | 1283534.0777 | 2691283.3239 | 1283534.0232
79 | 2691283.2674 | 1283534.0777 | 2691279.1865 | 1283538.013
80 | 2691236.6443 | 1283655.8735 | 2691242.9083 | 1283656.193 | 2691257.0842 | 1283650.7744 | 2691252.2111 | 1283639.667 | 2691249.4969 | 1283633.6197 | 2691268.2786 | 1283617.8078 | 2691273.0125 | 1283610.7638 | 2691253.439 | 1283595.7922
81 | 2691221.6493 | 1283571.668 | 2691233.4782 | 1283578.1901 | 2691253.439 | 1283595.7922
82 | 2691253.439 | 1283595.7922 | 2691257.2606 | 1283566.2255
83 | 2691236.6443 | 1283655.8735 | 2691197.5265 | 1283624.5297 | 2691166.1963 | 1283603.2153 | 2691156.0999 | 1283597.2957
84 | 2691221.6493 | 1283571.668 | 2691210.976 | 1283549.6725 | 2691203.0424 | 1283540.6405
85 | 2691255.1082 | 1283561.2323 | 2691256.9949 | 1283563.5079 | 2691257.2606 | 1283566.2255
86 | 2691279.1865 | 1283538.013 | 2691278.4057 | 1283538.766
87 | 2691156.0999 | 1283597.2957 | 2691128.3484 | 1283581.0246
88 | 2691200.1215 | 1283537.3152 | 2691203.0424 | 1283540.6405
89 | 2691255.1082 | 1283561.2323 | 2691243.2689 | 1283548.3243
90 | 2691255.1082 | 1283561.2323 | 2691264.0813 | 1283552.5793
91 | 2691264.0813 | 1283552.5793 | 2691278.4057 | 1283538.766
92 | 2691332.0381 | 1283513.0665 | 2691334.4805 | 1283517.6903 | 2691334.4805 | 1283517.6903
93 | 2691332.0381 | 1283513.0665 | 2691324.0626 | 1283497.9674
94 | 2691324.0626 | 1283497.9674 | 2691323.7254 | 1283497.329
95 | 2691323.7254 | 1283497.329 | 2691311.6586 | 1283474.4844
96 | 2691309.8071 | 1283470.9791 | 2691311.6586 | 1283474.4844
97 | 2691255.1644 | 1283369.6012 | 2691252.3581 | 1283364.6818
98 | 2691255.1644 | 1283369.6012 | 2691264.7496 | 1283386.4037
99 | 2691269.9296 | 1283395.4839 | 2691264.7496 | 1283386.4037
100 | 2691269.9296 | 1283395.4839 | 2691262.6403 | 1283401.3021
101 | 2691269.9296 | 1283395.4839 | 2691275.0673 | 1283405.2106
102 | 2691275.0673 | 1283405.2106 | 2691278.7016 | 1283412.091
103 | 2691285.6129 | 1283425.1752 | 2691278.7016 | 1283412.091
104 | 2691298.5161 | 1283449.6033 | 2691290.5915 | 1283434.6006
105 | 2691298.5161 | 1283449.6033 | 2691300.9693 | 1283454.2477
106 | 2691285.6129 | 1283425.1752 | 2691290.5915 | 1283434.6006
107 | 2691301.9303 | 1283456.0671 | 2691300.9693 | 1283454.2477
108 | 2691301.9303 | 1283456.0671 | 2691309.8071 | 1283470.9791
109 | 2691106.0399 | 1283127.8328 | 2691172.2059 | 1283159.6996
110 | 2691166.2365 | 1283318.3343 | 2691162.956 | 1283324.2602
111 | 2691166.2365 | 1283318.3343 | 2691178.2508 | 1283330.7876
112 | 2691223.6008 | 1283432.4629 | 2691217.9553 | 1283436.9691
113 | 2691215.407 | 1283439.0031 | 2691217.9553 | 1283436.9691
114 | 2691215.407 | 1283439.0031 | 2691212.0927 | 1283441.6486
115 | 2691141.3673 | 1283455.3679 | 2691142.7528 | 1283456.6605
116 | 2691141.3673 | 1283455.3679 | 2691138.9687 | 1283453.1301
117 | 2691144.0852 | 1283457.9035 | 2691142.7528 | 1283456.6605
118 | 2691123.2891 | 1283438.6302 | 2691127.3929 | 1283442.3306 | 2691138.9687 | 1283453.1301
119 | 2691144.0852 | 1283457.9035 | 2691144.8595 | 1283458.626 | 2691146.1272 | 1283463.7382
120 | 2691123.2891 | 1283438.6302 | 2691121.0115 | 1283436.5764
121 | 2691146.1272 | 1283463.7382 | 2691147.2623 | 1283468.316
122 | 2691121.0115 | 1283436.5764 | 2691119.6003 | 1283435.3039
123 | 2691140.9815 | 1283488.9591 | 2691143.9556 | 1283483.0778 | 2691147.2623 | 1283468.316
124 | 2691104.5623 | 1283421.7438 | 2691119.6003 | 1283435.3039
125 | 2691151.3077 | 1283495.569 | 2691140.9815 | 1283488.9591
126 | 2691140.9815 | 1283488.9591 | 2691129.764 | 1283483.1435
127 | 2691092.778 | 1283416.8067 | 2691104.0533 | 1283421.2848 | 2691104.5623 | 1283421.7438
128 | 2691151.3077 | 1283495.569 | 2691145.5406 | 1283506.9188
129 | 2691163.2779 | 1283503.65 | 2691151.3077 | 1283495.569
130 | 2691129.764 | 1283483.1435 | 2691115.3909 | 1283475.692
131 | 2691197.8495 | 1283468.3985 | 2691190.618 | 1283458.7894 | 2691212.0927 | 1283441.6486
132 | 2691197.8495 | 1283468.3985 | 2691197.8495 | 1283468.3985 | 2691196.0431 | 1283470.2405
133 | 2691196.0431 | 1283470.2405 | 2691192.0535 | 1283474.3085
134 | 2691242.3502 | 1283547.3227 | 2691243.2689 | 1283548.3243
135 | 2691092.778 | 1283416.8067 | 2691101.0517 | 1283405.1689 | 2691103.7982 | 1283400.3461
136 | 2691092.778 | 1283416.8067 | 2691086.863 | 1283417.6938
137 | 2691195.1289 | 1283531.6314 | 2691197.0727 | 1283533.8444
138 | 2691200.1215 | 1283537.3152 | 2691197.0727 | 1283533.8444
139 | 2691195.1289 | 1283531.6314 | 2691192.5463 | 1283528.6913 | 2691187.9919 | 1283524.7946
140 | 2691163.2779 | 1283503.65 | 2691187.9919 | 1283524.7946
141 | 2691163.2779 | 1283503.65 | 2691182.9266 | 1283483.6149
142 | 2691188.394 | 1283478.04 | 2691182.9266 | 1283483.6149
143 | 2691137.3214 | 1283523.0945 | 2691145.5406 | 1283506.9188
144 | 2691188.394 | 1283478.04 | 2691192.0535 | 1283474.3085
145 | 2691108.9693 | 1283388.1504 | 2691108.422 | 1283392.227 | 2691103.7982 | 1283400.3461
146 | 2691086.863 | 1283417.6938 | 2691085.0497 | 1283409.2029 | 2691079.8783 | 1283401.8165 | 2691076.0655 | 1283400.0772
147 | 2691086.863 | 1283417.6938 | 2691079.2941 | 1283428.4307
148 | 2691109.6779 | 1283382.8716 | 2691108.9693 | 1283388.1504
149 | 2691081.6557 | 1283357.283 | 2691085.7451 | 1283364.2411 | 2691101.5706 | 1283369.6793 | 2691106.0719 | 1283373.3076 | 2691109.6779 | 1283382.8716 | 2691109.6779 | 1283382.8716
150 | 2691081.8159 | 1283461.4985 | 2691095.1551 | 1283466.509 | 2691110.7121 | 1283473.2664 | 2691115.3909 | 1283475.692
151 | 2691137.3214 | 1283523.0945 | 2691134.5698 | 1283528.5098
152 | 2691081.8159 | 1283461.4985 | 2691080.6355 | 1283482.0783
153 | 2691079.0687 | 1283489.8574 | 2691080.4693 | 1283484.9759 | 2691080.6355 | 1283482.0783
154 | 2691071.637 | 1283508.471 | 2691076.0571 | 1283500.3545 | 2691079.0687 | 1283489.8574
155 | 2691081.6557 | 1283357.283 | 2691091.122 | 1283355.9169 | 2691104.1305 | 1283353.6827 | 2691108.5571 | 1283352.9171 | 2691123.1721 | 1283353.4681
156 | 2691081.6557 | 1283357.283 | 2691074.5652 | 1283301.1564
157 | 2691123.1721 | 1283353.4681 | 2691126.5033 | 1283353.5937
158 | 2691071.637 | 1283508.471 | 2691074.3165 | 1283511.9265 | 2691069.1404 | 1283527.2552
159 | 2691134.2636 | 1283529.1125 | 2691134.5698 | 1283528.5098
160 | 2691128.3484 | 1283581.0246 | 2691118.7199 | 1283575.3792 | 2691112.7203 | 1283573.0066 | 2691111.3258 | 1283572.8667
161 | 2691171.1286 | 1283400.6123 | 2691173.9839 | 1283407.1537
162 | 2691171.1286 | 1283400.6123 | 2691170.6427 | 1283399.4991
163 | 2691181.6961 | 1283402.3614 | 2691173.9839 | 1283407.1537 | 2691173.9839 | 1283407.1537
164 | 2691169.4632 | 1283396.7971 | 2691170.6427 | 1283399.4991
165 | 2691186.5407 | 1283399.351 | 2691181.6961 | 1283402.3614
166 | 2691158.4107 | 1283371.4759 | 2691169.4632 | 1283396.7971
167 | 2691186.5407 | 1283399.351 | 2691199.1982 | 1283391.4857 | 2691199.1982 | 1283391.4857
168 | 2691157.7926 | 1283370.0599 | 2691158.4107 | 1283371.4759
169 | 2691199.1982 | 1283391.4857 | 2691193.5087 | 1283369.1824
170 | 2691193.5087 | 1283369.1824 | 2691192.8198 | 1283366.4819
171 | 2691180.3236 | 1283334.1251 | 2691179.1756 | 1283331.7461 | 2691178.2508 | 1283330.7876
172 | 2691180.3236 | 1283334.1251 | 2691189.3238 | 1283352.777 | 2691192.8198 | 1283366.4819
173 | 2691162.956 | 1283324.2602 | 2691154.3546 | 1283339.7977
174 | 2691126.5033 | 1283353.5937 | 2691136.0732 | 1283353.9545 | 2691143.1505 | 1283352.685 | 2691153.5767 | 1283341.2029 | 2691154.3546 | 1283339.7977

## bus_geodata
| x | y | coords
0 | 2691464.1255 | 1283394.413
1 | 2691462.8247 | 1283394.3996
2 | 2691460.0019 | 1283394.3704
3 | 2691438.5576 | 1283396.6205
4 | 2691431.6102 | 1283380.3514
5 | 2691440.3994 | 1283407.2975
6 | 2691426.8212 | 1283369.1367
7 | 2691443.1325 | 1283441.0085
8 | 2691413.8583 | 1283348.8262
9 | 2691443.1836 | 1283441.8921
10 | 2691409.8018 | 1283342.4703
11 | 2691443.2941 | 1283443.8061
12 | 2691443.7883 | 1283452.3633
13 | 2691445.8466 | 1283469.7187
14 | 2691447.0118 | 1283474.1576
15 | 2691451.2533 | 1283490.3157
16 | 2691454.6436 | 1283503.2313
17 | 2691453.5554 | 1283499.086
18 | 2691464.013 | 1283524.3288
19 | 2691474.548 | 1283540.8714
20 | 2691421.9564 | 1283551.805
21 | 2691476.6664 | 1283543.2213
22 | 2691411.353 | 1283550.6329
23 | 2691403.6048 | 1283544.3517
24 | 2691432.2833 | 1283318.5711
25 | 2691442.5519 | 1283311.6023
26 | 2691424.6055 | 1283323.7817
27 | 2691451.0339 | 1283305.846
28 | 2691405.9531 | 1283336.4401
29 | 2691456.7714 | 1283298.7218
30 | 2691401.0577 | 1283331.6074
31 | 2691464.6941 | 1283288.8841
32 | 2691396.2462 | 1283326.8576
33 | 2691492.2737 | 1283254.6384
34 | 2691389.0639 | 1283320.1788
35 | 2691403.1902 | 1283517.3775
36 | 2691366.0929 | 1283536.8722
37 | 2691270.2462 | 1283259.029
38 | 2691257.1376 | 1283263.5709
39 | 2691238.4321 | 1283279.7331
40 | 2691223.4542 | 1283310.2843
41 | 2691223.8646 | 1283314.7338
42 | 2691312.7228 | 1283287.7533
43 | 2691303.988 | 1283308.1797
44 | 2691383.5922 | 1283315.8309
45 | 2691233.2001 | 1283331.0986
46 | 2691219.4031 | 1283311.3161
47 | 2691311.7506 | 1283335.7683
48 | 2691312.5389 | 1283337.3445
49 | 2691391.9234 | 1283492.9278
50 | 2691350.6575 | 1283530.8166
51 | 2691390.2048 | 1283489.6366
52 | 2691349.6724 | 1283530.0173
53 | 2691364.8367 | 1283441.0555
54 | 2691364.4339 | 1283440.2841
55 | 2691366.4298 | 1283444.1064
56 | 2691359.069 | 1283430.0102
57 | 2691369.3109 | 1283449.6239
58 | 2691351.7709 | 1283415.7831
59 | 2691378.8503 | 1283467.8923
60 | 2691350.1911 | 1283412.6245
61 | 2691382.6803 | 1283475.2268
62 | 2691339.1433 | 1283390.536
63 | 2691385.3966 | 1283480.4286
64 | 2691239.6115 | 1283342.3375
65 | 2691206.4863 | 1283295.5394
66 | 2691242.6837 | 1283347.7229
67 | 2691191.9877 | 1283277.7083
68 | 2691386.4058 | 1283482.3613
69 | 2691337.6467 | 1283387.5439
70 | 2691334.2606 | 1283380.7739
71 | 2691326.4881 | 1283365.2338
72 | 2691326.2151 | 1283364.688
73 | 2691293.3418 | 1283548.4085
74 | 2691304.4551 | 1283564.3666
75 | 2691288.9879 | 1283542.1565
76 | 2691283.3239 | 1283534.0232
77 | 2691283.2674 | 1283534.0777
78 | 2691253.439 | 1283595.7922
79 | 2691236.6443 | 1283655.8735
80 | 2691221.6493 | 1283571.668
81 | 2691257.2606 | 1283566.2255
82 | 2691279.1865 | 1283538.013
83 | 2691156.0999 | 1283597.2957
84 | 2691203.0424 | 1283540.6405
85 | 2691255.1082 | 1283561.2323
86 | 2691278.4057 | 1283538.766
87 | 2691334.4805 | 1283517.6903
88 | 2691332.0381 | 1283513.0665
89 | 2691324.0626 | 1283497.9674
90 | 2691323.7254 | 1283497.329
91 | 2691311.6586 | 1283474.4844
92 | 2691252.3581 | 1283364.6818
93 | 2691255.1644 | 1283369.6012
94 | 2691264.7496 | 1283386.4037
95 | 2691269.9296 | 1283395.4839
96 | 2691262.6403 | 1283401.3021
97 | 2691275.0673 | 1283405.2106
98 | 2691278.7016 | 1283412.091
99 | 2691298.5161 | 1283449.6033
100 | 2691290.5915 | 1283434.6006
101 | 2691300.9693 | 1283454.2477
102 | 2691285.6129 | 1283425.1752
103 | 2691301.9303 | 1283456.0671
104 | 2691309.8071 | 1283470.9791
105 | 2691172.2059 | 1283159.6996
106 | 2691166.2365 | 1283318.3343
107 | 2691223.6008 | 1283432.4629
108 | 2691217.9553 | 1283436.9691
109 | 2691215.407 | 1283439.0031
110 | 2691141.3673 | 1283455.3679
111 | 2691142.7528 | 1283456.6605
112 | 2691138.9687 | 1283453.1301
113 | 2691144.0852 | 1283457.9035
114 | 2691123.2891 | 1283438.6302
115 | 2691146.1272 | 1283463.7382
116 | 2691121.0115 | 1283436.5764
117 | 2691147.2623 | 1283468.316
118 | 2691119.6003 | 1283435.3039
119 | 2691140.9815 | 1283488.9591
120 | 2691104.5623 | 1283421.7438
121 | 2691151.3077 | 1283495.569
122 | 2691129.764 | 1283483.1435
123 | 2691212.0927 | 1283441.6486
124 | 2691197.8495 | 1283468.3985
125 | 2691196.0431 | 1283470.2405
126 | 2691264.0813 | 1283552.5793
127 | 2691243.2689 | 1283548.3243
128 | 2691242.3502 | 1283547.3227
129 | 2691092.778 | 1283416.8067
130 | 2691197.0727 | 1283533.8444
131 | 2691195.1289 | 1283531.6314
132 | 2691200.1215 | 1283537.3152
133 | 2691187.9919 | 1283524.7946
134 | 2691163.2779 | 1283503.65
135 | 2691182.9266 | 1283483.6149
136 | 2691145.5406 | 1283506.9188
137 | 2691188.394 | 1283478.04
138 | 2691192.0535 | 1283474.3085
139 | 2691103.7982 | 1283400.3461
140 | 2691086.863 | 1283417.6938
141 | 2691108.9693 | 1283388.1504
142 | 2691076.0655 | 1283400.0772
143 | 2691079.2941 | 1283428.4307
144 | 2691109.6779 | 1283382.8716
145 | 2691115.3909 | 1283475.692
146 | 2691137.3214 | 1283523.0945
147 | 2691081.8159 | 1283461.4985
148 | 2691080.6355 | 1283482.0783
149 | 2691079.0687 | 1283489.8574
150 | 2691081.6557 | 1283357.283
151 | 2691123.1721 | 1283353.4681
152 | 2691074.5652 | 1283301.1564
153 | 2691071.637 | 1283508.471
154 | 2691134.5698 | 1283528.5098
155 | 2691128.3484 | 1283581.0246
156 | 2691171.1286 | 1283400.6123
157 | 2691173.9839 | 1283407.1537
158 | 2691170.6427 | 1283399.4991
159 | 2691181.6961 | 1283402.3614
160 | 2691169.4632 | 1283396.7971
161 | 2691186.5407 | 1283399.351
162 | 2691158.4107 | 1283371.4759
163 | 2691199.1982 | 1283391.4857
164 | 2691157.7926 | 1283370.0599
165 | 2691193.5087 | 1283369.1824
166 | 2691180.3236 | 1283334.1251
167 | 2691178.2508 | 1283330.7876
168 | 2691192.8198 | 1283366.4819
169 | 2691162.956 | 1283324.2602
170 | 2691154.3546 | 1283339.7977
171 | 2691126.5033 | 1283353.5937
172 | 2691106.0399 | 1283127.8328
173 | 2691069.1404 | 1283527.2552
174 | 2691111.3258 | 1283572.8667
175 | 2691134.2636 | 1283529.1125
176 | 2691269.9296 | 1283395.4839

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1