## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_306-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_306-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_306-15_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_306-15_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_306-15_0_4_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_306-15_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_306-15_0_4_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_306-15_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_306-15_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_306-15_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_306-15_0_4_node_114 | 0.4 | n |  | TRUE
11 | bus_LV_306-15_0_4_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_306-15_0_4_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_306-15_0_4_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_306-15_0_4_node_69 | 0.4 | n |  | TRUE
15 | bus_LV_306-15_0_4_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_306-15_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_306-15_0_4_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_306-15_0_4_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_306-15_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_306-15_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_306-15_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_306-15_0_4_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_306-15_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_306-15_0_4_node_83 | 0.4 | n |  | TRUE
25 | bus_LV_306-15_0_4_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_306-15_0_4_node_91 | 0.4 | n |  | TRUE
27 | bus_LV_306-15_0_4_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_306-15_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_306-15_0_4_node_80 | 0.4 | n |  | TRUE
30 | bus_LV_306-15_0_4_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_306-15_0_4_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_306-15_0_4_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_306-15_0_4_node_76 | 0.4 | n |  | TRUE
34 | bus_LV_306-15_0_4_node_68 | 0.4 | n |  | TRUE
35 | bus_LV_306-15_0_4_node_98 | 0.4 | n |  | TRUE
36 | bus_LV_306-15_0_4_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_306-15_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_306-15_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_306-15_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_306-15_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_306-15_0_4_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_306-15_0_4_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_306-15_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_306-15_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_306-15_0_4_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_306-15_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_306-15_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_306-15_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_306-15_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_306-15_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_306-15_0_4_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_306-15_0_4_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_306-15_0_4_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_306-15_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_306-15_0_4_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_306-15_0_4_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_306-15_0_4_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_306-15_0_4_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_306-15_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_306-15_0_4_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_306-15_0_4_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_306-15_0_4_node_58 | 0.4 | n |  | TRUE
63 | bus_LV_306-15_0_4_node_59 | 0.4 | n |  | TRUE
64 | bus_LV_306-15_0_4_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_306-15_0_4_node_61 | 0.4 | n |  | TRUE
66 | bus_LV_306-15_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_306-15_0_4_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_306-15_0_4_node_64 | 0.4 | n |  | TRUE
69 | bus_LV_306-15_0_4_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_306-15_0_4_node_66 | 0.4 | n |  | TRUE
71 | bus_LV_306-15_0_4_node_67 | 0.4 | n |  | TRUE
72 | bus_LV_306-15_0_4_node_73 | 0.4 | n |  | TRUE
73 | bus_LV_306-15_0_4_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_306-15_0_4_node_71 | 0.4 | n |  | TRUE
75 | bus_LV_306-15_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_306-15_0_4_node_75 | 0.4 | n |  | TRUE
77 | bus_LV_306-15_0_4_node_77 | 0.4 | n |  | TRUE
78 | bus_LV_306-15_0_4_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_306-15_0_4_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_306-15_0_4_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_306-15_0_4_node_85 | 0.4 | n |  | TRUE
82 | bus_LV_306-15_0_4_node_86 | 0.4 | n |  | TRUE
83 | bus_LV_306-15_0_4_node_87 | 0.4 | n |  | TRUE
84 | bus_LV_306-15_0_4_node_88 | 0.4 | n |  | TRUE
85 | bus_LV_306-15_0_4_node_89 | 0.4 | n |  | TRUE
86 | bus_LV_306-15_0_4_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_306-15_0_4_node_110 | 0.4 | n |  | TRUE
88 | bus_LV_306-15_0_4_node_97 | 0.4 | n |  | TRUE
89 | bus_LV_306-15_0_4_node_103 | 0.4 | n |  | TRUE
90 | bus_LV_306-15_0_4_node_111 | 0.4 | n |  | TRUE
91 | bus_LV_306-15_0_4_node_109 | 0.4 | n |  | TRUE
92 | bus_LV_306-15_0_4_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_306-15_0_4_node_101 | 0.4 | n |  | TRUE
94 | bus_LV_306-15_0_4_node_92 | 0.4 | n |  | TRUE
95 | bus_LV_306-15_0_4_node_93 | 0.4 | n |  | TRUE
96 | bus_LV_306-15_0_4_node_94 | 0.4 | n |  | TRUE
97 | bus_LV_306-15_0_4_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_306-15_0_4_node_108 | 0.4 | n |  | TRUE
99 | bus_LV_306-15_0_4_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_306-15_0_4_node_100 | 0.4 | n |  | TRUE
101 | bus_LV_306-15_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_306-15_0_4_node_104 | 0.4 | n |  | TRUE
103 | bus_LV_306-15_0_4_node_105 | 0.4 | n |  | TRUE
104 | bus_LV_306-15_0_4_node_107 | 0.4 | n |  | TRUE
105 | bus_LV_306-15_0_4_node_112 | 0.4 | n |  | TRUE
106 | bus_LV_306-15_0_4_node_113 | 0.4 | n |  | TRUE
107 | bus_MV_404_0_node_17 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_306-15_0_4_load_0 | 0 | 0.0071649 | 0.0017957 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_306-15_0_4_load_6 | 4 | 0.010904 | 0.0027328 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_306-15_0_4_load_9 | 7 | 0.012916 | 0.0032371 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_306-15_0_4_load_10 | 8 | 0.0030582 | 0.00076646 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_306-15_0_4_load_114 | 10 | 0.0025624 | 0.00064219 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_306-15_0_4_load_31 | 11 | 0.0061223 | 0.0015344 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_306-15_0_4_load_40 | 13 | 0.0029579 | 0.00074132 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_306-15_0_4_load_16 | 15 | 0.030837 | 0.0077285 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_306-15_0_4_load_52 | 17 | 0.0028189 | 0.00070649 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_306-15_0_4_load_33 | 18 | 0.016539 | 0.0041451 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_306-15_0_4_load_11 | 20 | 0.0073967 | 0.0018538 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_306-15_0_4_load_23 | 23 | 0.031138 | 0.007804 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_306-15_0_4_load_83 | 24 | 0.0040839 | 0.0010235 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_306-15_0_4_load_22 | 28 | 0.0014418 | 0.00036136 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_306-15_0_4_load_78 | 30 | 0.0067315 | 0.0016871 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_306-15_0_4_load_19 | 31 | 0.0054262 | 0.0013599 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_306-15_0_4_load_76 | 33 | 0.0055271 | 0.0013852 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_306-15_0_4_load_68 | 34 | 0.0041627 | 0.0010433 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_306-15_0_4_load_98 | 35 | 0.0030449 | 0.00076313 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_306-15_0_4_load_26 | 36 | 0.0022555 | 0.00056529 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_306-15_0_4_load_27 | 37 | 0.0027506 | 0.00068937 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_306-15_0_4_load_30 | 39 | 0.0027497 | 0.00068914 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_306-15_0_4_load_32 | 40 | 0.0026178 | 0.00065609 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_306-15_0_4_load_34 | 41 | 0.0022096 | 0.00055378 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_306-15_0_4_load_45 | 42 | 0.0028051 | 0.00070301 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_306-15_0_4_load_43 | 43 | 0.0021782 | 0.00054592 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_306-15_0_4_load_41 | 44 | 0.0027059 | 0.00067817 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_306-15_0_4_load_44 | 45 | 0.0022087 | 0.00055355 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_306-15_0_4_load_35 | 46 | 0.0024348 | 0.00061023 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_306-15_0_4_load_36 | 47 | 0.0023204 | 0.00058154 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_306-15_0_4_load_38 | 48 | 0.002826 | 0.00070827 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_306-15_0_4_load_39 | 49 | 0.0034728 | 0.00087036 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_306-15_0_4_load_42 | 50 | 0.0020222 | 0.00050681 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_306-15_0_4_load_48 | 52 | 0.0033948 | 0.00085082 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_306-15_0_4_load_49 | 53 | 0.0023105 | 0.00057907 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_306-15_0_4_load_46 | 54 | 0.0021478 | 0.00053829 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_306-15_0_4_load_50 | 55 | 0.002123 | 0.00053207 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_306-15_0_4_load_51 | 56 | 0.0062694 | 0.0015713 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_306-15_0_4_load_53 | 57 | 0.0028457 | 0.00071319 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_306-15_0_4_load_54 | 58 | 0.0038886 | 0.00097458 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_306-15_0_4_load_55 | 59 | 0.0032801 | 0.00082206 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_306-15_0_4_load_56 | 60 | 0.0073771 | 0.0018489 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_306-15_0_4_load_57 | 61 | 0.0027898 | 0.00069918 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_306-15_0_4_load_58 | 62 | 0.0030594 | 0.00076676 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_306-15_0_4_load_59 | 63 | 0.0027453 | 0.00068803 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_306-15_0_4_load_60 | 64 | 0.0032334 | 0.00081036 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_306-15_0_4_load_61 | 65 | 0.0027819 | 0.0006972 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_306-15_0_4_load_62 | 66 | 0.0032883 | 0.00082413 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_306-15_0_4_load_63 | 67 | 0.0084026 | 0.0021059 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_306-15_0_4_load_64 | 68 | 0.0017612 | 0.00044139 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_306-15_0_4_load_65 | 69 | 0.0046683 | 0.00117 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_306-15_0_4_load_66 | 70 | 0.0040143 | 0.0010061 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_306-15_0_4_load_67 | 71 | 0.0026327 | 0.00065981 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_306-15_0_4_load_70 | 73 | 0.0025911 | 0.0006494 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_306-15_0_4_load_71 | 74 | 0.0070828 | 0.0017751 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_306-15_0_4_load_72 | 75 | 0.0010175 | 0.00025502 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_306-15_0_4_load_77 | 77 | 0.0015672 | 0.00039278 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_306-15_0_4_load_79 | 78 | 0.0011795 | 0.00029561 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_306-15_0_4_load_81 | 79 | 0.0024131 | 0.00060477 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_306-15_0_4_load_84 | 80 | 0.002125 | 0.00053257 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_306-15_0_4_load_85 | 81 | 0.0064294 | 0.0016114 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_306-15_0_4_load_86 | 82 | 0.0031401 | 0.00078697 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_306-15_0_4_load_88 | 84 | 0.0032079 | 0.00080399 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_306-15_0_4_load_89 | 85 | 0.001769 | 0.00044336 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_306-15_0_4_load_90 | 86 | 0.0052246 | 0.0013094 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_306-15_0_4_load_110 | 87 | 0.0021393 | 0.00053616 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_306-15_0_4_load_103 | 89 | 0.0034364 | 0.00086124 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_306-15_0_4_load_111 | 90 | 0.0036725 | 0.00092042 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_306-15_0_4_load_109 | 91 | 0.0041378 | 0.001037 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_306-15_0_4_load_95 | 92 | 0.0033412 | 0.00083738 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_306-15_0_4_load_101 | 93 | 0.0090141 | 0.0022591 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_306-15_0_4_load_92 | 94 | 0.0038775 | 0.0009718 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_306-15_0_4_load_93 | 95 | 0.00056798 | 0.00014235 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_306-15_0_4_load_94 | 96 | 0.00069114 | 0.00017322 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_306-15_0_4_load_96 | 97 | 0.0057517 | 0.0014415 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_306-15_0_4_load_108 | 98 | 0.00089826 | 0.00022512 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_306-15_0_4_load_99 | 99 | 0.0068309 | 0.001712 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_306-15_0_4_load_100 | 100 | 0.012394 | 0.0031063 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_306-15_0_4_load_102 | 101 | 0.012256 | 0.0030717 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_306-15_0_4_load_104 | 102 | 0.00040663 | 0.00010191 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_306-15_0_4_load_105 | 103 | 0.00049574 | 0.00012425 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_306-15_0_4_load_107 | 104 | 0.00060611 | 0.00015191 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_306-15_0_4_load_112 | 105 | 0.0019213 | 0.00048152 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_306-15_0_4_load_113 | 106 | 0.0085183 | 0.0021349 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_306-15_0_4_line_0 |  | 0 | 1 | 0.044485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_306-15_0_4_line_1 |  | 0 | 2 | 0.017762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_306-15_0_4_line_2 |  | 1 | 3 | 0.028863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_306-15_0_4_line_3 |  | 2 | 4 | 0.039793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_306-15_0_4_line_4 |  | 2 | 5 | 0.032276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_306-15_0_4_line_5 |  | 3 | 6 | 0.008028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_306-15_0_4_line_6 |  | 3 | 7 | 0.028942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_306-15_0_4_line_7 |  | 4 | 8 | 0.028624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_306-15_0_4_line_8 |  | 5 | 9 | 0.039437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_306-15_0_4_line_9 |  | 6 | 10 | 0.042504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_306-15_0_4_line_10 |  | 7 | 11 | 0.018446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_306-15_0_4_line_11 |  | 8 | 19 | 0.041098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_306-15_0_4_line_12 |  | 9 | 22 | 0.066194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_306-15_0_4_line_13 |  | 9 | 23 | 0.030119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_306-15_0_4_line_14 |  | 10 | 26 | 0.025247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_306-15_0_4_line_15 |  | 11 | 27 | 0.011811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
16 | LV_306-15_0_4_line_16 |  | 12 | 13 | 0.024366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_306-15_0_4_line_17 |  | 12 | 14 | 0.035108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_306-15_0_4_line_18 |  | 13 | 32 | 0.012039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_306-15_0_4_line_19 |  | 14 | 33 | 0.076981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_306-15_0_4_line_20 |  | 14 | 34 | 0.015696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_306-15_0_4_line_21 |  | 15 | 16 | 0.02047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_306-15_0_4_line_22 |  | 16 | 31 | 0.024623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_306-15_0_4_line_23 |  | 16 | 22 | 0.030154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_306-15_0_4_line_24 |  | 17 | 18 | 0.0037761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_306-15_0_4_line_25 |  | 18 | 38 | 0.010343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_306-15_0_4_line_26 |  | 19 | 21 | 0.071153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_306-15_0_4_line_27 |  | 19 | 25 | 0.025956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_306-15_0_4_line_28 |  | 20 | 21 | 0.053132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_306-15_0_4_line_29 |  | 22 | 28 | 0.031682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_306-15_0_4_line_30 |  | 24 | 25 | 0.037778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_306-15_0_4_line_31 |  | 25 | 29 | 0.025623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_306-15_0_4_line_32 |  | 26 | 89 | 0.017212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_306-15_0_4_line_33 |  | 26 | 84 | 0.032266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_306-15_0_4_line_34 |  | 27 | 39 | 0.016185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_306-15_0_4_line_35 |  | 27 | 36 | 0.012585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_306-15_0_4_line_36 |  | 28 | 35 | 0.006389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_306-15_0_4_line_37 |  | 29 | 30 | 0.06045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_306-15_0_4_line_38 |  | 30 | 78 | 0.014378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_306-15_0_4_line_39 |  | 32 | 46 | 0.017781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_306-15_0_4_line_40 |  | 33 | 72 | 0.021539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_306-15_0_4_line_41 |  | 34 | 71 | 0.024726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_306-15_0_4_line_42 |  | 36 | 37 | 0.0013313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_306-15_0_4_line_43 |  | 37 | 38 | 0.016846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_306-15_0_4_line_44 |  | 38 | 40 | 0.014761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_306-15_0_4_line_45 |  | 39 | 41 | 0.0049931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_306-15_0_4_line_46 |  | 40 | 42 | 0.0061779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_306-15_0_4_line_47 |  | 41 | 43 | 0.0070575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_306-15_0_4_line_48 |  | 42 | 44 | 0.0083883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_306-15_0_4_line_49 |  | 43 | 45 | 0.0049911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_306-15_0_4_line_50 |  | 44 | 48 | 0.0062374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_306-15_0_4_line_51 |  | 45 | 54 | 0.0049564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_306-15_0_4_line_52 |  | 46 | 47 | 0.0062735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_306-15_0_4_line_53 |  | 47 | 48 | 0.0062468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_306-15_0_4_line_54 |  | 49 | 50 | 0.0031016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_306-15_0_4_line_55 |  | 50 | 51 | 0.010118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_306-15_0_4_line_56 |  | 51 | 52 | 0.017035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_306-15_0_4_line_57 |  | 51 | 53 | 0.017874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_306-15_0_4_line_58 |  | 52 | 56 | 0.013268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_306-15_0_4_line_59 |  | 53 | 55 | 0.0050441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_306-15_0_4_line_60 |  | 54 | 55 | 0.0048589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_306-15_0_4_line_61 |  | 56 | 57 | 0.018244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_306-15_0_4_line_62 |  | 56 | 58 | 0.016754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_306-15_0_4_line_63 |  | 57 | 59 | 0.00027933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_306-15_0_4_line_64 |  | 58 | 60 | 0.0050976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_306-15_0_4_line_65 |  | 59 | 61 | 0.0060573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_306-15_0_4_line_66 |  | 61 | 62 | 0.00011088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_306-15_0_4_line_67 |  | 62 | 63 | 0.0061128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_306-15_0_4_line_68 |  | 63 | 64 | 8.7203e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_306-15_0_4_line_69 |  | 64 | 65 | 0.0062069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_306-15_0_4_line_70 |  | 65 | 66 | 0.00013497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_306-15_0_4_line_71 |  | 66 | 67 | 0.0047641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_306-15_0_4_line_72 |  | 68 | 69 | 0.014277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_306-15_0_4_line_73 |  | 68 | 70 | 0.075787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_306-15_0_4_line_74 |  | 69 | 71 | 0.0068725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_306-15_0_4_line_75 |  | 72 | 76 | 0.017938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_306-15_0_4_line_76 |  | 72 | 74 | 0.03911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_306-15_0_4_line_77 |  | 73 | 74 | 0.0049495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_306-15_0_4_line_78 |  | 73 | 75 | 0.016911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_306-15_0_4_line_79 |  | 76 | 77 | 0.0297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_306-15_0_4_line_80 |  | 78 | 79 | 0.02855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_306-15_0_4_line_81 |  | 80 | 81 | 0.023037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_306-15_0_4_line_82 |  | 80 | 82 | 0.0065022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_306-15_0_4_line_83 |  | 81 | 83 | 0.0098954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_306-15_0_4_line_84 |  | 82 | 84 | 0.020324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_306-15_0_4_line_85 |  | 83 | 85 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_306-15_0_4_line_86 |  | 83 | 86 | 0.025428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_306-15_0_4_line_87 |  | 85 | 87 | 0.016222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_306-15_0_4_line_88 |  | 86 | 88 | 0.0222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_306-15_0_4_line_89 |  | 87 | 90 | 0.0069383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_306-15_0_4_line_90 |  | 88 | 91 | 0.01792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_306-15_0_4_line_91 |  | 88 | 92 | 0.013321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_306-15_0_4_line_92 |  | 89 | 93 | 0.025429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_306-15_0_4_line_93 |  | 90 | 105 | 0.001976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_306-15_0_4_line_94 |  | 91 | 98 | 0.037242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_306-15_0_4_line_95 |  | 92 | 95 | 0.011467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_306-15_0_4_line_96 |  | 93 | 99 | 0.0070587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_306-15_0_4_line_97 |  | 94 | 95 | 0.014669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_306-15_0_4_line_98 |  | 94 | 96 | 0.012301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_306-15_0_4_line_99 |  | 96 | 97 | 0.0077265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_306-15_0_4_line_100 |  | 98 | 104 | 0.02219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_306-15_0_4_line_101 |  | 99 | 100 | 0.028441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_306-15_0_4_line_102 |  | 100 | 101 | 0.015555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_306-15_0_4_line_103 |  | 102 | 103 | 0.016558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_306-15_0_4_line_104 |  | 103 | 104 | 0.004152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_306-15_0_4_line_105 |  | 105 | 106 | 0.011676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_306-15_0_4_trafo_9 | 0.63 MVA 20/0.4 kV | 107 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2590276.7232 | 1214210.2182 | 2590282.3287 | 1214206.0511 | 2590311.9546 | 1214183.061
1 | 2590325.9872 | 1214172.1716 | 2590311.9546 | 1214183.061
2 | 2590276.7232 | 1214210.2182 | 2590285.2161 | 1214216.2187 | 2590294.4221 | 1214221.7401 | 2590301.4677 | 1214225.0637
3 | 2590325.9872 | 1214172.1716 | 2590344.3615 | 1214183.3478 | 2590361.3057 | 1214190.2247
4 | 2590347.8054 | 1214148.3336 | 2590325.9872 | 1214172.1716
5 | 2590301.4677 | 1214225.0637 | 2590308.7715 | 1214228.4425
6 | 2590301.4677 | 1214225.0637 | 2590295.0978 | 1214230.8441 | 2590279.0406 | 1214243.3293
7 | 2590361.3057 | 1214190.2247 | 2590380.5657 | 1214198.0415 | 2590387.6661 | 1214201.361
8 | 2590356.3982 | 1214113.1665 | 2590360.7508 | 1214118.3956 | 2590355.2723 | 1214130.6448 | 2590349.9174 | 1214144.15 | 2590347.8054 | 1214148.3336
9 | 2590308.7715 | 1214228.4425 | 2590308.2552 | 1214242.429 | 2590325.104 | 1214265.4249
10 | 2590264.4782 | 1214254.6522 | 2590279.0406 | 1214243.3293
11 | 2590408.8599 | 1214233.6823 | 2590398.434 | 1214206.395 | 2590387.6661 | 1214201.361
12 | 2590356.3982 | 1214113.1665 | 2590332.9842 | 1214085.4669 | 2590312.8447 | 1214063.2318
13 | 2590356.3982 | 1214113.1665 | 2590380.1594 | 1214094.6586
14 | 2590340.0254 | 1214285.7903 | 2590325.104 | 1214265.4249
15 | 2590256.5427 | 1214245.9048 | 2590264.4782 | 1214254.6522
16 | 2590161.1191 | 1214232.5887 | 2590163.9553 | 1214234.6629 | 2590176.9578 | 1214250.9646
17 | 2590161.1191 | 1214232.5887 | 2590148.3922 | 1214265.3172
18 | 2590184.4651 | 1214260.3766 | 2590176.9578 | 1214250.9646
19 | 2590148.3922 | 1214265.3172 | 2590140.9615 | 1214281.5498 | 2590135.1431 | 1214294.5446 | 2590126.817 | 1214311.1123 | 2590111.4383 | 1214332.5073
20 | 2590148.3922 | 1214265.3172 | 2590152.8689 | 1214267.4554 | 2590158.7203 | 1214276.4548
21 | 2590290.3673 | 1214083.4022 | 2590284.4281 | 1214087.9479 | 2590273.9723 | 1214095.6578
22 | 2590290.3673 | 1214083.4022 | 2590287.7693 | 1214078.4037 | 2590285.9179 | 1214074.8492 | 2590284.6532 | 1214072.4277 | 2590279.001 | 1214061.5593
23 | 2590290.3673 | 1214083.4022 | 2590312.8447 | 1214063.2318
24 | 2590228.8441 | 1214210.5914 | 2590231.2122 | 1214213.5326
25 | 2590237.6987 | 1214221.5889 | 2590231.2122 | 1214213.5326
26 | 2590408.8599 | 1214233.6823 | 2590413.8545 | 1214232.0955 | 2590419.3822 | 1214231.4084 | 2590426.8094 | 1214231.3074 | 2590436.6667 | 1214231.1358 | 2590442.2856 | 1214230.4819 | 2590446.8558 | 1214229.4295 | 2590453.0338 | 1214227.0181 | 2590458.8989 | 1214223.6846 | 2590463.9589 | 1214220.2523 | 2590474.4795 | 1214212.253
27 | 2590396.9117 | 1214255.7363 | 2590397.9674 | 1214251.1209 | 2590399.1678 | 1214246.7053 | 2590400.6046 | 1214242.9564 | 2590402.1338 | 1214239.9189 | 2590403.7936 | 1214237.8484 | 2590406.0912 | 1214235.6545 | 2590408.8599 | 1214233.6823
28 | 2590474.4795 | 1214212.253 | 2590466.0148 | 1214204.7847 | 2590432.6108 | 1214179.5839
29 | 2590312.8447 | 1214063.2318 | 2590335.619 | 1214041.2079
30 | 2590396.9117 | 1214255.7363 | 2590387.4388 | 1214254.1063 | 2590376.111 | 1214251.3343 | 2590360.407 | 1214246.2588
31 | 2590396.9117 | 1214255.7363 | 2590408.2914 | 1214257.7412 | 2590412.7281 | 1214258.7012 | 2590416.2003 | 1214259.6628 | 2590419.2097 | 1214260.8697 | 2590421.7101 | 1214262.0218
32 | 2590340.0254 | 1214285.7903 | 2590331.0196 | 1214300.4577
33 | 2590340.0254 | 1214285.7903 | 2590357.7587 | 1214309.3524 | 2590359.0987 | 1214311.7833
34 | 2590256.5427 | 1214245.9048 | 2590243.8465 | 1214255.9428
35 | 2590256.5427 | 1214245.9048 | 2590248.8335 | 1214235.957
36 | 2590335.619 | 1214041.2079 | 2590340.2117 | 1214036.7665
37 | 2590421.7101 | 1214262.0218 | 2590419.6291 | 1214266.5833 | 2590419.276 | 1214268.9741 | 2590419.2869 | 1214270.9975 | 2590419.6862 | 1214273.7317 | 2590421.3088 | 1214276.7975 | 2590435.6147 | 1214294.3731 | 2590449.8563 | 1214311.2755
38 | 2590449.8563 | 1214311.2755 | 2590459.1205 | 1214322.2705
39 | 2590184.4651 | 1214260.3766 | 2590198.8357 | 1214249.9057
40 | 2590094.8416 | 1214345.5184 | 2590107.0872 | 1214338.5607 | 2590111.4383 | 1214332.5073
41 | 2590158.7203 | 1214276.4548 | 2590172.1989 | 1214297.1846
42 | 2590248.018 | 1214234.9047 | 2590248.8335 | 1214235.957
43 | 2590237.6987 | 1214221.5889 | 2590248.018 | 1214234.9047
44 | 2590237.6987 | 1214221.5889 | 2590225.7686 | 1214230.2816
45 | 2590243.8465 | 1214255.9428 | 2590239.9297 | 1214259.0396
46 | 2590225.7686 | 1214230.2816 | 2590220.7755 | 1214233.9197
47 | 2590234.3935 | 1214263.4167 | 2590239.9297 | 1214259.0396
48 | 2590213.996 | 1214238.8595 | 2590220.7755 | 1214233.9197
49 | 2590230.4783 | 1214266.5122 | 2590234.3935 | 1214263.4167
50 | 2590213.996 | 1214238.8595 | 2590208.9548 | 1214242.5326
51 | 2590226.5903 | 1214269.5862 | 2590230.4783 | 1214266.5122
52 | 2590198.8357 | 1214249.9057 | 2590203.9061 | 1214246.2113
53 | 2590203.9061 | 1214246.2113 | 2590208.9548 | 1214242.5326
54 | 2590196.7408 | 1214276.3349 | 2590198.6319 | 1214278.7933
55 | 2590204.8012 | 1214286.8133 | 2590198.6319 | 1214278.7933
56 | 2590204.8012 | 1214286.8133 | 2590215.1893 | 1214300.3143
57 | 2590204.8012 | 1214286.8133 | 2590218.822 | 1214275.7281
58 | 2590223.2801 | 1214310.8296 | 2590215.1893 | 1214300.3143
59 | 2590218.822 | 1214275.7281 | 2590222.7787 | 1214272.5997
60 | 2590222.7787 | 1214272.5997 | 2590226.5903 | 1214269.5862
61 | 2590223.2801 | 1214310.8296 | 2590237.7518 | 1214299.7208
62 | 2590223.2801 | 1214310.8296 | 2590233.4967 | 1214324.1081
63 | 2590237.7518 | 1214299.7208 | 2590237.9734 | 1214299.5507
64 | 2590233.4967 | 1214324.1081 | 2590236.6052 | 1214328.1483
65 | 2590242.7783 | 1214295.8623 | 2590237.9734 | 1214299.5507
66 | 2590242.7783 | 1214295.8623 | 2590242.8662 | 1214295.7948
67 | 2590247.7152 | 1214292.0726 | 2590242.8662 | 1214295.7948
68 | 2590247.7152 | 1214292.0726 | 2590247.7221 | 1214292.0673
69 | 2590252.6456 | 1214288.2879 | 2590247.7221 | 1214292.0673
70 | 2590252.6456 | 1214288.2879 | 2590252.7527 | 1214288.2057
71 | 2590256.5317 | 1214285.3048 | 2590252.7527 | 1214288.2057
72 | 2590183.7276 | 1214314.9155 | 2590175.9452 | 1214302.9463
73 | 2590183.7276 | 1214314.9155 | 2590186.7125 | 1214319.5062 | 2590188.5728 | 1214323.8944 | 2590188.4747 | 1214328.8752 | 2590184.57 | 1214332.7283 | 2590179.2143 | 1214336.2614 | 2590170.6284 | 1214342.8127 | 2590168.9005 | 1214344.9501 | 2590168.353 | 1214349.1089 | 2590169.2927 | 1214352.487 | 2590173.2486 | 1214356.6161 | 2590179.7918 | 1214359.3067 | 2590186.4447 | 1214359.5069 | 2590194.3305 | 1214358.4014
74 | 2590175.9452 | 1214302.9463 | 2590172.1989 | 1214297.1846
75 | 2590094.8416 | 1214345.5184 | 2590081.2218 | 1214357.2367
76 | 2590094.8416 | 1214345.5184 | 2590124.5306 | 1214370.9776
77 | 2590128.2878 | 1214374.1995 | 2590124.5306 | 1214370.9776
78 | 2590128.2878 | 1214374.1995 | 2590141.125 | 1214385.2078
79 | 2590081.2218 | 1214357.2367 | 2590072.9061 | 1214384.3993 | 2590072.0282 | 1214385.3492
80 | 2590479.6626 | 1214341.9231 | 2590476.31 | 1214339.6218 | 2590465.8299 | 1214330.2334 | 2590459.1205 | 1214322.2705
81 | 2590366.6605 | 1214337.4038 | 2590367.6218 | 1214340.754 | 2590370.7156 | 1214347.1526 | 2590375.6678 | 1214352.2696 | 2590379.7644 | 1214355.6697
82 | 2590366.6605 | 1214337.4038 | 2590364.867 | 1214331.1538
83 | 2590387.3789 | 1214361.9894 | 2590379.7644 | 1214355.6697
84 | 2590364.867 | 1214331.1538 | 2590363.4287 | 1214326.1415 | 2590360.9426 | 1214315.1283 | 2590359.0987 | 1214311.7833
85 | 2590387.3789 | 1214361.9894 | 2590378.892 | 1214371.5266
86 | 2590387.3789 | 1214361.9894 | 2590406.7373 | 1214378.4761
87 | 2590378.892 | 1214371.5266 | 2590368.108 | 1214383.6452
88 | 2590423.6385 | 1214392.8701 | 2590406.7373 | 1214378.4761
89 | 2590363.2732 | 1214388.6201 | 2590367.4651 | 1214384.3677 | 2590368.108 | 1214383.6452
90 | 2590423.6385 | 1214392.8701 | 2590437.0055 | 1214404.806
91 | 2590423.6385 | 1214392.8701 | 2590421.2907 | 1214396.8206 | 2590416.9315 | 1214404.3795
92 | 2590331.0196 | 1214300.4577 | 2590331.0196 | 1214300.4577 | 2590318.6703 | 1214313.8633 | 2590312.5857 | 1214317.7178
93 | 2590363.2732 | 1214388.6201 | 2590361.886 | 1214390.0274
94 | 2590437.0055 | 1214404.806 | 2590464.7848 | 1214429.6112
95 | 2590416.9315 | 1214404.3795 | 2590411.2027 | 1214414.3132
96 | 2590306.6228 | 1214321.4952 | 2590312.5857 | 1214317.7178
97 | 2590403.8746 | 1214427.0202 | 2590411.2027 | 1214414.3132
98 | 2590403.8746 | 1214427.0202 | 2590397.7292 | 1214437.6764
99 | 2590393.8692 | 1214444.3697 | 2590397.7292 | 1214437.6764
100 | 2590464.7848 | 1214429.6112 | 2590481.3362 | 1214444.3906
101 | 2590306.6228 | 1214321.4952 | 2590282.597 | 1214336.7153
102 | 2590269.457 | 1214345.0394 | 2590282.597 | 1214336.7153
103 | 2590496.7837 | 1214458.1842 | 2590484.4332 | 1214447.156
104 | 2590481.3362 | 1214444.3906 | 2590484.4332 | 1214447.156
105 | 2590353.6891 | 1214398.3425 | 2590361.886 | 1214390.0274

## bus_geodata
| x | y | coords
0 | 2590311.9546 | 1214183.061
1 | 2590276.7232 | 1214210.2182
2 | 2590325.9872 | 1214172.1716
3 | 2590301.4677 | 1214225.0637
4 | 2590361.3057 | 1214190.2247
5 | 2590347.8054 | 1214148.3336
6 | 2590308.7715 | 1214228.4425
7 | 2590279.0406 | 1214243.3293
8 | 2590387.6661 | 1214201.361
9 | 2590356.3982 | 1214113.1665
10 | 2590325.104 | 1214265.4249
11 | 2590264.4782 | 1214254.6522
12 | 2590161.1191 | 1214232.5887
13 | 2590176.9578 | 1214250.9646
14 | 2590148.3922 | 1214265.3172
15 | 2590273.9723 | 1214095.6578
16 | 2590290.3672 | 1214083.4022
17 | 2590228.8441 | 1214210.5914
18 | 2590231.2122 | 1214213.5326
19 | 2590408.8599 | 1214233.6823
20 | 2590432.6108 | 1214179.5839
21 | 2590474.4795 | 1214212.253
22 | 2590312.8447 | 1214063.2318
23 | 2590380.1594 | 1214094.6586
24 | 2590360.407 | 1214246.2588
25 | 2590396.9117 | 1214255.7363
26 | 2590340.0254 | 1214285.7903
27 | 2590256.5427 | 1214245.9048
28 | 2590335.619 | 1214041.2079
29 | 2590421.7101 | 1214262.0218
30 | 2590449.8563 | 1214311.2755
31 | 2590279.001 | 1214061.5593
32 | 2590184.4651 | 1214260.3766
33 | 2590111.4383 | 1214332.5073
34 | 2590158.7203 | 1214276.4548
35 | 2590340.2117 | 1214036.7665
36 | 2590248.8335 | 1214235.957
37 | 2590248.018 | 1214234.9047
38 | 2590237.6987 | 1214221.5889
39 | 2590243.8466 | 1214255.9428
40 | 2590225.7686 | 1214230.2816
41 | 2590239.9297 | 1214259.0396
42 | 2590220.7755 | 1214233.9197
43 | 2590234.3935 | 1214263.4167
44 | 2590213.996 | 1214238.8595
45 | 2590230.4783 | 1214266.5122
46 | 2590198.8357 | 1214249.9057
47 | 2590203.9061 | 1214246.2113
48 | 2590208.9548 | 1214242.5326
49 | 2590196.7408 | 1214276.3349
50 | 2590198.6319 | 1214278.7933
51 | 2590204.8012 | 1214286.8133
52 | 2590215.1893 | 1214300.3143
53 | 2590218.822 | 1214275.7281
54 | 2590226.5903 | 1214269.5862
55 | 2590222.7787 | 1214272.5997
56 | 2590223.2801 | 1214310.8296
57 | 2590237.7518 | 1214299.7208
58 | 2590233.4967 | 1214324.1081
59 | 2590237.9734 | 1214299.5507
60 | 2590236.6052 | 1214328.1483
61 | 2590242.7783 | 1214295.8623
62 | 2590242.8662 | 1214295.7948
63 | 2590247.7152 | 1214292.0726
64 | 2590247.7221 | 1214292.0673
65 | 2590252.6456 | 1214288.2879
66 | 2590252.7527 | 1214288.2057
67 | 2590256.5317 | 1214285.3048
68 | 2590183.7276 | 1214314.9155
69 | 2590175.9452 | 1214302.9463
70 | 2590194.3305 | 1214358.4014
71 | 2590172.1989 | 1214297.1846
72 | 2590094.8416 | 1214345.5184
73 | 2590128.2878 | 1214374.1995
74 | 2590124.5306 | 1214370.9776
75 | 2590141.125 | 1214385.2078
76 | 2590081.2218 | 1214357.2367
77 | 2590072.0282 | 1214385.3492
78 | 2590459.1205 | 1214322.2705
79 | 2590479.6626 | 1214341.9231
80 | 2590366.6605 | 1214337.4038
81 | 2590379.7644 | 1214355.6697
82 | 2590364.867 | 1214331.1538
83 | 2590387.3789 | 1214361.9894
84 | 2590359.0987 | 1214311.7833
85 | 2590378.892 | 1214371.5266
86 | 2590406.7373 | 1214378.4761
87 | 2590368.108 | 1214383.6452
88 | 2590423.6385 | 1214392.8701
89 | 2590331.0196 | 1214300.4577
90 | 2590363.2732 | 1214388.6201
91 | 2590437.0055 | 1214404.806
92 | 2590416.9315 | 1214404.3795
93 | 2590312.5857 | 1214317.7178
94 | 2590403.8746 | 1214427.0202
95 | 2590411.2027 | 1214414.3132
96 | 2590397.7292 | 1214437.6764
97 | 2590393.8692 | 1214444.3697
98 | 2590464.7848 | 1214429.6112
99 | 2590306.6228 | 1214321.4952
100 | 2590282.597 | 1214336.7153
101 | 2590269.457 | 1214345.0394
102 | 2590496.7837 | 1214458.1842
103 | 2590484.4332 | 1214447.156
104 | 2590481.3362 | 1214444.3906
105 | 2590361.886 | 1214390.0274
106 | 2590353.6891 | 1214398.3425
107 | 2590301.4677 | 1214225.0637

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1