## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3203-11_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3203-11_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3203-11_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_3203-11_0_5_node_11 | 0.4 | n |  | TRUE
4 | bus_LV_3203-11_0_5_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_3203-11_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3203-11_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3203-11_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_3203-11_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_3203-11_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_3203-11_0_5_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_3203-11_0_5_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_3203-11_0_5_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_3203-11_0_5_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_3203-11_0_5_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_3203-11_0_5_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_3203-11_0_5_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_3203-11_0_5_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_3203-11_0_5_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_3203-11_0_5_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_3203-11_0_5_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_3203-11_0_5_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_3203-11_0_5_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_3203-11_0_5_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_3203-11_0_5_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_3203-11_0_5_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_3203-11_0_5_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_3203-11_0_5_node_112 | 0.4 | n |  | TRUE
28 | bus_LV_3203-11_0_5_node_113 | 0.4 | n |  | TRUE
29 | bus_LV_3203-11_0_5_node_23 | 0.4 | n |  | TRUE
30 | bus_LV_3203-11_0_5_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_3203-11_0_5_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_3203-11_0_5_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_3203-11_0_5_node_63 | 0.4 | n |  | TRUE
34 | bus_LV_3203-11_0_5_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_3203-11_0_5_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_3203-11_0_5_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_3203-11_0_5_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_3203-11_0_5_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_3203-11_0_5_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_3203-11_0_5_node_65 | 0.4 | n |  | TRUE
41 | bus_LV_3203-11_0_5_node_67 | 0.4 | n |  | TRUE
42 | bus_LV_3203-11_0_5_node_68 | 0.4 | n |  | TRUE
43 | bus_LV_3203-11_0_5_node_64 | 0.4 | n |  | TRUE
44 | bus_LV_3203-11_0_5_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_3203-11_0_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_3203-11_0_5_node_161 | 0.4 | n |  | TRUE
47 | bus_LV_3203-11_0_5_node_164 | 0.4 | n |  | TRUE
48 | bus_LV_3203-11_0_5_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_3203-11_0_5_node_72 | 0.4 | n |  | TRUE
50 | bus_LV_3203-11_0_5_node_62 | 0.4 | n |  | TRUE
51 | bus_LV_3203-11_0_5_node_39 | 0.4 | n |  | TRUE
52 | bus_LV_3203-11_0_5_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_3203-11_0_5_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_3203-11_0_5_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_3203-11_0_5_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_3203-11_0_5_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_3203-11_0_5_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_3203-11_0_5_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_3203-11_0_5_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_3203-11_0_5_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_3203-11_0_5_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_3203-11_0_5_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_3203-11_0_5_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_3203-11_0_5_node_53 | 0.4 | n |  | TRUE
65 | bus_LV_3203-11_0_5_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_3203-11_0_5_node_163 | 0.4 | n |  | TRUE
67 | bus_LV_3203-11_0_5_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_3203-11_0_5_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_3203-11_0_5_node_140 | 0.4 | n |  | TRUE
70 | bus_LV_3203-11_0_5_node_141 | 0.4 | n |  | TRUE
71 | bus_LV_3203-11_0_5_node_139 | 0.4 | n |  | TRUE
72 | bus_LV_3203-11_0_5_node_142 | 0.4 | n |  | TRUE
73 | bus_LV_3203-11_0_5_node_143 | 0.4 | n |  | TRUE
74 | bus_LV_3203-11_0_5_node_162 | 0.4 | n |  | TRUE
75 | bus_LV_3203-11_0_5_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_3203-11_0_5_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_3203-11_0_5_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_3203-11_0_5_node_138 | 0.4 | n |  | TRUE
79 | bus_LV_3203-11_0_5_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_3203-11_0_5_node_66 | 0.4 | n |  | TRUE
81 | bus_LV_3203-11_0_5_node_82 | 0.4 | n |  | TRUE
82 | bus_LV_3203-11_0_5_node_79 | 0.4 | n |  | TRUE
83 | bus_LV_3203-11_0_5_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_3203-11_0_5_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_3203-11_0_5_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_3203-11_0_5_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_3203-11_0_5_node_85 | 0.4 | n |  | TRUE
88 | bus_LV_3203-11_0_5_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_3203-11_0_5_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_3203-11_0_5_node_77 | 0.4 | n |  | TRUE
91 | bus_LV_3203-11_0_5_node_78 | 0.4 | n |  | TRUE
92 | bus_LV_3203-11_0_5_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_3203-11_0_5_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_3203-11_0_5_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_3203-11_0_5_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_3203-11_0_5_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_3203-11_0_5_node_93 | 0.4 | n |  | TRUE
98 | bus_LV_3203-11_0_5_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_3203-11_0_5_node_91 | 0.4 | n |  | TRUE
100 | bus_LV_3203-11_0_5_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_3203-11_0_5_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_3203-11_0_5_node_86 | 0.4 | n |  | TRUE
103 | bus_LV_3203-11_0_5_node_87 | 0.4 | n |  | TRUE
104 | bus_LV_3203-11_0_5_node_122 | 0.4 | n |  | TRUE
105 | bus_LV_3203-11_0_5_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_3203-11_0_5_node_147 | 0.4 | n |  | TRUE
107 | bus_LV_3203-11_0_5_node_144 | 0.4 | n |  | TRUE
108 | bus_LV_3203-11_0_5_node_99 | 0.4 | n |  | TRUE
109 | bus_LV_3203-11_0_5_node_148 | 0.4 | n |  | TRUE
110 | bus_LV_3203-11_0_5_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_3203-11_0_5_node_96 | 0.4 | n |  | TRUE
112 | bus_LV_3203-11_0_5_node_97 | 0.4 | n |  | TRUE
113 | bus_LV_3203-11_0_5_node_98 | 0.4 | n |  | TRUE
114 | bus_LV_3203-11_0_5_node_100 | 0.4 | n |  | TRUE
115 | bus_LV_3203-11_0_5_node_102 | 0.4 | n |  | TRUE
116 | bus_LV_3203-11_0_5_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_3203-11_0_5_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_3203-11_0_5_node_123 | 0.4 | n |  | TRUE
119 | bus_LV_3203-11_0_5_node_117 | 0.4 | n |  | TRUE
120 | bus_LV_3203-11_0_5_node_128 | 0.4 | n |  | TRUE
121 | bus_LV_3203-11_0_5_node_115 | 0.4 | n |  | TRUE
122 | bus_LV_3203-11_0_5_node_105 | 0.4 | n |  | TRUE
123 | bus_LV_3203-11_0_5_node_106 | 0.4 | n |  | TRUE
124 | bus_LV_3203-11_0_5_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_3203-11_0_5_node_108 | 0.4 | n |  | TRUE
126 | bus_LV_3203-11_0_5_node_109 | 0.4 | n |  | TRUE
127 | bus_LV_3203-11_0_5_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_3203-11_0_5_node_134 | 0.4 | n |  | TRUE
129 | bus_LV_3203-11_0_5_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_3203-11_0_5_node_135 | 0.4 | n |  | TRUE
131 | bus_LV_3203-11_0_5_node_114 | 0.4 | n |  | TRUE
132 | bus_LV_3203-11_0_5_node_116 | 0.4 | n |  | TRUE
133 | bus_LV_3203-11_0_5_node_118 | 0.4 | n |  | TRUE
134 | bus_LV_3203-11_0_5_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_3203-11_0_5_node_120 | 0.4 | n |  | TRUE
136 | bus_LV_3203-11_0_5_node_145 | 0.4 | n |  | TRUE
137 | bus_LV_3203-11_0_5_node_127 | 0.4 | n |  | TRUE
138 | bus_LV_3203-11_0_5_node_124 | 0.4 | n |  | TRUE
139 | bus_LV_3203-11_0_5_node_125 | 0.4 | n |  | TRUE
140 | bus_LV_3203-11_0_5_node_126 | 0.4 | n |  | TRUE
141 | bus_LV_3203-11_0_5_node_129 | 0.4 | n |  | TRUE
142 | bus_LV_3203-11_0_5_node_131 | 0.4 | n |  | TRUE
143 | bus_LV_3203-11_0_5_node_130 | 0.4 | n |  | TRUE
144 | bus_LV_3203-11_0_5_node_132 | 0.4 | n |  | TRUE
145 | bus_LV_3203-11_0_5_node_160 | 0.4 | n |  | TRUE
146 | bus_LV_3203-11_0_5_node_159 | 0.4 | n |  | TRUE
147 | bus_LV_3203-11_0_5_node_146 | 0.4 | n |  | TRUE
148 | bus_LV_3203-11_0_5_node_150 | 0.4 | n |  | TRUE
149 | bus_LV_3203-11_0_5_node_151 | 0.4 | n |  | TRUE
150 | bus_LV_3203-11_0_5_node_155 | 0.4 | n |  | TRUE
151 | bus_LV_3203-11_0_5_node_149 | 0.4 | n |  | TRUE
152 | bus_LV_3203-11_0_5_node_152 | 0.4 | n |  | TRUE
153 | bus_LV_3203-11_0_5_node_157 | 0.4 | n |  | TRUE
154 | bus_LV_3203-11_0_5_node_153 | 0.4 | n |  | TRUE
155 | bus_LV_3203-11_0_5_node_154 | 0.4 | n |  | TRUE
156 | bus_LV_3203-11_0_5_node_156 | 0.4 | n |  | TRUE
157 | bus_LV_3203-11_0_5_node_158 | 0.4 | n |  | TRUE
158 | bus_MV_583_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3203-11_0_5_load_0 | 0 | 0.0028976 | 0.00072622 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3203-11_0_5_load_1 | 1 | 0.0011794 | 0.00029559 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3203-11_0_5_load_3 | 2 | 0.00065229 | 0.00016348 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3203-11_0_5_load_11 | 3 | 0.0015219 | 0.00038142 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3203-11_0_5_load_5 | 5 | 0.0028972 | 0.00072611 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3203-11_0_5_load_6 | 6 | 0.0028988 | 0.00072651 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3203-11_0_5_load_7 | 7 | 0.0025304 | 0.00063419 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3203-11_0_5_load_8 | 8 | 0.0046621 | 0.0011684 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3203-11_0_5_load_9 | 9 | 0.0022002 | 0.00055142 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3203-11_0_5_load_10 | 10 | 0.003523 | 0.00088294 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3203-11_0_5_load_13 | 11 | 0.003944 | 0.00098847 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3203-11_0_5_load_14 | 12 | 0.012725 | 0.0031892 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3203-11_0_5_load_28 | 14 | 0.0021768 | 0.00054556 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3203-11_0_5_load_32 | 16 | 0.0018466 | 0.00046281 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3203-11_0_5_load_34 | 17 | 0.0035234 | 0.00088306 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3203-11_0_5_load_15 | 19 | 0.0029792 | 0.00074667 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3203-11_0_5_load_16 | 20 | 0.0034541 | 0.00086568 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3203-11_0_5_load_21 | 21 | 0.0063621 | 0.0015945 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3203-11_0_5_load_22 | 22 | 0.0027108 | 0.00067939 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3203-11_0_5_load_17 | 23 | 0.003261 | 0.00081729 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3203-11_0_5_load_18 | 24 | 0.0023565 | 0.00059059 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3203-11_0_5_load_19 | 25 | 0.0060551 | 0.0015176 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3203-11_0_5_load_20 | 26 | 0.0057887 | 0.0014508 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3203-11_0_5_load_112 | 27 | 0.0032803 | 0.00082212 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3203-11_0_5_load_113 | 28 | 0.0031252 | 0.00078325 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3203-11_0_5_load_23 | 29 | 0.0073253 | 0.0018359 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3203-11_0_5_load_24 | 30 | 0.0024621 | 0.00061707 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3203-11_0_5_load_25 | 31 | 0.0044867 | 0.0011245 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3203-11_0_5_load_26 | 32 | 0.0016996 | 0.00042596 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3203-11_0_5_load_61 | 34 | 0.0019234 | 0.00048204 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3203-11_0_5_load_30 | 35 | 0.0057704 | 0.0014462 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3203-11_0_5_load_31 | 37 | 0.0018056 | 0.00045252 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3203-11_0_5_load_74 | 39 | 0.0052304 | 0.0013109 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3203-11_0_5_load_68 | 42 | 0.0011137 | 0.00027911 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3203-11_0_5_load_64 | 43 | 0.0037764 | 0.00094646 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3203-11_0_5_load_36 | 44 | 0.0037869 | 0.00094909 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3203-11_0_5_load_37 | 45 | 0.0025998 | 0.00065157 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3203-11_0_5_load_161 | 46 | 0.003387 | 0.00084886 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3203-11_0_5_load_164 | 47 | 0.0017721 | 0.00044413 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3203-11_0_5_load_45 | 48 | 0.0038408 | 0.0009626 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3203-11_0_5_load_72 | 49 | 0.0019929 | 0.00049946 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3203-11_0_5_load_62 | 50 | 0.0037573 | 0.00094167 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3203-11_0_5_load_39 | 51 | 0.0020931 | 0.00052459 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3203-11_0_5_load_40 | 52 | 0.0038973 | 0.00097675 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3203-11_0_5_load_41 | 53 | 0.0021218 | 0.00053177 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3203-11_0_5_load_42 | 54 | 0.0022366 | 0.00056055 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3203-11_0_5_load_44 | 56 | 0.0026546 | 0.00066531 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3203-11_0_5_load_50 | 57 | 0.0031626 | 0.00079263 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3203-11_0_5_load_46 | 59 | 0.0014441 | 0.00036192 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3203-11_0_5_load_48 | 60 | 0.0020211 | 0.00050654 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3203-11_0_5_load_49 | 61 | 0.0014444 | 0.000362 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3203-11_0_5_load_52 | 63 | 0.00045196 | 0.00011327 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3203-11_0_5_load_54 | 65 | 0.0015464 | 0.00038757 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3203-11_0_5_load_163 | 66 | 0.0056181 | 0.001408 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3203-11_0_5_load_55 | 67 | 0.002902 | 0.0007273 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3203-11_0_5_load_59 | 68 | 0.0018231 | 0.00045691 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3203-11_0_5_load_140 | 69 | 0.0012001 | 0.00030076 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3203-11_0_5_load_143 | 73 | 0.0082814 | 0.0020755 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3203-11_0_5_load_162 | 74 | 0.0016372 | 0.00041031 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3203-11_0_5_load_56 | 75 | 0.0021555 | 0.00054022 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3203-11_0_5_load_57 | 76 | 0.0031574 | 0.00079131 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3203-11_0_5_load_58 | 77 | 0.0051321 | 0.0012862 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3203-11_0_5_load_138 | 78 | 0.0054909 | 0.0013761 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3203-11_0_5_load_70 | 79 | 0.0021751 | 0.00054514 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3203-11_0_5_load_66 | 80 | 0.0029863 | 0.00074844 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3203-11_0_5_load_82 | 81 | 0.0064149 | 0.0016077 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3203-11_0_5_load_69 | 83 | 0.002973 | 0.0007451 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3203-11_0_5_load_71 | 84 | 0.0030563 | 0.00076597 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3203-11_0_5_load_73 | 85 | 0.0017104 | 0.00042867 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3203-11_0_5_load_84 | 86 | 0.0036474 | 0.00091412 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3203-11_0_5_load_75 | 88 | 0.0036538 | 0.00091572 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3203-11_0_5_load_78 | 91 | 0.003231 | 0.00080975 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3203-11_0_5_load_80 | 92 | 0.0067009 | 0.0016794 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3203-11_0_5_load_81 | 93 | 0.0038651 | 0.00096869 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3203-11_0_5_load_83 | 94 | 0.0027736 | 0.00069512 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3203-11_0_5_load_92 | 95 | 0.0036774 | 0.00092165 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3203-11_0_5_load_93 | 97 | 0.0016011 | 0.00040127 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3203-11_0_5_load_91 | 99 | 0.04843 | 0.012138 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3203-11_0_5_load_88 | 100 | 0.0097573 | 0.0024454 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3203-11_0_5_load_94 | 101 | 0.001628 | 0.00040802 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3203-11_0_5_load_86 | 102 | 0.0078334 | 0.0019632 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3203-11_0_5_load_87 | 103 | 0.0054746 | 0.0013721 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3203-11_0_5_load_122 | 104 | 0.0093029 | 0.0023315 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3203-11_0_5_load_101 | 105 | 0.00813 | 0.0020376 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3203-11_0_5_load_147 | 106 | 0.0096824 | 0.0024266 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3203-11_0_5_load_144 | 107 | 0.0031119 | 0.00077993 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3203-11_0_5_load_99 | 108 | 0.0032191 | 0.00080679 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3203-11_0_5_load_95 | 110 | 0.0040918 | 0.0010255 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3203-11_0_5_load_96 | 111 | 0.0045703 | 0.0011454 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3203-11_0_5_load_97 | 112 | 0.015383 | 0.0038554 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3203-11_0_5_load_98 | 113 | 0.0023339 | 0.00058494 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3203-11_0_5_load_100 | 114 | 0.0077028 | 0.0019305 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3203-11_0_5_load_102 | 115 | 0.0027628 | 0.00069241 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3203-11_0_5_load_103 | 116 | 0.0048609 | 0.0012182 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3203-11_0_5_load_123 | 118 | 0.0033755 | 0.00084599 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3203-11_0_5_load_117 | 119 | 0.0087346 | 0.0021891 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3203-11_0_5_load_128 | 120 | 0.0038489 | 0.00096462 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3203-11_0_5_load_105 | 122 | 0.0014684 | 0.00036802 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3203-11_0_5_load_107 | 124 | 0.0067071 | 0.001681 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3203-11_0_5_load_108 | 125 | 0.0034384 | 0.00086175 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3203-11_0_5_load_109 | 126 | 0.0018093 | 0.00045346 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3203-11_0_5_load_110 | 127 | 0.001188 | 0.00029775 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3203-11_0_5_load_134 | 128 | 0.0020205 | 0.00050638 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3203-11_0_5_load_135 | 130 | 0.0019561 | 0.00049026 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3203-11_0_5_load_114 | 131 | 0.0041136 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3203-11_0_5_load_116 | 132 | 0.0012911 | 0.00032359 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3203-11_0_5_load_118 | 133 | 0.0050371 | 0.0012624 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3203-11_0_5_load_119 | 134 | 0.0028908 | 0.0007245 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3203-11_0_5_load_120 | 135 | 0.0068707 | 0.001722 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3203-11_0_5_load_145 | 136 | 0.017036 | 0.0042696 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3203-11_0_5_load_124 | 138 | 0.0064345 | 0.0016126 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3203-11_0_5_load_125 | 139 | 0.00428 | 0.0010727 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3203-11_0_5_load_126 | 140 | 0.004342 | 0.0010882 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3203-11_0_5_load_129 | 141 | 0.0059289 | 0.0014859 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3203-11_0_5_load_131 | 142 | 0.0035274 | 0.00088405 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3203-11_0_5_load_130 | 143 | 0.0031959 | 0.00080097 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3203-11_0_5_load_132 | 144 | 0.0026506 | 0.00066429 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3203-11_0_5_load_160 | 145 | 0.0029296 | 0.00073422 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3203-11_0_5_load_150 | 148 | 0.0060642 | 0.0015198 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3203-11_0_5_load_151 | 149 | 0.013283 | 0.003329 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3203-11_0_5_load_152 | 152 | 0.0048776 | 0.0012224 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3203-11_0_5_load_157 | 153 | 0.0087632 | 0.0021963 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3203-11_0_5_load_153 | 154 | 0.014367 | 0.0036008 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_3203-11_0_5_load_154 | 155 | 0.0045437 | 0.0011388 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_3203-11_0_5_load_156 | 156 | 0.0053395 | 0.0013382 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_3203-11_0_5_load_158 | 157 | 0.0041231 | 0.0010333 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 101 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3203-11_0_5_line_0 |  | 0 | 1 | 0.0255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3203-11_0_5_line_1 |  | 1 | 2 | 0.041142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3203-11_0_5_line_2 |  | 2 | 3 | 0.031321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3203-11_0_5_line_3 |  | 3 | 4 | 0.026119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3203-11_0_5_line_4 |  | 4 | 13 | 0.020387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_3203-11_0_5_line_5 |  | 4 | 14 | 0.012379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_3203-11_0_5_line_6 |  | 5 | 6 | 0.024199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3203-11_0_5_line_7 |  | 6 | 7 | 0.016254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3203-11_0_5_line_8 |  | 7 | 8 | 0.038895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3203-11_0_5_line_9 |  | 8 | 9 | 0.028891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3203-11_0_5_line_10 |  | 9 | 10 | 0.015835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3203-11_0_5_line_11 |  | 10 | 11 | 0.011858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3203-11_0_5_line_12 |  | 11 | 12 | 0.035168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3203-11_0_5_line_13 |  | 12 | 19 | 0.0062026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3203-11_0_5_line_14 |  | 13 | 15 | 0.03581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_3203-11_0_5_line_15 |  | 13 | 16 | 0.047425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_3203-11_0_5_line_16 |  | 13 | 17 | 0.024759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_3203-11_0_5_line_17 |  | 14 | 18 | 0.0090981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3203-11_0_5_line_18 |  | 15 | 33 | 0.004295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_3203-11_0_5_line_19 |  | 15 | 34 | 0.046702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_3203-11_0_5_line_20 |  | 16 | 35 | 0.0045359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_3203-11_0_5_line_21 |  | 17 | 36 | 0.04625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_3203-11_0_5_line_22 |  | 18 | 32 | 0.049437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3203-11_0_5_line_23 |  | 19 | 20 | 0.0075055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3203-11_0_5_line_24 |  | 20 | 21 | 0.012729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3203-11_0_5_line_25 |  | 21 | 22 | 0.0065043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3203-11_0_5_line_26 |  | 22 | 29 | 0.011129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3203-11_0_5_line_27 |  | 23 | 24 | 0.00031934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3203-11_0_5_line_28 |  | 23 | 25 | 0.0058002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3203-11_0_5_line_29 |  | 25 | 26 | 0.028372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3203-11_0_5_line_30 |  | 26 | 27 | 0.021257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3203-11_0_5_line_31 |  | 27 | 28 | 0.010174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3203-11_0_5_line_32 |  | 28 | 129 | 0.061425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3203-11_0_5_line_33 |  | 29 | 30 | 0.021883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3203-11_0_5_line_34 |  | 30 | 31 | 0.030619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3203-11_0_5_line_35 |  | 31 | 32 | 0.0074637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3203-11_0_5_line_36 |  | 33 | 49 | 0.01224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_3203-11_0_5_line_37 |  | 34 | 50 | 0.0036041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3203-11_0_5_line_38 |  | 35 | 37 | 0.026708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_3203-11_0_5_line_39 |  | 36 | 44 | 0.013421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_3203-11_0_5_line_40 |  | 36 | 45 | 0.035015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3203-11_0_5_line_41 |  | 37 | 38 | 0.051359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_3203-11_0_5_line_42 |  | 38 | 39 | 0.080879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3203-11_0_5_line_43 |  | 38 | 40 | 0.009581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_3203-11_0_5_line_44 |  | 40 | 41 | 0.018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_3203-11_0_5_line_45 |  | 40 | 42 | 0.060536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_3203-11_0_5_line_46 |  | 40 | 43 | 0.02144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_3203-11_0_5_line_47 |  | 41 | 81 | 0.0019378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_3203-11_0_5_line_48 |  | 43 | 80 | 0.020131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_3203-11_0_5_line_49 |  | 44 | 46 | 0.0076278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_3203-11_0_5_line_50 |  | 45 | 47 | 0.006221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3203-11_0_5_line_51 |  | 46 | 48 | 0.0090369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_3203-11_0_5_line_52 |  | 48 | 55 | 0.037864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_3203-11_0_5_line_53 |  | 49 | 79 | 0.01075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_3203-11_0_5_line_54 |  | 51 | 52 | 0.043528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3203-11_0_5_line_55 |  | 51 | 53 | 0.025301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3203-11_0_5_line_56 |  | 52 | 54 | 0.00030422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3203-11_0_5_line_57 |  | 54 | 55 | 0.027425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3203-11_0_5_line_58 |  | 55 | 56 | 0.022441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_3203-11_0_5_line_59 |  | 56 | 57 | 0.043434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_3203-11_0_5_line_60 |  | 57 | 58 | 0.018439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_3203-11_0_5_line_61 |  | 58 | 61 | 0.024948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_3203-11_0_5_line_62 |  | 58 | 59 | 0.033572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3203-11_0_5_line_63 |  | 59 | 60 | 0.073109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3203-11_0_5_line_64 |  | 61 | 62 | 0.026243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_3203-11_0_5_line_65 |  | 62 | 63 | 0.019144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_3203-11_0_5_line_66 |  | 62 | 64 | 0.010492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_3203-11_0_5_line_67 |  | 63 | 65 | 0.031988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_3203-11_0_5_line_68 |  | 64 | 66 | 0.16554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3203-11_0_5_line_69 |  | 65 | 67 | 0.044599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3203-11_0_5_line_70 |  | 65 | 68 | 0.19416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3203-11_0_5_line_71 |  | 66 | 72 | 0.030546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3203-11_0_5_line_72 |  | 67 | 75 | 0.027754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3203-11_0_5_line_73 |  | 69 | 70 | 0.045757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3203-11_0_5_line_74 |  | 69 | 71 | 0.043495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3203-11_0_5_line_75 |  | 70 | 72 | 0.011849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3203-11_0_5_line_76 |  | 70 | 73 | 0.033622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3203-11_0_5_line_77 |  | 71 | 78 | 0.08849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3203-11_0_5_line_78 |  | 72 | 74 | 0.0056617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3203-11_0_5_line_79 |  | 75 | 76 | 0.029186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3203-11_0_5_line_80 |  | 76 | 77 | 0.019252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3203-11_0_5_line_81 |  | 81 | 82 | 0.014067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_3203-11_0_5_line_82 |  | 82 | 94 | 0.054045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_3203-11_0_5_line_83 |  | 82 | 89 | 0.00779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_3203-11_0_5_line_84 |  | 83 | 84 | 0.051467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_3203-11_0_5_line_85 |  | 84 | 85 | 0.011741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_3203-11_0_5_line_86 |  | 85 | 86 | 0.033557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_3203-11_0_5_line_87 |  | 86 | 87 | 0.028431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_3203-11_0_5_line_88 |  | 87 | 102 | 0.040181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_3203-11_0_5_line_89 |  | 88 | 89 | 0.018723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_3203-11_0_5_line_90 |  | 88 | 90 | 0.010655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_3203-11_0_5_line_91 |  | 89 | 91 | 0.017089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_3203-11_0_5_line_92 |  | 90 | 92 | 0.01985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_3203-11_0_5_line_93 |  | 90 | 93 | 0.032941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_3203-11_0_5_line_94 |  | 92 | 95 | 0.047924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_3203-11_0_5_line_95 |  | 93 | 96 | 0.042802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_3203-11_0_5_line_96 |  | 94 | 97 | 0.01353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_3203-11_0_5_line_97 |  | 96 | 98 | 0.029946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_3203-11_0_5_line_98 |  | 96 | 99 | 0.042297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_3203-11_0_5_line_99 |  | 96 | 100 | 0.018976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_3203-11_0_5_line_100 |  | 97 | 101 | 0.0099008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_3203-11_0_5_line_101 |  | 98 | 104 | 0.010316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_3203-11_0_5_line_102 |  | 98 | 105 | 0.04041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_3203-11_0_5_line_103 |  | 99 | 106 | 0.015331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3203-11_0_5_line_104 |  | 100 | 103 | 0.054836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_3203-11_0_5_line_105 |  | 101 | 110 | 0.020822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3203-11_0_5_line_106 |  | 102 | 103 | 0.038072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_3203-11_0_5_line_107 |  | 104 | 107 | 0.036508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_3203-11_0_5_line_108 |  | 105 | 108 | 0.0062474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_3203-11_0_5_line_109 |  | 106 | 109 | 0.022146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3203-11_0_5_line_110 |  | 107 | 136 | 0.036539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_3203-11_0_5_line_111 |  | 108 | 113 | 0.025556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_3203-11_0_5_line_112 |  | 109 | 151 | 0.045318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3203-11_0_5_line_113 |  | 110 | 111 | 0.0087037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3203-11_0_5_line_114 |  | 111 | 112 | 0.024645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3203-11_0_5_line_115 |  | 113 | 114 | 0.0043239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_3203-11_0_5_line_116 |  | 114 | 115 | 0.019212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_3203-11_0_5_line_117 |  | 115 | 116 | 0.013652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_3203-11_0_5_line_118 |  | 116 | 117 | 0.015175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_3203-11_0_5_line_119 |  | 117 | 118 | 0.041384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_3203-11_0_5_line_120 |  | 117 | 119 | 0.033585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_3203-11_0_5_line_121 |  | 118 | 120 | 0.0001879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_3203-11_0_5_line_122 |  | 119 | 121 | 0.0062836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_3203-11_0_5_line_123 |  | 120 | 137 | 0.023144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
124 | LV_3203-11_0_5_line_124 |  | 121 | 132 | 0.038834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_3203-11_0_5_line_125 |  | 121 | 131 | 0.011466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_3203-11_0_5_line_126 |  | 122 | 123 | 0.029411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_3203-11_0_5_line_127 |  | 123 | 124 | 0.025535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_3203-11_0_5_line_128 |  | 123 | 125 | 0.010701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_3203-11_0_5_line_129 |  | 124 | 126 | 0.016944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_3203-11_0_5_line_130 |  | 126 | 127 | 0.038012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_3203-11_0_5_line_131 |  | 126 | 128 | 0.044141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_3203-11_0_5_line_132 |  | 127 | 129 | 0.024593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_3203-11_0_5_line_133 |  | 128 | 130 | 0.0008475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_3203-11_0_5_line_134 |  | 129 | 131 | 0.010455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_3203-11_0_5_line_135 |  | 132 | 133 | 0.020433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_3203-11_0_5_line_136 |  | 133 | 134 | 0.023174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_3203-11_0_5_line_137 |  | 134 | 135 | 0.0078943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_3203-11_0_5_line_138 |  | 136 | 147 | 0.019972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_3203-11_0_5_line_139 |  | 137 | 141 | 0.0054602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_3203-11_0_5_line_140 |  | 137 | 139 | 0.021999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_3203-11_0_5_line_141 |  | 138 | 139 | 0.00060004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_3203-11_0_5_line_142 |  | 138 | 140 | 0.025301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_3203-11_0_5_line_143 |  | 141 | 142 | 0.026371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_3203-11_0_5_line_144 |  | 142 | 143 | 0.016181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_3203-11_0_5_line_145 |  | 143 | 144 | 0.0057707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_3203-11_0_5_line_146 |  | 145 | 146 | 0.023251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_3203-11_0_5_line_147 |  | 146 | 157 | 0.0062484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_3203-11_0_5_line_148 |  | 147 | 148 | 0.017029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_3203-11_0_5_line_149 |  | 147 | 149 | 0.030923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_3203-11_0_5_line_150 |  | 149 | 150 | 0.010572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
151 | LV_3203-11_0_5_line_151 |  | 150 | 153 | 0.029159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_3203-11_0_5_line_152 |  | 150 | 154 | 0.019742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_3203-11_0_5_line_153 |  | 151 | 152 | 0.060395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_3203-11_0_5_line_154 |  | 153 | 157 | 0.0057079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_3203-11_0_5_line_155 |  | 154 | 155 | 0.0044117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_3203-11_0_5_line_156 |  | 155 | 156 | 0.0081523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3203-11_0_5_trafo_94 | 0.63 MVA 20/0.4 kV | 158 | 101 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2746605.5969 | 1256738.1796 | 2746608.1773 | 1256716.4407 | 2746608.5069 | 1256712.8478
1 | 2746608.5069 | 1256712.8478 | 2746610.9583 | 1256686.1246 | 2746612.4829 | 1256671.8998
2 | 2746615.8207 | 1256640.757 | 2746612.4829 | 1256671.8998
3 | 2746621.2168 | 1256615.31 | 2746619.3183 | 1256620.9796 | 2746618.202 | 1256624.3108 | 2746616.6018 | 1256633.4689 | 2746615.8207 | 1256640.757
4 | 2746621.2168 | 1256615.31 | 2746627.1764 | 1256608.6512 | 2746627.0229 | 1256597.1918
5 | 2746621.2168 | 1256615.31 | 2746610.7991 | 1256621.9967
6 | 2746564.0971 | 1256758.1103 | 2746569.809 | 1256734.5953
7 | 2746569.809 | 1256734.5953 | 2746569.8569 | 1256734.3982 | 2746573.3662 | 1256729.4914 | 2746576.1813 | 1256722.4543 | 2746573.8055 | 1256721.903
8 | 2746535.9136 | 1256713.128 | 2746539.7748 | 1256714.0227 | 2746559.7074 | 1256718.6317 | 2746573.8055 | 1256721.903
9 | 2746507.4485 | 1256709.5783 | 2746510.4765 | 1256709.2041 | 2746521.1777 | 1256709.7139 | 2746524.9961 | 1256710.5981 | 2746535.9136 | 1256713.128
10 | 2746507.4485 | 1256709.5783 | 2746499.9796 | 1256710.5012 | 2746491.6785 | 1256710.8739
11 | 2746482.5718 | 1256703.5638 | 2746482.5718 | 1256703.5638 | 2746486.5494 | 1256708.0777 | 2746489.9364 | 1256709.9299 | 2746491.6785 | 1256710.8739 | 2746491.6785 | 1256710.8739
12 | 2746482.5718 | 1256703.5638 | 2746482.1764 | 1256700.64 | 2746480.664 | 1256684.0199 | 2746483.2244 | 1256677.8217 | 2746484.3766 | 1256669.075
13 | 2746486.3765 | 1256663.2037 | 2746484.3766 | 1256669.075 | 2746484.3766 | 1256669.075
14 | 2746627.0229 | 1256597.1918 | 2746648.8282 | 1256576.1893 | 2746652.8552 | 1256572.3186
15 | 2746627.0229 | 1256597.1918 | 2746614.2761 | 1256563.5325 | 2746608.5481 | 1256553.6383
16 | 2746627.0229 | 1256597.1918 | 2746636.5936 | 1256618.049 | 2746637.3508 | 1256619.6934
17 | 2746602.4152 | 1256625.332 | 2746608.4206 | 1256623.5233 | 2746610.7991 | 1256621.9967
18 | 2746655.9547 | 1256569.3369 | 2746652.8552 | 1256572.3186
19 | 2746652.8552 | 1256572.3186 | 2746664.1945 | 1256574.7908 | 2746671.5704 | 1256579.7894 | 2746680.5632 | 1256588.0424 | 2746692.7819 | 1256594.8357
20 | 2746606.2755 | 1256549.7128 | 2746608.5481 | 1256553.6383
21 | 2746661.485 | 1256659.1165 | 2746652.0152 | 1256643.9339 | 2746647.6532 | 1256636.9746 | 2746642.3621 | 1256628.5354 | 2746638.8059 | 1256622.8529 | 2746637.3508 | 1256619.6934
22 | 2746602.4152 | 1256625.332 | 2746593.2697 | 1256624.7605 | 2746585.2345 | 1256621.7031 | 2746565.9374 | 1256614.2737 | 2746559.7792 | 1256611.8968 | 2746555.4992 | 1256610.8887
23 | 2746486.3765 | 1256663.2037 | 2746488.7966 | 1256656.0991
24 | 2746493.6963 | 1256644.3821 | 2746490.8532 | 1256650.0613 | 2746488.7966 | 1256656.0991
25 | 2746493.6963 | 1256644.3821 | 2746496.608 | 1256638.5659
26 | 2746496.608 | 1256638.5659 | 2746500.3785 | 1256631.0341 | 2746502.2486 | 1256629.0775
27 | 2746345.2294 | 1256585.7097 | 2746344.9283 | 1256585.8159
28 | 2746344.9283 | 1256585.8159 | 2746339.4581 | 1256587.7445
29 | 2746316.1935 | 1256573.8466 | 2746326.5839 | 1256581.1326 | 2746331.9217 | 1256586.1805 | 2746334.163 | 1256587.9932 | 2746337.4259 | 1256588.4632 | 2746338.6286 | 1256588.037 | 2746339.4581 | 1256587.7445
30 | 2746316.1935 | 1256573.8466 | 2746316.1935 | 1256573.8466 | 2746299.748 | 1256560.3785
31 | 2746299.748 | 1256560.3785 | 2746299.6133 | 1256560.2682 | 2746291.4802 | 1256554.4505 | 2746291.4802 | 1256554.4505
32 | 2746318.5494 | 1256506.3617 | 2746303.9914 | 1256518.0911 | 2746294.5096 | 1256528.3668 | 2746287.1389 | 1256541.7532 | 2746289.0412 | 1256549.0406 | 2746291.4802 | 1256554.4505
33 | 2746502.2486 | 1256629.0775 | 2746508.3643 | 1256622.6792 | 2746512.764 | 1256618.0725 | 2746517.79 | 1256615.5945 | 2746518.7391 | 1256615.1276
34 | 2746548.2307 | 1256609.1987 | 2746541.8727 | 1256609.2399 | 2746535.941 | 1256609.2931 | 2746533.4733 | 1256609.3098 | 2746522.6554 | 1256613.2014 | 2746518.7391 | 1256615.1276
35 | 2746548.2307 | 1256609.1987 | 2746548.2795 | 1256609.1984 | 2746550.3049 | 1256609.6712 | 2746555.2409 | 1256610.8278 | 2746555.4992 | 1256610.8887
36 | 2746655.9547 | 1256569.3369 | 2746650.0331 | 1256558.6246
37 | 2746695.9318 | 1256596.587 | 2746692.7819 | 1256594.8357
38 | 2746606.2755 | 1256549.7128 | 2746592.894 | 1256526.5988
39 | 2746661.485 | 1256659.1165 | 2746667.2759 | 1256668.3911 | 2746668.5917 | 1256670.5015
40 | 2746661.485 | 1256659.1165 | 2746643.4553 | 1256689.1323
41 | 2746562.3203 | 1256485.5818 | 2746565.9914 | 1256488.7646 | 2746567.2251 | 1256489.8296 | 2746573.7606 | 1256498.9112 | 2746578.757 | 1256505.8528 | 2746589.5962 | 1256520.9023 | 2746592.894 | 1256526.5988
42 | 2746517.7222 | 1256543.701 | 2746516.1771 | 1256542.417 | 2746514.1836 | 1256540.0432 | 2746512.79 | 1256537.5174 | 2746512.9946 | 1256534.1303 | 2746514.0305 | 1256531.2976 | 2746518.1327 | 1256527.1284 | 2746555.4962 | 1256493.6318 | 2746560.5016 | 1256487.7278 | 2746562.3203 | 1256485.5818
43 | 2746555.0667 | 1256479.2962 | 2746562.3203 | 1256485.5818
44 | 2746555.0667 | 1256479.2962 | 2746541.2904 | 1256467.3659
45 | 2746555.0667 | 1256479.2962 | 2746523.3926 | 1256512.1663 | 2746510.9625 | 1256520.5224
46 | 2746555.0667 | 1256479.2962 | 2746571.3465 | 1256465.3451
47 | 2746541.2904 | 1256467.3659 | 2746539.8255 | 1256466.0975
48 | 2746589.7222 | 1256457.9668 | 2746574.9711 | 1256462.239 | 2746571.3465 | 1256465.3451
49 | 2746672.6275 | 1256676.9742 | 2746668.5917 | 1256670.5015
50 | 2746637.5509 | 1256687.1731 | 2746643.4553 | 1256689.1323
51 | 2746677.6348 | 1256684.4826 | 2746676.1577 | 1256682.6361 | 2746672.6275 | 1256676.9742
52 | 2746701.2803 | 1256714.0556 | 2746694.5771 | 1256705.6703 | 2746687.1861 | 1256696.4226 | 2746677.6348 | 1256684.4826
53 | 2746644.8323 | 1256549.2163 | 2746650.0331 | 1256558.6246
54 | 2746680.36 | 1256732.2557 | 2746647.5199 | 1256760.8256
55 | 2746626.0811 | 1256770.3251 | 2746630.8541 | 1256768.0078 | 2746637.7013 | 1256769.3675 | 2746647.5199 | 1256760.8256
56 | 2746680.5895 | 1256732.056 | 2746680.36 | 1256732.2557
57 | 2746701.2803 | 1256714.0556 | 2746680.5895 | 1256732.056
58 | 2746701.2803 | 1256714.0556 | 2746715.276 | 1256731.5974
59 | 2746715.276 | 1256731.5974 | 2746721.3593 | 1256739.222 | 2746728.9986 | 1256748.7983 | 2746743.1584 | 1256764.8839
60 | 2746755.3422 | 1256778.7247 | 2746743.1584 | 1256764.8839
61 | 2746755.3422 | 1256778.7247 | 2746768.9408 | 1256794.4215 | 2746771.7584 | 1256797.5093
62 | 2746755.3422 | 1256778.7247 | 2746743.7363 | 1256788.5355 | 2746738.3064 | 1256793.3055 | 2746735.8958 | 1256794.9807 | 2746729.5988 | 1256797.2936 | 2746728.117 | 1256797.549
63 | 2746655.9397 | 1256790.2618 | 2746660.3713 | 1256791.0612 | 2746664.6508 | 1256790.3888 | 2746719.4454 | 1256799.0436 | 2746728.117 | 1256797.549
64 | 2746788.346 | 1256817.8364 | 2746774.4129 | 1256800.4185 | 2746771.7584 | 1256797.5093
65 | 2746788.346 | 1256817.8364 | 2746795.9083 | 1256805.5786 | 2746797.1699 | 1256801.0088
66 | 2746795.4034 | 1256825.6189 | 2746788.346 | 1256817.8364
67 | 2746806.4597 | 1256770.4106 | 2746801.5289 | 1256785.2205 | 2746797.1699 | 1256801.0088
68 | 2746795.4034 | 1256825.6189 | 2746929.7981 | 1256922.2661
69 | 2746806.4597 | 1256770.4106 | 2746806.4612 | 1256770.4062 | 2746812.8246 | 1256752.3464 | 2746793.2163 | 1256736.1282
70 | 2746806.4597 | 1256770.4106 | 2746982.8997 | 1256689.3742
71 | 2746954.3407 | 1256940.4509 | 2746929.7981 | 1256922.2661
72 | 2746772.22 | 1256717.9787 | 2746781.7245 | 1256726.2056 | 2746792.183 | 1256735.2736 | 2746793.2163 | 1256736.1282
73 | 2746962.6635 | 1256948.9102 | 2746997.1353 | 1256978.9997
74 | 2747033.6985 | 1257002.5371 | 2746997.9168 | 1256979.6819 | 2746997.1353 | 1256978.9997
75 | 2746962.6635 | 1256948.9102 | 2746954.3407 | 1256940.4509
76 | 2746962.6635 | 1256948.9102 | 2746952.3947 | 1256968.9748 | 2746946.9021 | 1256978.6005
77 | 2747033.6985 | 1257002.5371 | 2747107.6711 | 1257051.1018
78 | 2746954.3407 | 1256940.4509 | 2746954.5914 | 1256934.7948
79 | 2746772.22 | 1256717.9787 | 2746759.2628 | 1256706.7632 | 2746750.0092 | 1256699.0456
80 | 2746735.2241 | 1256686.7147 | 2746750.0092 | 1256699.0456
81 | 2746529.1909 | 1256456.8896 | 2746539.8255 | 1256466.0975
82 | 2746529.1909 | 1256456.8896 | 2746512.979 | 1256467.1317 | 2746507.115 | 1256470.8458 | 2746486.718 | 1256483.7313 | 2746483.5041 | 1256485.762
83 | 2746529.1909 | 1256456.8896 | 2746523.2343 | 1256451.8485
84 | 2746629.7806 | 1256487.4933 | 2746628.7188 | 1256468.5092 | 2746622.4834 | 1256438.1921 | 2746622.253 | 1256436.7081
85 | 2746620.5975 | 1256425.0905 | 2746620.6811 | 1256426.5807 | 2746622.253 | 1256436.7081
86 | 2746619.7431 | 1256391.7248 | 2746619.2895 | 1256406.9272 | 2746619.1746 | 1256410.6502 | 2746619.8646 | 1256412.0353 | 2746620.5975 | 1256425.0905
87 | 2746620.5971 | 1256363.3063 | 2746619.8691 | 1256387.5005 | 2746619.7431 | 1256391.7248
88 | 2746620.5971 | 1256363.3063 | 2746587.3472 | 1256350.415 | 2746584.9632 | 1256349.4884 | 2746582.9447 | 1256349.038
89 | 2746523.2343 | 1256451.8485 | 2746513.1906 | 1256443.3584 | 2746509.6393 | 1256439.0653
90 | 2746502.8463 | 1256430.857 | 2746508.3628 | 1256437.5222 | 2746509.6393 | 1256439.0653
91 | 2746523.2343 | 1256451.8485 | 2746528.6918 | 1256447.4904 | 2746535.1413 | 1256446.0375 | 2746538.6643 | 1256445.7578
92 | 2746502.8463 | 1256430.857 | 2746518.0994 | 1256425.8184 | 2746521.8409 | 1256425.2389
93 | 2746502.8463 | 1256430.857 | 2746498.3848 | 1256425.4636 | 2746489.749 | 1256407.9552 | 2746487.1411 | 1256402.6634 | 2746486.9113 | 1256402.1975
94 | 2746569.4035 | 1256425.6658 | 2746560.0098 | 1256423.8315 | 2746546.4844 | 1256422.7846 | 2746530.9758 | 1256423.824 | 2746521.8409 | 1256425.2389
95 | 2746474.2147 | 1256361.5816 | 2746475.531 | 1256371.8019 | 2746479.8399 | 1256384.2761 | 2746483.9871 | 1256396.268 | 2746486.9113 | 1256402.1975
96 | 2746483.5041 | 1256485.762 | 2746479.8578 | 1256488.0658 | 2746475.8871 | 1256490.5811 | 2746472.9737 | 1256494.0328
97 | 2746450.456 | 1256379.8004 | 2746456.8831 | 1256375.9001 | 2746474.2147 | 1256361.5816
98 | 2746474.2147 | 1256361.5816 | 2746472.7318 | 1256355.0386 | 2746464.8662 | 1256320.3307
99 | 2746474.2147 | 1256361.5816 | 2746492.2618 | 1256355.7161
100 | 2746472.9737 | 1256494.0328 | 2746466.5877 | 1256501.5988
101 | 2746450.456 | 1256379.8004 | 2746440.2148 | 1256378.5574
102 | 2746450.456 | 1256379.8004 | 2746439.7627 | 1256392.9709 | 2746431.5832 | 1256403.0451 | 2746428.0575 | 1256407.3954 | 2746425.4039 | 1256410.6552 | 2746425.0222 | 1256411.2008
103 | 2746461.4779 | 1256305.3793 | 2746464.8662 | 1256320.3307
104 | 2746545.6273 | 1256344.2429 | 2746544.8059 | 1256344.345 | 2746516.5681 | 1256347.8162 | 2746492.2618 | 1256355.7161
105 | 2746466.5877 | 1256501.5988 | 2746462.4161 | 1256506.5411 | 2746455.4358 | 1256514.8098 | 2746453.559 | 1256517.803
106 | 2746582.9447 | 1256349.038 | 2746571.0216 | 1256346.3513 | 2746555.9771 | 1256342.9646 | 2746549.6574 | 1256343.7422 | 2746545.6273 | 1256344.2429
107 | 2746407.8629 | 1256362.6643 | 2746414.1749 | 1256367.1243 | 2746433.9963 | 1256377.8025 | 2746440.2148 | 1256378.5574
108 | 2746421.4417 | 1256416.3204 | 2746425.0222 | 1256411.2008
109 | 2746456.5833 | 1256283.7814 | 2746461.4779 | 1256305.3793
110 | 2746407.8629 | 1256362.6643 | 2746385.4985 | 1256346.8623 | 2746380.781 | 1256339.0164
111 | 2746406.4346 | 1256436.9558 | 2746408.2032 | 1256435.2425 | 2746412.7558 | 1256428.7265 | 2746417.5974 | 1256421.8173 | 2746421.4417 | 1256416.3204
112 | 2746456.5833 | 1256283.7814 | 2746452.2177 | 1256267.8024 | 2746447.7372 | 1256239.3974
113 | 2746453.559 | 1256517.803 | 2746450.1413 | 1256523.2537 | 2746448.834 | 1256525.1097
114 | 2746434.6421 | 1256545.2583 | 2746448.834 | 1256525.1097
115 | 2746406.4346 | 1256436.9558 | 2746403.8818 | 1256439.4286 | 2746403.3299 | 1256439.9652
116 | 2746389.541 | 1256453.343 | 2746389.541 | 1256453.343 | 2746394.6048 | 1256448.4301 | 2746398.8178 | 1256444.3526 | 2746403.3299 | 1256439.9652
117 | 2746389.541 | 1256453.343 | 2746388.105 | 1256454.0526 | 2746383.6597 | 1256456.2337 | 2746377.2897 | 1256459.3664
118 | 2746363.6707 | 1256466.0602 | 2746371.1713 | 1256462.3754 | 2746377.2897 | 1256459.3664
119 | 2746363.6707 | 1256466.0602 | 2746354.0187 | 1256465.8214 | 2746341.9736 | 1256463.1989 | 2746329.1275 | 1256455.1292 | 2746325.8675 | 1256452.4312
120 | 2746363.6707 | 1256466.0602 | 2746355.5626 | 1256477.5264 | 2746342.2318 | 1256491.8147
121 | 2746325.7227 | 1256452.3114 | 2746325.8675 | 1256452.4312
122 | 2746337.9452 | 1256496.4092 | 2746342.2318 | 1256491.8147
123 | 2746307.8845 | 1256437.565 | 2746310.5539 | 1256439.7664 | 2746321.7854 | 1256449.053 | 2746325.7227 | 1256452.3114
124 | 2746337.9452 | 1256496.4092 | 2746344.6527 | 1256501.6023 | 2746370.8103 | 1256516.9964
125 | 2746337.9452 | 1256496.4092 | 2746328.6658 | 1256502.4635 | 2746328.3054 | 1256502.6024
126 | 2746240.5203 | 1256565.1464 | 2746243.2775 | 1256573.8674 | 2746244.9226 | 1256581.1817 | 2746246.839 | 1256585.4554 | 2746248.8048 | 1256587.7284 | 2746250.3711 | 1256589.9915 | 2746252.2156 | 1256591.4086
127 | 2746240.5203 | 1256565.1464 | 2746247.5762 | 1256542.8213 | 2746248.8781 | 1256541.1459
128 | 2746240.5203 | 1256565.1464 | 2746237.9331 | 1256573.3571 | 2746237.3031 | 1256575.3526
129 | 2746248.8781 | 1256541.1459 | 2746256.3356 | 1256531.549 | 2746260.4383 | 1256529.0755
130 | 2746260.4383 | 1256529.0755 | 2746270.6891 | 1256522.8952 | 2746295.3176 | 1256514.43
131 | 2746260.4383 | 1256529.0755 | 2746223.5441 | 1256504.8425
132 | 2746318.5494 | 1256506.3617 | 2746299.6978 | 1256512.9245 | 2746295.3176 | 1256514.43
133 | 2746222.9295 | 1256504.259 | 2746223.5441 | 1256504.8425
134 | 2746318.5494 | 1256506.3617 | 2746328.3054 | 1256502.6024
135 | 2746382.7216 | 1256532.8624 | 2746375.6644 | 1256519.8532 | 2746370.8103 | 1256516.9964
136 | 2746382.7216 | 1256532.8624 | 2746382.7216 | 1256532.8624 | 2746383.8513 | 1256533.5577 | 2746389.678 | 1256537.1386 | 2746402.4749 | 1256544.9807
137 | 2746409.2027 | 1256549.1107 | 2746407.9097 | 1256548.3113 | 2746402.4749 | 1256544.9807
138 | 2746370.4897 | 1256321.9005 | 2746380.781 | 1256339.0164
139 | 2746307.8845 | 1256437.565 | 2746303.3797 | 1256434.4795
140 | 2746307.8845 | 1256437.565 | 2746293.2771 | 1256454.014
141 | 2746292.8786 | 1256454.4627 | 2746293.2771 | 1256454.014
142 | 2746276.0787 | 1256473.3806 | 2746292.8786 | 1256454.4627
143 | 2746303.3797 | 1256434.4795 | 2746296.1765 | 1256429.5458 | 2746291.9397 | 1256426.6494 | 2746282.4922 | 1256421.4999 | 2746280.9586 | 1256420.6612
144 | 2746265.7986 | 1256415.0273 | 2746267.153 | 1256415.3817 | 2746274.2015 | 1256418.0806 | 2746277.7592 | 1256419.4476 | 2746280.9586 | 1256420.6612 | 2746280.9586 | 1256420.6612
145 | 2746260.2159 | 1256413.5664 | 2746265.7986 | 1256415.0273
146 | 2746295.5777 | 1256344.838 | 2746272.3614 | 1256343.5688
147 | 2746295.5777 | 1256344.838 | 2746301.6428 | 1256346.3406
148 | 2746370.4897 | 1256321.9005 | 2746362.0199 | 1256307.127
149 | 2746370.4897 | 1256321.9005 | 2746354.7499 | 1256333.189 | 2746344.6697 | 1256338.8343
150 | 2746335.4455 | 1256344.0001 | 2746344.6697 | 1256338.8343
151 | 2746335.4455 | 1256344.0001 | 2746330.4494 | 1256346.7904 | 2746310.3891 | 1256348.5075 | 2746307.1832 | 1256347.7132
152 | 2746335.4455 | 1256344.0001 | 2746340.5493 | 1256352.4122 | 2746339.5009 | 1256362.2594
153 | 2746447.7372 | 1256239.3974 | 2746416.3193 | 1256253.3562 | 2746413.0827 | 1256256.3902 | 2746412.4457 | 1256261.7018 | 2746418.0879 | 1256276.9192
154 | 2746301.6428 | 1256346.3406 | 2746307.1832 | 1256347.7132
155 | 2746339.5009 | 1256362.2594 | 2746339.0338 | 1256366.6463
156 | 2746338.1707 | 1256374.7527 | 2746339.0338 | 1256366.6463

## bus_geodata
| x | y | coords
0 | 2746605.5969 | 1256738.1796
1 | 2746608.5069 | 1256712.8478
2 | 2746612.4829 | 1256671.8998
3 | 2746615.8207 | 1256640.757
4 | 2746621.2168 | 1256615.31
5 | 2746564.0971 | 1256758.1103
6 | 2746569.809 | 1256734.5953
7 | 2746573.8055 | 1256721.903
8 | 2746535.9136 | 1256713.128
9 | 2746507.4485 | 1256709.5783
10 | 2746491.6785 | 1256710.8739
11 | 2746482.5718 | 1256703.5638
12 | 2746484.3766 | 1256669.075
13 | 2746627.0229 | 1256597.1918
14 | 2746610.7991 | 1256621.9967
15 | 2746652.8552 | 1256572.3186
16 | 2746608.5481 | 1256553.6383
17 | 2746637.3508 | 1256619.6934
18 | 2746602.4152 | 1256625.332
19 | 2746486.3765 | 1256663.2037
20 | 2746488.7966 | 1256656.0991
21 | 2746493.6963 | 1256644.3821
22 | 2746496.608 | 1256638.5659
23 | 2746344.9283 | 1256585.8159
24 | 2746345.2294 | 1256585.7097
25 | 2746339.4581 | 1256587.7445
26 | 2746316.1935 | 1256573.8466
27 | 2746299.748 | 1256560.3785
28 | 2746291.4802 | 1256554.4505
29 | 2746502.2486 | 1256629.0775
30 | 2746518.7391 | 1256615.1276
31 | 2746548.2307 | 1256609.1987
32 | 2746555.4992 | 1256610.8887
33 | 2746655.9547 | 1256569.3369
34 | 2746692.7819 | 1256594.8357
35 | 2746606.2755 | 1256549.7128
36 | 2746661.485 | 1256659.1165
37 | 2746592.894 | 1256526.5988
38 | 2746562.3203 | 1256485.5818
39 | 2746517.7222 | 1256543.701
40 | 2746555.0667 | 1256479.2962
41 | 2746541.2904 | 1256467.3659
42 | 2746510.9625 | 1256520.5224
43 | 2746571.3465 | 1256465.3451
44 | 2746668.5917 | 1256670.5015
45 | 2746643.4553 | 1256689.1323
46 | 2746672.6275 | 1256676.9742
47 | 2746637.5509 | 1256687.1731
48 | 2746677.6348 | 1256684.4826
49 | 2746650.0331 | 1256558.6246
50 | 2746695.9318 | 1256596.587
51 | 2746647.5199 | 1256760.8256
52 | 2746680.36 | 1256732.2557
53 | 2746626.0811 | 1256770.3251
54 | 2746680.5895 | 1256732.056
55 | 2746701.2803 | 1256714.0556
56 | 2746715.276 | 1256731.5974
57 | 2746743.1584 | 1256764.8839
58 | 2746755.3422 | 1256778.7247
59 | 2746728.117 | 1256797.549
60 | 2746655.9397 | 1256790.2618
61 | 2746771.7584 | 1256797.5093
62 | 2746788.346 | 1256817.8364
63 | 2746797.1699 | 1256801.0088
64 | 2746795.4034 | 1256825.6189
65 | 2746806.4597 | 1256770.4106
66 | 2746929.7981 | 1256922.2661
67 | 2746793.2163 | 1256736.1282
68 | 2746982.8997 | 1256689.3742
69 | 2746997.1353 | 1256978.9997
70 | 2746962.6635 | 1256948.9102
71 | 2747033.6985 | 1257002.5371
72 | 2746954.3407 | 1256940.4509
73 | 2746946.9021 | 1256978.6005
74 | 2746954.5914 | 1256934.7948
75 | 2746772.22 | 1256717.9787
76 | 2746750.0092 | 1256699.0456
77 | 2746735.2241 | 1256686.7147
78 | 2747107.6711 | 1257051.1018
79 | 2746644.8323 | 1256549.2163
80 | 2746589.7222 | 1256457.9668
81 | 2746539.8255 | 1256466.0975
82 | 2746529.1909 | 1256456.8896
83 | 2746629.7806 | 1256487.4933
84 | 2746622.253 | 1256436.7081
85 | 2746620.5975 | 1256425.0905
86 | 2746619.7431 | 1256391.7248
87 | 2746620.5971 | 1256363.3063
88 | 2746509.6393 | 1256439.0653
89 | 2746523.2343 | 1256451.8485
90 | 2746502.8463 | 1256430.857
91 | 2746538.6643 | 1256445.7578
92 | 2746521.8409 | 1256425.2389
93 | 2746486.9113 | 1256402.1975
94 | 2746483.5041 | 1256485.762
95 | 2746569.4035 | 1256425.6658
96 | 2746474.2147 | 1256361.5816
97 | 2746472.9737 | 1256494.0328
98 | 2746450.456 | 1256379.8004
99 | 2746464.8662 | 1256320.3307
100 | 2746492.2618 | 1256355.7161
101 | 2746466.5877 | 1256501.5988
102 | 2746582.9447 | 1256349.038
103 | 2746545.6273 | 1256344.2429
104 | 2746440.2148 | 1256378.5574
105 | 2746425.0222 | 1256411.2008
106 | 2746461.4779 | 1256305.3793
107 | 2746407.8629 | 1256362.6643
108 | 2746421.4417 | 1256416.3204
109 | 2746456.5833 | 1256283.7814
110 | 2746453.559 | 1256517.803
111 | 2746448.834 | 1256525.1097
112 | 2746434.6421 | 1256545.2583
113 | 2746406.4346 | 1256436.9558
114 | 2746403.3299 | 1256439.9652
115 | 2746389.541 | 1256453.343
116 | 2746377.2897 | 1256459.3664
117 | 2746363.6707 | 1256466.0602
118 | 2746325.8675 | 1256452.4312
119 | 2746342.2318 | 1256491.8147
120 | 2746325.7227 | 1256452.3114
121 | 2746337.9452 | 1256496.4092
122 | 2746252.2156 | 1256591.4086
123 | 2746240.5203 | 1256565.1464
124 | 2746248.8781 | 1256541.1459
125 | 2746237.3031 | 1256575.3526
126 | 2746260.4383 | 1256529.0755
127 | 2746295.3176 | 1256514.43
128 | 2746223.5441 | 1256504.8425
129 | 2746318.5494 | 1256506.3617
130 | 2746222.9295 | 1256504.259
131 | 2746328.3054 | 1256502.6024
132 | 2746370.8103 | 1256516.9964
133 | 2746382.7216 | 1256532.8624
134 | 2746402.4749 | 1256544.9807
135 | 2746409.2027 | 1256549.1107
136 | 2746380.781 | 1256339.0164
137 | 2746307.8845 | 1256437.565
138 | 2746292.8786 | 1256454.4627
139 | 2746293.2771 | 1256454.014
140 | 2746276.0787 | 1256473.3806
141 | 2746303.3797 | 1256434.4795
142 | 2746280.9586 | 1256420.6612
143 | 2746265.7986 | 1256415.0273
144 | 2746260.2159 | 1256413.5664
145 | 2746272.3614 | 1256343.5688
146 | 2746295.5777 | 1256344.838
147 | 2746370.4897 | 1256321.9005
148 | 2746362.0199 | 1256307.127
149 | 2746344.6697 | 1256338.8343
150 | 2746335.4455 | 1256344.0001
151 | 2746447.7372 | 1256239.3974
152 | 2746418.0879 | 1256276.9192
153 | 2746307.1832 | 1256347.7132
154 | 2746339.5009 | 1256362.2594
155 | 2746339.0338 | 1256366.6463
156 | 2746338.1707 | 1256374.7527
157 | 2746301.6428 | 1256346.3406
158 | 2746434.6421 | 1256545.2583

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1