## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3203-20_1_2_node_13 | 0.4 | n |  | TRUE
1 | bus_LV_3203-20_1_2_node_19 | 0.4 | n |  | TRUE
2 | bus_LV_3203-20_1_2_node_106 | 0.4 | n |  | TRUE
3 | bus_LV_3203-20_1_2_node_105 | 0.4 | n |  | TRUE
4 | bus_LV_3203-20_1_2_node_18 | 0.4 | n |  | TRUE
5 | bus_LV_3203-20_1_2_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_3203-20_1_2_node_57 | 0.4 | n |  | TRUE
7 | bus_LV_3203-20_1_2_node_107 | 0.4 | n |  | TRUE
8 | bus_LV_3203-20_1_2_node_102 | 0.4 | n |  | TRUE
9 | bus_LV_3203-20_1_2_node_103 | 0.4 | n |  | TRUE
10 | bus_LV_3203-20_1_2_node_101 | 0.4 | n |  | TRUE
11 | bus_LV_3203-20_1_2_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_3203-20_1_2_node_59 | 0.4 | n |  | TRUE
13 | bus_LV_3203-20_1_2_node_60 | 0.4 | n |  | TRUE
14 | bus_LV_3203-20_1_2_node_62 | 0.4 | n |  | TRUE
15 | bus_LV_3203-20_1_2_node_64 | 0.4 | n |  | TRUE
16 | bus_LV_3203-20_1_2_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_3203-20_1_2_node_67 | 0.4 | n |  | TRUE
18 | bus_LV_3203-20_1_2_node_68 | 0.4 | n |  | TRUE
19 | bus_LV_3203-20_1_2_node_69 | 0.4 | n |  | TRUE
20 | bus_LV_3203-20_1_2_node_66 | 0.4 | n |  | TRUE
21 | bus_LV_3203-20_1_2_node_97 | 0.4 | n |  | TRUE
22 | bus_LV_3203-20_1_2_node_70 | 0.4 | n |  | TRUE
23 | bus_LV_3203-20_1_2_node_100 | 0.4 | n |  | TRUE
24 | bus_LV_3203-20_1_2_node_71 | 0.4 | n |  | TRUE
25 | bus_LV_3203-20_1_2_node_72 | 0.4 | n |  | TRUE
26 | bus_LV_3203-20_1_2_node_73 | 0.4 | n |  | TRUE
27 | bus_LV_3203-20_1_2_node_88 | 0.4 | n |  | TRUE
28 | bus_LV_3203-20_1_2_node_99 | 0.4 | n |  | TRUE
29 | bus_LV_3203-20_1_2_node_91 | 0.4 | n |  | TRUE
30 | bus_LV_3203-20_1_2_node_90 | 0.4 | n |  | TRUE
31 | bus_LV_3203-20_1_2_node_92 | 0.4 | n |  | TRUE
32 | bus_LV_3203-20_1_2_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_3203-20_1_2_node_93 | 0.4 | n |  | TRUE
34 | bus_LV_3203-20_1_2_node_94 | 0.4 | n |  | TRUE
35 | bus_LV_3203-20_1_2_node_95 | 0.4 | n |  | TRUE
36 | bus_LV_3203-20_1_2_node_96 | 0.4 | n |  | TRUE
37 | bus_LV_3203-20_1_2_node_111 | 0.4 | n |  | TRUE
38 | bus_LV_3203-20_1_2_node_104 | 0.4 | n |  | TRUE
39 | bus_LV_3203-20_1_2_node_112 | 0.4 | n |  | TRUE
40 | bus_MV_583_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3203-20_1_2_load_106 | 2 | 0.012581 | 0.0031531 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3203-20_1_2_load_105 | 3 | 0.00068015 | 0.00017046 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3203-20_1_2_load_57 | 6 | 0.068037 | 0.017052 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3203-20_1_2_load_107 | 7 | 0.0011923 | 0.00029882 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3203-20_1_2_load_103 | 9 | 0.0027223 | 0.00068228 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3203-20_1_2_load_101 | 10 | 0.002643 | 0.0006624 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3203-20_1_2_load_58 | 11 | 0.0045676 | 0.0011448 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3203-20_1_2_load_59 | 12 | 0.0011909 | 0.00029847 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3203-20_1_2_load_60 | 13 | 0.018898 | 0.0047363 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3203-20_1_2_load_65 | 16 | 0.036443 | 0.0091335 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3203-20_1_2_load_67 | 17 | 0.011888 | 0.0029793 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3203-20_1_2_load_68 | 18 | 0.002851 | 0.00071454 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3203-20_1_2_load_69 | 19 | 0.0046074 | 0.0011547 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3203-20_1_2_load_66 | 20 | 0.0013863 | 0.00034744 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3203-20_1_2_load_70 | 22 | 0.0031036 | 0.00077782 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3203-20_1_2_load_100 | 23 | 0.00067138 | 0.00016826 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3203-20_1_2_load_71 | 24 | 0.0050169 | 0.0012573 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3203-20_1_2_load_72 | 25 | 0.0010377 | 0.00026007 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3203-20_1_2_load_99 | 28 | 0.0012181 | 0.00030529 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3203-20_1_2_load_90 | 30 | 0.0013378 | 0.00033529 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3203-20_1_2_load_92 | 31 | 0.0039338 | 0.00098591 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3203-20_1_2_load_98 | 32 | 0.0028933 | 0.00072514 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3203-20_1_2_load_93 | 33 | 0.011522 | 0.0028876 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3203-20_1_2_load_94 | 34 | 0.0056781 | 0.0014231 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3203-20_1_2_load_95 | 35 | 0.0033142 | 0.00083062 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3203-20_1_2_load_96 | 36 | 0.0046158 | 0.0011568 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3203-20_1_2_load_111 | 37 | 0.002755 | 0.00069046 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3203-20_1_2_load_104 | 38 | 0.00057134 | 0.00014319 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3203-20_1_2_load_112 | 39 | 0.00073247 | 0.00018357 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3203-20_1_2_line_0 |  | 0 | 1 | 0.005353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3203-20_1_2_line_1 |  | 0 | 2 | 0.0054194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3203-20_1_2_line_2 |  | 0 | 3 | 0.045716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3203-20_1_2_line_3 |  | 1 | 7 | 0.040182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3203-20_1_2_line_4 |  | 3 | 38 | 0.025191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3203-20_1_2_line_5 |  | 4 | 5 | 0.056559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3203-20_1_2_line_6 |  | 4 | 6 | 0.044382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3203-20_1_2_line_7 |  | 5 | 8 | 0.010508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3203-20_1_2_line_8 |  | 5 | 9 | 0.025922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3203-20_1_2_line_9 |  | 5 | 10 | 0.017559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3203-20_1_2_line_10 |  | 6 | 11 | 0.042367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3203-20_1_2_line_11 |  | 8 | 38 | 0.028096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3203-20_1_2_line_12 |  | 9 | 39 | 0.0019302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3203-20_1_2_line_13 |  | 10 | 23 | 0.0061616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3203-20_1_2_line_14 |  | 12 | 13 | 0.03471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3203-20_1_2_line_15 |  | 13 | 14 | 0.061085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3203-20_1_2_line_16 |  | 14 | 15 | 0.0124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3203-20_1_2_line_17 |  | 14 | 16 | 0.010639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3203-20_1_2_line_18 |  | 15 | 17 | 0.023468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3203-20_1_2_line_19 |  | 15 | 18 | 0.018964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3203-20_1_2_line_20 |  | 16 | 19 | 0.015748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3203-20_1_2_line_21 |  | 17 | 22 | 0.0080083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3203-20_1_2_line_22 |  | 18 | 23 | 0.029304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3203-20_1_2_line_23 |  | 20 | 21 | 0.010585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3203-20_1_2_line_24 |  | 21 | 26 | 0.018903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3203-20_1_2_line_25 |  | 21 | 36 | 0.0011708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3203-20_1_2_line_26 |  | 22 | 24 | 0.030376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3203-20_1_2_line_27 |  | 24 | 25 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3203-20_1_2_line_28 |  | 25 | 26 | 0.0074527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3203-20_1_2_line_29 |  | 27 | 28 | 0.01573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3203-20_1_2_line_30 |  | 27 | 29 | 0.005136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3203-20_1_2_line_31 |  | 28 | 37 | 0.011018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3203-20_1_2_line_32 |  | 29 | 31 | 0.017434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3203-20_1_2_line_33 |  | 29 | 30 | 0.030771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3203-20_1_2_line_34 |  | 31 | 32 | 0.0062614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3203-20_1_2_line_35 |  | 33 | 34 | 0.027228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3203-20_1_2_line_36 |  | 34 | 35 | 0.019283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3203-20_1_2_line_37 |  | 35 | 36 | 0.029009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3203-20_1_2_line_38 |  | 37 | 39 | 0.016339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3203-20_1_2_trafo_101 | 0.63 MVA 20/0.4 kV | 40 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2746988.7723 | 1254661.4782 | 2746989.5379 | 1254656.181
1 | 2746988.7723 | 1254661.4782 | 2746987.9976 | 1254666.8419
2 | 2746988.7723 | 1254661.4782 | 2746999.8869 | 1254661.5986 | 2747033.8083 | 1254668.4227
3 | 2746989.5379 | 1254656.181 | 2747005.8605 | 1254619.4632
4 | 2747058.5046 | 1254673.391 | 2747033.8083 | 1254668.4227
5 | 2747094.7307 | 1254635.4392 | 2747108.5999 | 1254641.0335 | 2747096.4179 | 1254680.8138
6 | 2747094.7307 | 1254635.4392 | 2747060.836 | 1254618.3699 | 2747054.8977 | 1254615.8987
7 | 2747086.0491 | 1254678.9322 | 2747096.4179 | 1254680.8138
8 | 2747096.4179 | 1254680.8138 | 2747121.9576 | 1254685.2472
9 | 2747096.4179 | 1254680.8138 | 2747088.466 | 1254696.4686
10 | 2747054.8977 | 1254615.8987 | 2747034.488 | 1254607.4052 | 2747026.6315 | 1254626.0808
11 | 2747086.0491 | 1254678.9322 | 2747058.5046 | 1254673.391
12 | 2747123.8593 | 1254685.5774 | 2747121.9576 | 1254685.2472
13 | 2747085.6756 | 1254701.962 | 2747088.466 | 1254696.4686
14 | 2747127.0334 | 1254810.0669 | 2747102.847 | 1254785.1715
15 | 2747061.2591 | 1254740.4315 | 2747100.6351 | 1254782.8948 | 2747102.847 | 1254785.1715
16 | 2747061.2591 | 1254740.4315 | 2747068.9142 | 1254741.5671 | 2747073.5799 | 1254742.1168
17 | 2747061.2591 | 1254740.4315 | 2747051.3087 | 1254736.6652
18 | 2747073.5799 | 1254742.1168 | 2747096.8857 | 1254744.8751
19 | 2747073.5799 | 1254742.1168 | 2747074.6087 | 1254735.6473 | 2747069.3491 | 1254734.3932 | 2747072.2612 | 1254728.3708 | 2747072.4044 | 1254728.0889
20 | 2747051.3087 | 1254736.6652 | 2747046.4469 | 1254734.825 | 2747036.7234 | 1254730.7325
21 | 2747104.8385 | 1254745.8163 | 2747096.8857 | 1254744.8751
22 | 2747085.6756 | 1254701.962 | 2747072.4044 | 1254728.0889
23 | 2747175.7175 | 1254755.5559 | 2747177.6701 | 1254765.9589
24 | 2747175.7175 | 1254755.5559 | 2747157.0958 | 1254752.0008
25 | 2747175.7175 | 1254755.5559 | 2747176.8598 | 1254755.8123
26 | 2747104.8385 | 1254745.8163 | 2747135.0035 | 1254749.3863
27 | 2747149.6947 | 1254751.1249 | 2747135.0035 | 1254749.3863
28 | 2747157.0958 | 1254752.0008 | 2747149.6947 | 1254751.1249
29 | 2747166.3254 | 1254692.862 | 2747150.8161 | 1254690.2374
30 | 2747171.4064 | 1254693.7113 | 2747166.3254 | 1254692.862
31 | 2747150.8161 | 1254690.2374 | 2747146.3707 | 1254689.4852 | 2747139.9574 | 1254688.3719
32 | 2747171.4064 | 1254693.7113 | 2747167.2823 | 1254710.6508
33 | 2747171.4064 | 1254693.7113 | 2747180.6751 | 1254697.9457 | 2747200.9043 | 1254701.7329
34 | 2747167.2823 | 1254710.6508 | 2747165.8012 | 1254716.7345
35 | 2747249.52 | 1254776.2042 | 2747230.7634 | 1254770.0157 | 2747223.582 | 1254767.9339
36 | 2747205.0615 | 1254762.5649 | 2747223.582 | 1254767.9339
37 | 2747205.0615 | 1254762.5649 | 2747198.6168 | 1254760.6966 | 2747176.8598 | 1254755.8123
38 | 2747123.8593 | 1254685.5774 | 2747139.9574 | 1254688.3719

## bus_geodata
| x | y | coords
0 | 2746988.7723 | 1254661.4782
1 | 2746989.5379 | 1254656.181
2 | 2746987.9976 | 1254666.8419
3 | 2747033.8083 | 1254668.4227
4 | 2747094.7307 | 1254635.4392
5 | 2747096.4179 | 1254680.8138
6 | 2747054.8977 | 1254615.8987
7 | 2747005.8605 | 1254619.4632
8 | 2747086.0491 | 1254678.9322
9 | 2747121.9576 | 1254685.2472
10 | 2747088.466 | 1254696.4686
11 | 2747026.6315 | 1254626.0808
12 | 2747127.0334 | 1254810.0669
13 | 2747102.847 | 1254785.1715
14 | 2747061.2591 | 1254740.4315
15 | 2747073.5799 | 1254742.1168
16 | 2747051.3087 | 1254736.6652
17 | 2747096.8857 | 1254744.8751
18 | 2747072.4044 | 1254728.0889
19 | 2747036.7234 | 1254730.7325
20 | 2747177.6701 | 1254765.9589
21 | 2747175.7175 | 1254755.5559
22 | 2747104.8385 | 1254745.8163
23 | 2747085.6756 | 1254701.962
24 | 2747135.0035 | 1254749.3863
25 | 2747149.6947 | 1254751.1249
26 | 2747157.0958 | 1254752.0008
27 | 2747166.3254 | 1254692.862
28 | 2747150.8161 | 1254690.2374
29 | 2747171.4064 | 1254693.7113
30 | 2747200.9043 | 1254701.7329
31 | 2747167.2823 | 1254710.6508
32 | 2747165.8012 | 1254716.7345
33 | 2747249.52 | 1254776.2042
34 | 2747223.582 | 1254767.9339
35 | 2747205.0615 | 1254762.5649
36 | 2747176.8598 | 1254755.8123
37 | 2747139.9574 | 1254688.3719
38 | 2747058.5046 | 1254673.391
39 | 2747123.8593 | 1254685.5774
40 | 2747096.4179 | 1254680.8138

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1