## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3217-4_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3217-4_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3217-4_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3217-4_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3217-4_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_3217-4_0_6_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_3217-4_0_6_node_122 | 0.4 | n |  | TRUE
7 | bus_LV_3217-4_0_6_node_92 | 0.4 | n |  | TRUE
8 | bus_LV_3217-4_0_6_node_120 | 0.4 | n |  | TRUE
9 | bus_LV_3217-4_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_3217-4_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_3217-4_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_3217-4_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_3217-4_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_3217-4_0_6_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_3217-4_0_6_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_3217-4_0_6_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_3217-4_0_6_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_3217-4_0_6_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_3217-4_0_6_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_3217-4_0_6_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_3217-4_0_6_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_3217-4_0_6_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_3217-4_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_3217-4_0_6_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_3217-4_0_6_node_138 | 0.4 | n |  | TRUE
26 | bus_LV_3217-4_0_6_node_139 | 0.4 | n |  | TRUE
27 | bus_LV_3217-4_0_6_node_136 | 0.4 | n |  | TRUE
28 | bus_LV_3217-4_0_6_node_173 | 0.4 | n |  | TRUE
29 | bus_LV_3217-4_0_6_node_167 | 0.4 | n |  | TRUE
30 | bus_LV_3217-4_0_6_node_129 | 0.4 | n |  | TRUE
31 | bus_LV_3217-4_0_6_node_142 | 0.4 | n |  | TRUE
32 | bus_LV_3217-4_0_6_node_130 | 0.4 | n |  | TRUE
33 | bus_LV_3217-4_0_6_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_3217-4_0_6_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_3217-4_0_6_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_3217-4_0_6_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_3217-4_0_6_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_3217-4_0_6_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_3217-4_0_6_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_3217-4_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_3217-4_0_6_node_89 | 0.4 | n |  | TRUE
42 | bus_LV_3217-4_0_6_node_84 | 0.4 | n |  | TRUE
43 | bus_LV_3217-4_0_6_node_90 | 0.4 | n |  | TRUE
44 | bus_LV_3217-4_0_6_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_3217-4_0_6_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_3217-4_0_6_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_3217-4_0_6_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_3217-4_0_6_node_85 | 0.4 | n |  | TRUE
49 | bus_LV_3217-4_0_6_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_3217-4_0_6_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_3217-4_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_3217-4_0_6_node_128 | 0.4 | n |  | TRUE
53 | bus_LV_3217-4_0_6_node_127 | 0.4 | n |  | TRUE
54 | bus_LV_3217-4_0_6_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_3217-4_0_6_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_3217-4_0_6_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_3217-4_0_6_node_58 | 0.4 | n |  | TRUE
58 | bus_LV_3217-4_0_6_node_62 | 0.4 | n |  | TRUE
59 | bus_LV_3217-4_0_6_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_3217-4_0_6_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_3217-4_0_6_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_3217-4_0_6_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_3217-4_0_6_node_44 | 0.4 | n |  | TRUE
64 | bus_LV_3217-4_0_6_node_46 | 0.4 | n |  | TRUE
65 | bus_LV_3217-4_0_6_node_83 | 0.4 | n |  | TRUE
66 | bus_LV_3217-4_0_6_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_3217-4_0_6_node_70 | 0.4 | n |  | TRUE
68 | bus_LV_3217-4_0_6_node_152 | 0.4 | n |  | TRUE
69 | bus_LV_3217-4_0_6_node_71 | 0.4 | n |  | TRUE
70 | bus_LV_3217-4_0_6_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_3217-4_0_6_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_3217-4_0_6_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_3217-4_0_6_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_3217-4_0_6_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_3217-4_0_6_node_76 | 0.4 | n |  | TRUE
76 | bus_LV_3217-4_0_6_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_3217-4_0_6_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_3217-4_0_6_node_50 | 0.4 | n |  | TRUE
79 | bus_LV_3217-4_0_6_node_51 | 0.4 | n |  | TRUE
80 | bus_LV_3217-4_0_6_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_3217-4_0_6_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_3217-4_0_6_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_3217-4_0_6_node_135 | 0.4 | n |  | TRUE
84 | bus_LV_3217-4_0_6_node_132 | 0.4 | n |  | TRUE
85 | bus_LV_3217-4_0_6_node_137 | 0.4 | n |  | TRUE
86 | bus_LV_3217-4_0_6_node_131 | 0.4 | n |  | TRUE
87 | bus_LV_3217-4_0_6_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_3217-4_0_6_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_3217-4_0_6_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_3217-4_0_6_node_64 | 0.4 | n |  | TRUE
91 | bus_LV_3217-4_0_6_node_66 | 0.4 | n |  | TRUE
92 | bus_LV_3217-4_0_6_node_68 | 0.4 | n |  | TRUE
93 | bus_LV_3217-4_0_6_node_69 | 0.4 | n |  | TRUE
94 | bus_LV_3217-4_0_6_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_3217-4_0_6_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_3217-4_0_6_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_3217-4_0_6_node_77 | 0.4 | n |  | TRUE
98 | bus_LV_3217-4_0_6_node_153 | 0.4 | n |  | TRUE
99 | bus_LV_3217-4_0_6_node_154 | 0.4 | n |  | TRUE
100 | bus_LV_3217-4_0_6_node_75 | 0.4 | n |  | TRUE
101 | bus_LV_3217-4_0_6_node_183 | 0.4 | n |  | TRUE
102 | bus_LV_3217-4_0_6_node_184 | 0.4 | n |  | TRUE
103 | bus_LV_3217-4_0_6_node_78 | 0.4 | n |  | TRUE
104 | bus_LV_3217-4_0_6_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_3217-4_0_6_node_80 | 0.4 | n |  | TRUE
106 | bus_LV_3217-4_0_6_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_3217-4_0_6_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_3217-4_0_6_node_86 | 0.4 | n |  | TRUE
109 | bus_LV_3217-4_0_6_node_87 | 0.4 | n |  | TRUE
110 | bus_LV_3217-4_0_6_node_88 | 0.4 | n |  | TRUE
111 | bus_LV_3217-4_0_6_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_3217-4_0_6_node_93 | 0.4 | n |  | TRUE
113 | bus_LV_3217-4_0_6_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_3217-4_0_6_node_95 | 0.4 | n |  | TRUE
115 | bus_LV_3217-4_0_6_node_96 | 0.4 | n |  | TRUE
116 | bus_LV_3217-4_0_6_node_97 | 0.4 | n |  | TRUE
117 | bus_LV_3217-4_0_6_node_98 | 0.4 | n |  | TRUE
118 | bus_LV_3217-4_0_6_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_3217-4_0_6_node_100 | 0.4 | n |  | TRUE
120 | bus_LV_3217-4_0_6_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_3217-4_0_6_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_3217-4_0_6_node_103 | 0.4 | n |  | TRUE
123 | bus_LV_3217-4_0_6_node_104 | 0.4 | n |  | TRUE
124 | bus_LV_3217-4_0_6_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_3217-4_0_6_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_3217-4_0_6_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_3217-4_0_6_node_107 | 0.4 | n |  | TRUE
128 | bus_LV_3217-4_0_6_node_105 | 0.4 | n |  | TRUE
129 | bus_LV_3217-4_0_6_node_111 | 0.4 | n |  | TRUE
130 | bus_LV_3217-4_0_6_node_125 | 0.4 | n |  | TRUE
131 | bus_LV_3217-4_0_6_node_106 | 0.4 | n |  | TRUE
132 | bus_LV_3217-4_0_6_node_112 | 0.4 | n |  | TRUE
133 | bus_LV_3217-4_0_6_node_126 | 0.4 | n |  | TRUE
134 | bus_LV_3217-4_0_6_node_113 | 0.4 | n |  | TRUE
135 | bus_LV_3217-4_0_6_node_114 | 0.4 | n |  | TRUE
136 | bus_LV_3217-4_0_6_node_115 | 0.4 | n |  | TRUE
137 | bus_LV_3217-4_0_6_node_116 | 0.4 | n |  | TRUE
138 | bus_LV_3217-4_0_6_node_117 | 0.4 | n |  | TRUE
139 | bus_LV_3217-4_0_6_node_121 | 0.4 | n |  | TRUE
140 | bus_LV_3217-4_0_6_node_118 | 0.4 | n |  | TRUE
141 | bus_LV_3217-4_0_6_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_3217-4_0_6_node_119 | 0.4 | n |  | TRUE
143 | bus_LV_3217-4_0_6_node_124 | 0.4 | n |  | TRUE
144 | bus_LV_3217-4_0_6_node_171 | 0.4 | n |  | TRUE
145 | bus_LV_3217-4_0_6_node_189 | 0.4 | n |  | TRUE
146 | bus_LV_3217-4_0_6_node_188 | 0.4 | n |  | TRUE
147 | bus_LV_3217-4_0_6_node_169 | 0.4 | n |  | TRUE
148 | bus_LV_3217-4_0_6_node_133 | 0.4 | n |  | TRUE
149 | bus_LV_3217-4_0_6_node_134 | 0.4 | n |  | TRUE
150 | bus_LV_3217-4_0_6_node_151 | 0.4 | n |  | TRUE
151 | bus_LV_3217-4_0_6_node_150 | 0.4 | n |  | TRUE
152 | bus_LV_3217-4_0_6_node_140 | 0.4 | n |  | TRUE
153 | bus_LV_3217-4_0_6_node_141 | 0.4 | n |  | TRUE
154 | bus_LV_3217-4_0_6_node_143 | 0.4 | n |  | TRUE
155 | bus_LV_3217-4_0_6_node_144 | 0.4 | n |  | TRUE
156 | bus_LV_3217-4_0_6_node_145 | 0.4 | n |  | TRUE
157 | bus_LV_3217-4_0_6_node_146 | 0.4 | n |  | TRUE
158 | bus_LV_3217-4_0_6_node_147 | 0.4 | n |  | TRUE
159 | bus_LV_3217-4_0_6_node_148 | 0.4 | n |  | TRUE
160 | bus_LV_3217-4_0_6_node_149 | 0.4 | n |  | TRUE
161 | bus_LV_3217-4_0_6_node_155 | 0.4 | n |  | TRUE
162 | bus_LV_3217-4_0_6_node_156 | 0.4 | n |  | TRUE
163 | bus_LV_3217-4_0_6_node_157 | 0.4 | n |  | TRUE
164 | bus_LV_3217-4_0_6_node_158 | 0.4 | n |  | TRUE
165 | bus_LV_3217-4_0_6_node_159 | 0.4 | n |  | TRUE
166 | bus_LV_3217-4_0_6_node_160 | 0.4 | n |  | TRUE
167 | bus_LV_3217-4_0_6_node_163 | 0.4 | n |  | TRUE
168 | bus_LV_3217-4_0_6_node_168 | 0.4 | n |  | TRUE
169 | bus_LV_3217-4_0_6_node_161 | 0.4 | n |  | TRUE
170 | bus_LV_3217-4_0_6_node_162 | 0.4 | n |  | TRUE
171 | bus_LV_3217-4_0_6_node_164 | 0.4 | n |  | TRUE
172 | bus_LV_3217-4_0_6_node_165 | 0.4 | n |  | TRUE
173 | bus_LV_3217-4_0_6_node_170 | 0.4 | n |  | TRUE
174 | bus_LV_3217-4_0_6_node_166 | 0.4 | n |  | TRUE
175 | bus_LV_3217-4_0_6_node_172 | 0.4 | n |  | TRUE
176 | bus_LV_3217-4_0_6_node_174 | 0.4 | n |  | TRUE
177 | bus_LV_3217-4_0_6_node_190 | 0.4 | n |  | TRUE
178 | bus_LV_3217-4_0_6_node_187 | 0.4 | n |  | TRUE
179 | bus_LV_3217-4_0_6_node_175 | 0.4 | n |  | TRUE
180 | bus_LV_3217-4_0_6_node_176 | 0.4 | n |  | TRUE
181 | bus_LV_3217-4_0_6_node_177 | 0.4 | n |  | TRUE
182 | bus_LV_3217-4_0_6_node_180 | 0.4 | n |  | TRUE
183 | bus_LV_3217-4_0_6_node_178 | 0.4 | n |  | TRUE
184 | bus_LV_3217-4_0_6_node_181 | 0.4 | n |  | TRUE
185 | bus_LV_3217-4_0_6_node_179 | 0.4 | n |  | TRUE
186 | bus_LV_3217-4_0_6_node_182 | 0.4 | n |  | TRUE
187 | bus_LV_3217-4_0_6_node_186 | 0.4 | n |  | TRUE
188 | bus_LV_3217-4_0_6_node_185 | 0.4 | n |  | TRUE
189 | bus_LV_3217-4_0_6_node_192 | 0.4 | n |  | TRUE
190 | bus_LV_3217-4_0_6_node_191 | 0.4 | n |  | TRUE
191 | bus_MV_48_0_node_165 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3217-4_0_6_load_0 | 0 | 0.0038332 | 0.0009607 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3217-4_0_6_load_3 | 3 | 0.0019875 | 0.0004981 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3217-4_0_6_load_6 | 5 | 0.0021227 | 0.00053199 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3217-4_0_6_load_120 | 8 | 0.0064014 | 0.0016043 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3217-4_0_6_load_7 | 9 | 0.00023474 | 5.8832e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3217-4_0_6_load_10 | 12 | 0.0013503 | 0.00033843 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3217-4_0_6_load_11 | 13 | 0.00025556 | 6.4048e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3217-4_0_6_load_17 | 14 | 0.0017057 | 0.0004275 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3217-4_0_6_load_18 | 15 | 0.0014549 | 0.00036463 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3217-4_0_6_load_14 | 16 | 0.00062533 | 0.00015672 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3217-4_0_6_load_12 | 17 | 0.0018923 | 0.00047427 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3217-4_0_6_load_22 | 19 | 0.00030837 | 7.7285e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3217-4_0_6_load_20 | 20 | 0.0014905 | 0.00037355 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3217-4_0_6_load_21 | 22 | 0.00032673 | 8.1885e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3217-4_0_6_load_16 | 23 | 0.0003323 | 8.3282e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3217-4_0_6_load_15 | 24 | 0.0008257 | 0.00020694 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3217-4_0_6_load_138 | 25 | 0.0021374 | 0.00053569 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3217-4_0_6_load_139 | 26 | 0.0010814 | 0.00027104 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3217-4_0_6_load_136 | 27 | 0.0014523 | 0.00036399 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3217-4_0_6_load_167 | 29 | 0.0029013 | 0.00072714 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3217-4_0_6_load_129 | 30 | 0.00091192 | 0.00022855 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3217-4_0_6_load_142 | 31 | 0.0063259 | 0.0015854 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3217-4_0_6_load_23 | 33 | 0.0012268 | 0.00030747 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3217-4_0_6_load_26 | 35 | 0.0023443 | 0.00058753 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3217-4_0_6_load_28 | 37 | 0.00070404 | 0.00017645 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3217-4_0_6_load_29 | 38 | 0.0041497 | 0.00104 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3217-4_0_6_load_31 | 40 | 0.00051964 | 0.00013023 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3217-4_0_6_load_89 | 41 | 0.0013319 | 0.00033381 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3217-4_0_6_load_90 | 43 | 0.0010614 | 0.00026601 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3217-4_0_6_load_41 | 45 | 0.00082459 | 0.00020666 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3217-4_0_6_load_37 | 47 | 0.0035019 | 0.00087765 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3217-4_0_6_load_85 | 48 | 0.0021974 | 0.00055072 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3217-4_0_6_load_32 | 49 | 0.0052888 | 0.0013255 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3217-4_0_6_load_33 | 50 | 0.00083904 | 0.00021028 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3217-4_0_6_load_127 | 53 | 0.0033979 | 0.00085159 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3217-4_0_6_load_35 | 54 | 0.0051313 | 0.001286 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3217-4_0_6_load_36 | 55 | 0.0023442 | 0.00058752 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3217-4_0_6_load_54 | 59 | 0.0058093 | 0.0014559 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3217-4_0_6_load_38 | 60 | 0.0007323 | 0.00018353 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3217-4_0_6_load_40 | 61 | 0.0024036 | 0.00060241 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3217-4_0_6_load_43 | 62 | 0.0010421 | 0.00026119 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3217-4_0_6_load_44 | 63 | 0.0015089 | 0.00037816 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3217-4_0_6_load_83 | 65 | 0.0015029 | 0.00037665 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3217-4_0_6_load_70 | 67 | 0.0070358 | 0.0017633 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3217-4_0_6_load_152 | 68 | 0.0038786 | 0.00097206 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3217-4_0_6_load_71 | 69 | 0.0057662 | 0.0014451 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3217-4_0_6_load_48 | 71 | 0.0091233 | 0.0022865 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3217-4_0_6_load_47 | 72 | 0.0048931 | 0.0012263 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3217-4_0_6_load_55 | 74 | 0.0029506 | 0.00073949 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3217-4_0_6_load_76 | 75 | 0.0067431 | 0.00169 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3217-4_0_6_load_63 | 76 | 0.005965 | 0.001495 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3217-4_0_6_load_50 | 78 | 0.0021979 | 0.00055083 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3217-4_0_6_load_51 | 79 | 0.0032495 | 0.00081439 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3217-4_0_6_load_53 | 81 | 0.0019794 | 0.00049609 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3217-4_0_6_load_135 | 83 | 0.0021647 | 0.00054252 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3217-4_0_6_load_132 | 84 | 0.0021649 | 0.00054258 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3217-4_0_6_load_137 | 85 | 0.0014573 | 0.00036522 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3217-4_0_6_load_131 | 86 | 0.0016728 | 0.00041925 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3217-4_0_6_load_60 | 87 | 0.0015844 | 0.0003971 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3217-4_0_6_load_59 | 88 | 0.0015998 | 0.00040095 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3217-4_0_6_load_61 | 89 | 0.0015759 | 0.00039496 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3217-4_0_6_load_64 | 90 | 0.0047471 | 0.0011897 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3217-4_0_6_load_66 | 91 | 0.0076163 | 0.0019088 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3217-4_0_6_load_69 | 93 | 0.0052292 | 0.0013106 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3217-4_0_6_load_74 | 95 | 0.0052847 | 0.0013245 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3217-4_0_6_load_73 | 96 | 0.0036848 | 0.0009235 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3217-4_0_6_load_77 | 97 | 0.0029617 | 0.00074228 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3217-4_0_6_load_153 | 98 | 0.0033765 | 0.00084624 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3217-4_0_6_load_154 | 99 | 0.0026836 | 0.00067258 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3217-4_0_6_load_75 | 100 | 0.0017273 | 0.0004329 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3217-4_0_6_load_183 | 101 | 0.0021445 | 0.00053746 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3217-4_0_6_load_184 | 102 | 0.004486 | 0.0011243 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3217-4_0_6_load_78 | 103 | 0.007923 | 0.0019857 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3217-4_0_6_load_79 | 104 | 0.0017807 | 0.00044628 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3217-4_0_6_load_80 | 105 | 0.0017794 | 0.00044595 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3217-4_0_6_load_81 | 106 | 0.0073601 | 0.0018446 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3217-4_0_6_load_86 | 108 | 0.0020613 | 0.00051662 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3217-4_0_6_load_87 | 109 | 0.0015968 | 0.00040019 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3217-4_0_6_load_88 | 110 | 0.012003 | 0.0030083 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3217-4_0_6_load_91 | 111 | 0.0011202 | 0.00028075 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3217-4_0_6_load_93 | 112 | 0.0015985 | 0.00040062 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3217-4_0_6_load_94 | 113 | 0.0026222 | 0.00065718 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3217-4_0_6_load_95 | 114 | 0.0015949 | 0.00039971 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3217-4_0_6_load_96 | 115 | 0.0031811 | 0.00079726 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3217-4_0_6_load_97 | 116 | 0.0014269 | 0.00035762 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3217-4_0_6_load_100 | 119 | 0.0016677 | 0.00041795 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3217-4_0_6_load_101 | 120 | 0.0027779 | 0.0006962 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3217-4_0_6_load_103 | 122 | 0.0035625 | 0.00089284 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3217-4_0_6_load_104 | 123 | 0.0014873 | 0.00037274 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3217-4_0_6_load_108 | 124 | 0.0011019 | 0.00027616 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3217-4_0_6_load_109 | 125 | 0.0041056 | 0.001029 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3217-4_0_6_load_110 | 126 | 0.0022482 | 0.00056346 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3217-4_0_6_load_107 | 127 | 0.0021984 | 0.00055097 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3217-4_0_6_load_105 | 128 | 0.0015368 | 0.00038516 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3217-4_0_6_load_111 | 129 | 0.002174 | 0.00054486 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3217-4_0_6_load_125 | 130 | 0.0026999 | 0.00067665 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3217-4_0_6_load_106 | 131 | 0.002483 | 0.00062231 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3217-4_0_6_load_126 | 133 | 0.001962 | 0.00049173 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3217-4_0_6_load_113 | 134 | 0.0033179 | 0.00083154 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3217-4_0_6_load_114 | 135 | 0.0024144 | 0.00060511 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3217-4_0_6_load_115 | 136 | 0.0041199 | 0.0010325 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3217-4_0_6_load_117 | 138 | 0.0041179 | 0.001032 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3217-4_0_6_load_121 | 139 | 0.0019738 | 0.00049467 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3217-4_0_6_load_118 | 140 | 0.0062296 | 0.0015613 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3217-4_0_6_load_123 | 141 | 0.0017837 | 0.00044705 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3217-4_0_6_load_119 | 142 | 0.0062295 | 0.0015613 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3217-4_0_6_load_124 | 143 | 0.001734 | 0.00043457 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3217-4_0_6_load_188 | 146 | 0.0027187 | 0.00068138 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3217-4_0_6_load_169 | 147 | 0.0032141 | 0.00080553 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3217-4_0_6_load_133 | 148 | 0.0051415 | 0.0012886 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3217-4_0_6_load_134 | 149 | 0.0015675 | 0.00039286 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_3217-4_0_6_load_151 | 150 | 0.0014486 | 0.00036304 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_3217-4_0_6_load_150 | 151 | 0.0014399 | 0.00036086 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_3217-4_0_6_load_141 | 153 | 0.0048782 | 0.0012226 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_3217-4_0_6_load_143 | 154 | 0.0020057 | 0.00050268 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_3217-4_0_6_load_144 | 155 | 0.0019827 | 0.00049691 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_3217-4_0_6_load_145 | 156 | 0.0010488 | 0.00026285 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_3217-4_0_6_load_146 | 157 | 0.0033315 | 0.00083496 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_3217-4_0_6_load_147 | 158 | 0.0010481 | 0.00026269 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_3217-4_0_6_load_148 | 159 | 0.012184 | 0.0030535 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_3217-4_0_6_load_149 | 160 | 0.0051959 | 0.0013022 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_3217-4_0_6_load_155 | 161 | 0.0030003 | 0.00075196 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_3217-4_0_6_load_156 | 162 | 0.0049141 | 0.0012316 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_3217-4_0_6_load_158 | 164 | 0.0023455 | 0.00058784 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_3217-4_0_6_load_159 | 165 | 0.0047504 | 0.0011906 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_3217-4_0_6_load_160 | 166 | 0.00506 | 0.0012681 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_3217-4_0_6_load_163 | 167 | 0.0058524 | 0.0014668 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_3217-4_0_6_load_161 | 169 | 0.0042118 | 0.0010556 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_3217-4_0_6_load_162 | 170 | 0.0044111 | 0.0011055 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_3217-4_0_6_load_164 | 171 | 0.0014443 | 0.00036197 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_3217-4_0_6_load_165 | 172 | 0.0017714 | 0.00044396 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_3217-4_0_6_load_170 | 173 | 0.0015378 | 0.0003854 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_3217-4_0_6_load_172 | 175 | 0.0019575 | 0.0004906 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_3217-4_0_6_load_174 | 176 | 0.0033099 | 0.00082955 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_3217-4_0_6_load_190 | 177 | 0.0031013 | 0.00077725 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_3217-4_0_6_load_187 | 178 | 0.003469 | 0.00086941 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_3217-4_0_6_load_176 | 180 | 0.0041264 | 0.0010342 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_3217-4_0_6_load_177 | 181 | 0.0027246 | 0.00068286 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_3217-4_0_6_load_180 | 182 | 0.0019872 | 0.00049804 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_3217-4_0_6_load_178 | 183 | 0.0017667 | 0.00044278 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_3217-4_0_6_load_181 | 184 | 0.0034156 | 0.00085604 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_3217-4_0_6_load_179 | 185 | 0.0016151 | 0.00040479 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_3217-4_0_6_load_186 | 187 | 0.0020419 | 0.00051174 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_3217-4_0_6_load_185 | 188 | 0.0042678 | 0.0010696 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_3217-4_0_6_load_192 | 189 | 0.0010185 | 0.00025526 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_3217-4_0_6_load_191 | 190 | 0.0022182 | 0.00055595 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 92 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3217-4_0_6_line_0 |  | 0 | 1 | 0.014909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3217-4_0_6_line_1 |  | 0 | 2 | 0.047434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3217-4_0_6_line_2 |  | 1 | 3 | 0.027945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3217-4_0_6_line_3 |  | 2 | 4 | 0.25195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3217-4_0_6_line_4 |  | 4 | 5 | 0.11657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3217-4_0_6_line_5 |  | 5 | 6 | 0.017613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3217-4_0_6_line_6 |  | 6 | 7 | 0.083047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_3217-4_0_6_line_7 |  | 6 | 8 | 0.019065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3217-4_0_6_line_8 |  | 7 | 111 | 0.046195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_3217-4_0_6_line_9 |  | 8 | 137 | 0.027324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3217-4_0_6_line_10 |  | 9 | 10 | 0.021301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3217-4_0_6_line_11 |  | 10 | 11 | 0.040988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3217-4_0_6_line_12 |  | 10 | 12 | 0.024997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3217-4_0_6_line_13 |  | 10 | 13 | 0.027284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3217-4_0_6_line_14 |  | 11 | 17 | 0.020976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3217-4_0_6_line_15 |  | 11 | 18 | 0.016403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3217-4_0_6_line_16 |  | 14 | 15 | 0.020083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3217-4_0_6_line_17 |  | 14 | 16 | 0.22764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3217-4_0_6_line_18 |  | 15 | 20 | 0.027897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3217-4_0_6_line_19 |  | 16 | 24 | 0.028675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3217-4_0_6_line_20 |  | 18 | 19 | 0.010033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3217-4_0_6_line_21 |  | 19 | 22 | 0.010403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3217-4_0_6_line_22 |  | 20 | 28 | 0.056302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3217-4_0_6_line_23 |  | 21 | 22 | 0.010806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3217-4_0_6_line_24 |  | 21 | 23 | 0.016052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3217-4_0_6_line_25 |  | 23 | 24 | 0.033651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3217-4_0_6_line_26 |  | 25 | 26 | 0.039459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3217-4_0_6_line_27 |  | 25 | 27 | 0.016026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3217-4_0_6_line_28 |  | 26 | 152 | 0.0043537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3217-4_0_6_line_29 |  | 27 | 149 | 0.01814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3217-4_0_6_line_30 |  | 28 | 32 | 0.029054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3217-4_0_6_line_31 |  | 29 | 30 | 0.073486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3217-4_0_6_line_32 |  | 29 | 31 | 0.013579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3217-4_0_6_line_33 |  | 30 | 32 | 0.08422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3217-4_0_6_line_34 |  | 31 | 153 | 0.0042554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3217-4_0_6_line_35 |  | 33 | 34 | 0.031562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3217-4_0_6_line_36 |  | 34 | 35 | 0.02101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3217-4_0_6_line_37 |  | 34 | 36 | 0.046516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3217-4_0_6_line_38 |  | 35 | 37 | 0.0028936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3217-4_0_6_line_39 |  | 36 | 38 | 0.0476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3217-4_0_6_line_40 |  | 36 | 39 | 0.094304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3217-4_0_6_line_41 |  | 37 | 40 | 0.033323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3217-4_0_6_line_42 |  | 39 | 41 | 0.020623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_3217-4_0_6_line_43 |  | 39 | 42 | 0.005607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_3217-4_0_6_line_44 |  | 41 | 43 | 0.14245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_3217-4_0_6_line_45 |  | 42 | 48 | 0.025194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_3217-4_0_6_line_46 |  | 43 | 111 | 0.02519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_3217-4_0_6_line_47 |  | 44 | 45 | 0.026784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3217-4_0_6_line_48 |  | 44 | 46 | 0.00468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3217-4_0_6_line_49 |  | 44 | 47 | 0.029011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3217-4_0_6_line_50 |  | 45 | 62 | 0.040291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3217-4_0_6_line_51 |  | 46 | 63 | 0.016763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3217-4_0_6_line_52 |  | 46 | 64 | 0.064228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3217-4_0_6_line_53 |  | 47 | 60 | 0.0089133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3217-4_0_6_line_54 |  | 48 | 109 | 0.0092835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_3217-4_0_6_line_55 |  | 49 | 50 | 0.023805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3217-4_0_6_line_56 |  | 50 | 51 | 0.10054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3217-4_0_6_line_57 |  | 51 | 52 | 0.13714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3217-4_0_6_line_58 |  | 52 | 53 | 0.07785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3217-4_0_6_line_59 |  | 53 | 57 | 0.03653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3217-4_0_6_line_60 |  | 54 | 55 | 0.038873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3217-4_0_6_line_61 |  | 55 | 56 | 0.012654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3217-4_0_6_line_62 |  | 56 | 57 | 0.011453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3217-4_0_6_line_63 |  | 56 | 58 | 0.059744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3217-4_0_6_line_64 |  | 56 | 59 | 0.036991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3217-4_0_6_line_65 |  | 58 | 87 | 0.01025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3217-4_0_6_line_66 |  | 59 | 79 | 0.01895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3217-4_0_6_line_67 |  | 60 | 61 | 0.036555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3217-4_0_6_line_68 |  | 63 | 65 | 0.0088351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3217-4_0_6_line_69 |  | 64 | 69 | 0.016665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_3217-4_0_6_line_70 |  | 64 | 70 | 0.00605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_3217-4_0_6_line_71 |  | 66 | 67 | 0.036188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3217-4_0_6_line_72 |  | 66 | 68 | 0.01373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3217-4_0_6_line_73 |  | 67 | 73 | 0.023539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3217-4_0_6_line_74 |  | 68 | 74 | 0.029676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3217-4_0_6_line_75 |  | 69 | 75 | 0.0034083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_3217-4_0_6_line_76 |  | 70 | 76 | 0.018074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_3217-4_0_6_line_77 |  | 71 | 72 | 0.0057405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3217-4_0_6_line_78 |  | 72 | 77 | 0.017246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3217-4_0_6_line_79 |  | 73 | 93 | 0.0029065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_3217-4_0_6_line_80 |  | 74 | 80 | 0.0044211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3217-4_0_6_line_81 |  | 75 | 97 | 0.011919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_3217-4_0_6_line_82 |  | 76 | 90 | 0.019282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_3217-4_0_6_line_83 |  | 77 | 78 | 0.027279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3217-4_0_6_line_84 |  | 77 | 79 | 0.019275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3217-4_0_6_line_85 |  | 77 | 80 | 0.007474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3217-4_0_6_line_86 |  | 78 | 81 | 0.03729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3217-4_0_6_line_87 |  | 80 | 82 | 0.048625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3217-4_0_6_line_88 |  | 82 | 83 | 0.011142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3217-4_0_6_line_89 |  | 82 | 84 | 0.020542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3217-4_0_6_line_90 |  | 83 | 85 | 0.012247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3217-4_0_6_line_91 |  | 84 | 86 | 0.0065386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3217-4_0_6_line_92 |  | 85 | 150 | 0.0061517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3217-4_0_6_line_93 |  | 86 | 148 | 0.02549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3217-4_0_6_line_94 |  | 87 | 88 | 0.014111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3217-4_0_6_line_95 |  | 88 | 89 | 0.0039409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3217-4_0_6_line_96 |  | 90 | 91 | 0.0043504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_3217-4_0_6_line_97 |  | 91 | 92 | 0.017853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_3217-4_0_6_line_98 |  | 92 | 94 | 0.010222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_3217-4_0_6_line_99 |  | 93 | 95 | 0.0070878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_3217-4_0_6_line_100 |  | 94 | 96 | 0.015124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3217-4_0_6_line_101 |  | 94 | 95 | 0.038125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_3217-4_0_6_line_102 |  | 96 | 98 | 0.019169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3217-4_0_6_line_103 |  | 97 | 103 | 0.013355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_3217-4_0_6_line_104 |  | 98 | 99 | 0.0045277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3217-4_0_6_line_105 |  | 99 | 161 | 0.0059569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3217-4_0_6_line_106 |  | 100 | 101 | 0.12716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3217-4_0_6_line_107 |  | 101 | 102 | 0.0038284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3217-4_0_6_line_108 |  | 102 | 188 | 0.025741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3217-4_0_6_line_109 |  | 103 | 104 | 0.02486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_3217-4_0_6_line_110 |  | 104 | 105 | 0.0097633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_3217-4_0_6_line_111 |  | 105 | 106 | 0.025374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_3217-4_0_6_line_112 |  | 106 | 107 | 0.016299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
113 | LV_3217-4_0_6_line_113 |  | 107 | 108 | 0.018175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3217-4_0_6_line_114 |  | 107 | 109 | 0.015181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_3217-4_0_6_line_115 |  | 108 | 110 | 0.01889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3217-4_0_6_line_116 |  | 112 | 113 | 0.0097116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3217-4_0_6_line_117 |  | 112 | 114 | 0.0098949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_3217-4_0_6_line_118 |  | 113 | 115 | 0.00043564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_3217-4_0_6_line_119 |  | 114 | 116 | 0.0042761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_3217-4_0_6_line_120 |  | 116 | 117 | 0.028259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_3217-4_0_6_line_121 |  | 117 | 118 | 0.029234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_3217-4_0_6_line_122 |  | 117 | 119 | 0.012067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_3217-4_0_6_line_123 |  | 118 | 120 | 0.018535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_3217-4_0_6_line_124 |  | 118 | 121 | 0.032098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_3217-4_0_6_line_125 |  | 118 | 122 | 0.030853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_3217-4_0_6_line_126 |  | 119 | 123 | 0.019931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_3217-4_0_6_line_127 |  | 120 | 124 | 0.02786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_3217-4_0_6_line_128 |  | 121 | 125 | 0.019156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_3217-4_0_6_line_129 |  | 121 | 126 | 0.0067356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_3217-4_0_6_line_130 |  | 122 | 127 | 0.0055744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_3217-4_0_6_line_131 |  | 123 | 128 | 0.0094002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_3217-4_0_6_line_132 |  | 124 | 129 | 0.0018163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_3217-4_0_6_line_133 |  | 126 | 130 | 0.012615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_3217-4_0_6_line_134 |  | 128 | 131 | 0.0065892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_3217-4_0_6_line_135 |  | 129 | 132 | 0.018344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_3217-4_0_6_line_136 |  | 130 | 133 | 0.0057841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_3217-4_0_6_line_137 |  | 132 | 134 | 0.031866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_3217-4_0_6_line_138 |  | 132 | 135 | 0.020097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_3217-4_0_6_line_139 |  | 134 | 136 | 0.010272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_3217-4_0_6_line_140 |  | 135 | 137 | 0.0048305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_3217-4_0_6_line_141 |  | 136 | 138 | 0.0099192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_3217-4_0_6_line_142 |  | 137 | 139 | 0.019229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_3217-4_0_6_line_143 |  | 138 | 140 | 0.015926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_3217-4_0_6_line_144 |  | 139 | 141 | 0.0026023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_3217-4_0_6_line_145 |  | 140 | 142 | 0.0047895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_3217-4_0_6_line_146 |  | 141 | 143 | 0.023884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_3217-4_0_6_line_147 |  | 144 | 145 | 0.074494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_3217-4_0_6_line_148 |  | 144 | 146 | 0.020954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_3217-4_0_6_line_149 |  | 144 | 147 | 0.028304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_3217-4_0_6_line_150 |  | 145 | 177 | 0.002665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_3217-4_0_6_line_151 |  | 146 | 178 | 0.0012976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_3217-4_0_6_line_152 |  | 148 | 149 | 0.035912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_3217-4_0_6_line_153 |  | 150 | 151 | 0.0048261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_3217-4_0_6_line_154 |  | 151 | 160 | 0.00077264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_3217-4_0_6_line_155 |  | 152 | 153 | 0.018682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_3217-4_0_6_line_156 |  | 154 | 155 | 0.0004778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_3217-4_0_6_line_157 |  | 154 | 156 | 0.015595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_3217-4_0_6_line_158 |  | 155 | 157 | 0.016393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_3217-4_0_6_line_159 |  | 156 | 158 | 0.00657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_3217-4_0_6_line_160 |  | 157 | 159 | 0.0051437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_3217-4_0_6_line_161 |  | 158 | 160 | 0.021383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_3217-4_0_6_line_162 |  | 161 | 162 | 0.028967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_3217-4_0_6_line_163 |  | 162 | 163 | 0.010811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_3217-4_0_6_line_164 |  | 163 | 164 | 0.010919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_3217-4_0_6_line_165 |  | 163 | 165 | 0.021173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_3217-4_0_6_line_166 |  | 165 | 166 | 0.019214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_3217-4_0_6_line_167 |  | 166 | 169 | 0.0072179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_3217-4_0_6_line_168 |  | 167 | 168 | 0.012231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_3217-4_0_6_line_169 |  | 168 | 173 | 0.012448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_3217-4_0_6_line_170 |  | 168 | 174 | 0.003638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_3217-4_0_6_line_171 |  | 169 | 170 | 0.01683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_3217-4_0_6_line_172 |  | 170 | 171 | 0.016182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_3217-4_0_6_line_173 |  | 171 | 172 | 0.018503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_3217-4_0_6_line_174 |  | 172 | 174 | 0.014481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_3217-4_0_6_line_175 |  | 173 | 175 | 0.0074001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_3217-4_0_6_line_176 |  | 175 | 176 | 0.030193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_3217-4_0_6_line_177 |  | 176 | 179 | 0.013811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_3217-4_0_6_line_178 |  | 177 | 190 | 0.015367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_3217-4_0_6_line_179 |  | 178 | 187 | 0.030748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_3217-4_0_6_line_180 |  | 179 | 180 | 0.015763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_3217-4_0_6_line_181 |  | 179 | 181 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_3217-4_0_6_line_182 |  | 180 | 182 | 0.021608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_3217-4_0_6_line_183 |  | 181 | 183 | 0.0081882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_3217-4_0_6_line_184 |  | 182 | 184 | 0.00062873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_3217-4_0_6_line_185 |  | 183 | 185 | 0.010173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_3217-4_0_6_line_186 |  | 184 | 186 | 0.014978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_3217-4_0_6_line_187 |  | 186 | 187 | 0.012251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_3217-4_0_6_line_188 |  | 186 | 188 | 0.018274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_3217-4_0_6_line_189 |  | 189 | 190 | 0.024779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3217-4_0_6_trafo_68 | 0.63 MVA 20/0.4 kV | 191 | 92 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2749618.1712 | 1262142.1313 | 2749628.3467 | 1262153.0279
1 | 2749661.9863 | 1262185.761 | 2749650.5143 | 1262178.5747 | 2749639.5128 | 1262167.3963 | 2749630.479 | 1262155.3113 | 2749628.3467 | 1262153.0279
2 | 2749618.1712 | 1262142.1313 | 2749603.4093 | 1262155.3155 | 2749597.2794 | 1262160.691
3 | 2749898.6736 | 1262099.3899 | 2749661.9863 | 1262185.761
4 | 2749898.6736 | 1262099.3899 | 2749912.3357 | 1262123.349 | 2749936.3796 | 1262163.8766 | 2749954.4818 | 1262199.4044 | 2749955.3826 | 1262201.1852
5 | 2749963.3323 | 1262216.9018 | 2749955.3826 | 1262201.1852
6 | 2750000.7859 | 1262275.5323 | 2749985.9642 | 1262280.3613 | 2749976.1995 | 1262251.9631 | 2749971.7368 | 1262236.5234 | 2749965.3063 | 1262220.8002 | 2749963.3323 | 1262216.9018
7 | 2749963.3323 | 1262216.9018 | 2749973.2893 | 1262205.0535 | 2749976.6957 | 1262203.925
8 | 2750000.7859 | 1262275.5323 | 2750044.4131 | 1262260.3455
9 | 2750002.6332 | 1262195.3322 | 2749976.6957 | 1262203.925
10 | 2750559.703 | 1261343.6986 | 2750541.9994 | 1261331.8528
11 | 2750559.703 | 1261343.6986 | 2750554.9024 | 1261347.4691 | 2750536.5352 | 1261367.9555 | 2750531.0768 | 1261372.9884
12 | 2750559.703 | 1261343.6986 | 2750573.4767 | 1261334.8403 | 2750581.3295 | 1261331.2827
13 | 2750559.703 | 1261343.6986 | 2750552.0074 | 1261333.259 | 2750552.2735 | 1261318.9467
14 | 2750543.7843 | 1261389.7062 | 2750531.0768 | 1261372.9884
15 | 2750518.4303 | 1261383.4771 | 2750531.0768 | 1261372.9884
16 | 2750484.6457 | 1261716.0078 | 2750486.4327 | 1261715.4285 | 2750489.8436 | 1261716.483 | 2750493.2369 | 1261718.2266 | 2750496.6528 | 1261719.081 | 2750500.2917 | 1261719.1737 | 2750503.8079 | 1261718.166
17 | 2750503.8079 | 1261718.166 | 2750526.167 | 1261491.6246
18 | 2750484.6457 | 1261716.0078 | 2750481.9478 | 1261716.8825 | 2750471.5019 | 1261722.0998 | 2750459.5212 | 1261728.0664
19 | 2750526.167 | 1261491.6246 | 2750525.0141 | 1261487.5932 | 2750521.4431 | 1261472.9877 | 2750519.7649 | 1261463.6913 | 2750519.7649 | 1261463.6913
20 | 2750518.4303 | 1261383.4771 | 2750521.4109 | 1261393.0575
21 | 2750521.4109 | 1261393.0575 | 2750521.8101 | 1261394.3406 | 2750521.8235 | 1261403.3994
22 | 2750405.6424 | 1261741.9782 | 2750413.1669 | 1261741.9473 | 2750420.8634 | 1261741.3757 | 2750429.4053 | 1261739.58 | 2750438.5705 | 1261736.9883 | 2750450.0002 | 1261732.8081 | 2750459.5212 | 1261728.0664
23 | 2750521.8395 | 1261414.2057 | 2750521.8235 | 1261403.3994
24 | 2750521.8395 | 1261414.2057 | 2750521.3238 | 1261420.243 | 2750520.058 | 1261430.1553
25 | 2750519.7649 | 1261463.6913 | 2750518.5765 | 1261445.8209 | 2750519.2144 | 1261436.7614 | 2750520.058 | 1261430.1553
26 | 2750461.5051 | 1261927.9087 | 2750459.2398 | 1261925.9809 | 2750453.2984 | 1261920.9915 | 2750443.9684 | 1261919.1079 | 2750434.2139 | 1261920.8727 | 2750428.4639 | 1261924.3522 | 2750426.9378 | 1261926.425
27 | 2750472.2117 | 1261939.5336 | 2750469.4519 | 1261934.6716 | 2750461.5051 | 1261927.9087
28 | 2750424.3566 | 1261929.9311 | 2750426.9378 | 1261926.425
29 | 2750479.3013 | 1261956.0325 | 2750477.6576 | 1261949.028 | 2750472.9367 | 1261940.8108 | 2750472.2117 | 1261939.5336
30 | 2750388.0902 | 1261765.1663 | 2750405.6424 | 1261741.9782
31 | 2750394.9885 | 1261908.2293 | 2750424.6937 | 1261841.0148
32 | 2750394.9885 | 1261908.2293 | 2750405.9096 | 1261916.2995
33 | 2750388.0902 | 1261765.1663 | 2750407.8298 | 1261806.5095 | 2750424.6937 | 1261841.0148
34 | 2750409.3319 | 1261918.8285 | 2750405.9096 | 1261916.2995
35 | 2750230.8464 | 1262332.1941 | 2750231.5522 | 1262340.309 | 2750234.6615 | 1262363.5177
36 | 2750230.8464 | 1262332.1941 | 2750246.0438 | 1262326.53 | 2750250.5767 | 1262324.9784
37 | 2750230.3153 | 1262285.7785 | 2750229.166 | 1262312.8987 | 2750230.8464 | 1262332.1941
38 | 2750250.5767 | 1262324.9784 | 2750253.3144 | 1262324.0412
39 | 2750230.3153 | 1262285.7785 | 2750200.6753 | 1262294.6903 | 2750186.7708 | 1262304.0578
40 | 2750219.9551 | 1262193.0782 | 2750222.4597 | 1262197.7464 | 2750227.0596 | 1262210.4315 | 2750231.1367 | 1262266.5135 | 2750230.3153 | 1262285.7785
41 | 2750278.5984 | 1262334.6095 | 2750276.357 | 1262327.3008 | 2750271.1375 | 1262322.6858 | 2750263.5866 | 1262320.5251 | 2750253.3144 | 1262324.0412
42 | 2750219.9551 | 1262193.0782 | 2750201.6181 | 1262202.5163
43 | 2750219.9551 | 1262193.0782 | 2750224.5671 | 1262189.8699
44 | 2750201.6181 | 1262202.5163 | 2750191.1672 | 1262207.8953 | 2750170.7366 | 1262216.5853 | 2750155.8545 | 1262221.7016 | 2750119.5731 | 1262234.1821 | 2750068.2031 | 1262252.0641
45 | 2750224.5671 | 1262189.8699 | 2750216.1551 | 1262166.1214
46 | 2750044.4131 | 1262260.3455 | 2750068.2031 | 1262252.0641
47 | 2750315.8166 | 1262125.8571 | 2750336.6422 | 1262109.0147
48 | 2750313.1633 | 1262121.9969 | 2750315.8166 | 1262125.8571
49 | 2750315.8166 | 1262125.8571 | 2750332.2485 | 1262149.7663
50 | 2750336.6422 | 1262109.0147 | 2750358.1095 | 1262091.6533 | 2750369.5978 | 1262086.2819
51 | 2750313.1633 | 1262121.9969 | 2750300.6793 | 1262133.1842
52 | 2750313.1633 | 1262121.9969 | 2750346.4813 | 1262093.593 | 2750336.6444 | 1262087.3478 | 2750328.5851 | 1262083.8284
53 | 2750332.2485 | 1262149.7663 | 2750337.297 | 1262157.1121
54 | 2750221.6077 | 1262158.6079 | 2750216.1551 | 1262166.1214
55 | 2750824.8059 | 1262161.4668 | 2750816.479 | 1262139.1661
56 | 2750781.3101 | 1262044.9784 | 2750816.479 | 1262139.1661
57 | 2750644.1817 | 1262043.1161 | 2750781.3101 | 1262044.9784
58 | 2750644.1817 | 1262043.1161 | 2750609.5546 | 1262044.7249 | 2750570.5087 | 1262046.3882 | 2750566.4063 | 1262046.2556
59 | 2750529.8953 | 1262045.0755 | 2750566.4063 | 1262046.2556
60 | 2750539.5813 | 1262053.6826 | 2750562.4076 | 1262053.9785 | 2750578.4401 | 1262053.3392
61 | 2750526.9287 | 1262053.5196 | 2750531.2995 | 1262053.5753 | 2750539.5813 | 1262053.6826
62 | 2750529.8953 | 1262045.0755 | 2750526.9957 | 1262044.9683 | 2750526.9287 | 1262053.5196
63 | 2750529.988 | 1262112.1673 | 2750525.2464 | 1262099.1447 | 2750524.0164 | 1262071.3745 | 2750526.9287 | 1262053.5196
64 | 2750526.9287 | 1262053.5196 | 2750524.8891 | 1262053.3898 | 2750503.3328 | 1262052.0733 | 2750491.7643 | 1262051.3672 | 2750490.0136 | 1262051.5555
65 | 2750529.988 | 1262112.1673 | 2750540.1 | 1262110.4914
66 | 2750490.0136 | 1262051.5555 | 2750473.5394 | 1262053.3277 | 2750471.1984 | 1262053.7584
67 | 2750348.8283 | 1262191.801 | 2750337.297 | 1262157.1121 | 2750337.297 | 1262157.1121
68 | 2750294.0996 | 1262139.0805 | 2750300.6793 | 1262133.1842
69 | 2750328.5851 | 1262083.8284 | 2750325.7668 | 1262082.6 | 2750318.1004 | 1262082.0046 | 2750312.2767 | 1262082.9573
70 | 2750327.9088 | 1262077.8163 | 2750328.5851 | 1262083.8284
71 | 2750403.9448 | 1262067.2718 | 2750402.138 | 1262063.6222 | 2750395.892 | 1262057.5685 | 2750393.1847 | 1262054.9415 | 2750375.295 | 1262046.8256
72 | 2750403.9448 | 1262067.2718 | 2750416.8447 | 1262062.5713
73 | 2750353.2374 | 1262038.7097 | 2750367.5488 | 1262043.3114 | 2750375.295 | 1262046.8256
74 | 2750444.6401 | 1262052.1768 | 2750423.4312 | 1262060.1713 | 2750416.8447 | 1262062.5713
75 | 2750308.913 | 1262083.5075 | 2750312.2767 | 1262082.9573
76 | 2750327.9088 | 1262077.8163 | 2750327.3691 | 1262070.5842 | 2750320.4382 | 1262062.2731
77 | 2750435.7727 | 1262062.3557 | 2750430.3251 | 1262064.1658
78 | 2750452.2418 | 1262057.2455 | 2750442.6794 | 1262060.0607 | 2750435.7727 | 1262062.3557
79 | 2750353.2374 | 1262038.7097 | 2750350.4706 | 1262037.8196
80 | 2750448.7771 | 1262050.6174 | 2750444.6401 | 1262052.1768
81 | 2750308.913 | 1262083.5075 | 2750307.2151 | 1262083.7853 | 2750298.6301 | 1262087.5932 | 2750297.9968 | 1262088.0925
82 | 2750320.4382 | 1262062.2731 | 2750319.1248 | 1262060.6982 | 2750310.3993 | 1262054.0253 | 2750305.7371 | 1262049.8682
83 | 2750452.2418 | 1262057.2455 | 2750457.1598 | 1262064.2331 | 2750468.9469 | 1262078.795
84 | 2750452.2418 | 1262057.2455 | 2750471.1984 | 1262053.7584
85 | 2750448.7771 | 1262050.6174 | 2750452.2418 | 1262057.2455
86 | 2750468.9469 | 1262078.795 | 2750492.4082 | 1262107.7792
87 | 2750448.7771 | 1262050.6174 | 2750469.6305 | 1262046.6772 | 2750478.9037 | 1262045.156 | 2750466.4884 | 1262032.116
88 | 2750466.4884 | 1262032.116 | 2750465.0761 | 1262030.1448 | 2750460.1187 | 1262022.9741
89 | 2750466.4884 | 1262032.116 | 2750476.9007 | 1262026.4196 | 2750482.7021 | 1262020.9172 | 2750483.1432 | 1262020.4029
90 | 2750460.1187 | 1262022.9741 | 2750458.8379 | 1262021.1215 | 2750456.6275 | 1262012.6012 | 2750456.2413 | 1262011.4735
91 | 2750487.4003 | 1262015.44 | 2750483.1432 | 1262020.4029
92 | 2750454.2486 | 1262005.6534 | 2750456.2413 | 1262011.4735
93 | 2750487.4003 | 1262015.44 | 2750488.1171 | 1262014.6042 | 2750488.6776 | 1262008.5791 | 2750485.1391 | 1262001.5932 | 2750481.7696 | 1261993.8887 | 2750481.5152 | 1261991.8069
94 | 2750554.0211 | 1262108.1842 | 2750540.1 | 1262110.4914
95 | 2750554.0211 | 1262108.1842 | 2750557.9091 | 1262107.5399
96 | 2750305.7371 | 1262049.8682 | 2750302.4901 | 1262046.9729
97 | 2750296.5483 | 1262030.1384 | 2750299.8598 | 1262039.2427 | 2750302.4901 | 1262046.9729 | 2750302.4901 | 1262046.9729
98 | 2750306.6945 | 1262028.6725 | 2750296.5483 | 1262030.1384
99 | 2750350.4706 | 1262037.8196 | 2750343.7233 | 1262035.6488
100 | 2750306.6945 | 1262028.6725 | 2750307.1719 | 1262024.7251 | 2750307.4084 | 1262013.58
101 | 2750306.6945 | 1262028.6725 | 2750322.0053 | 1262028.6615 | 2750343.7233 | 1262035.6488
102 | 2750308.28 | 1261994.434 | 2750307.5522 | 1262006.8057 | 2750307.4084 | 1262013.58
103 | 2750297.9968 | 1262088.0925 | 2750288.7221 | 1262095.4049 | 2750287.6371 | 1262096.5038
104 | 2750308.28 | 1261994.434 | 2750308.5459 | 1261989.9141
105 | 2750308.8958 | 1261983.9675 | 2750308.5459 | 1261989.9141
106 | 2750186.4915 | 1261865.6003 | 2750070.9994 | 1261918.8012
107 | 2750186.4915 | 1261865.6003 | 2750189.9769 | 1261864.0166
108 | 2750189.9769 | 1261864.0166 | 2750213.4121 | 1261853.3685
109 | 2750287.6371 | 1262096.5038 | 2750276.6824 | 1262107.6001 | 2750270.1625 | 1262114.1862
110 | 2750263.2937 | 1262121.1246 | 2750270.1625 | 1262114.1862
111 | 2750263.2937 | 1262121.1246 | 2750258.0053 | 1262126.4668 | 2750247.176 | 1262139.0932 | 2750246.1138 | 1262139.6987
112 | 2750231.9543 | 1262147.7709 | 2750246.1138 | 1262139.6987
113 | 2750231.9543 | 1262147.7709 | 2750234.1183 | 1262143.5994 | 2750236.9263 | 1262130.4198
114 | 2750231.9543 | 1262147.7709 | 2750230.2108 | 1262151.1188 | 2750221.6077 | 1262158.6079
115 | 2750234.5001 | 1262112.567 | 2750237.9135 | 1262118.2593 | 2750237.7903 | 1262126.3643 | 2750236.9263 | 1262130.4198
116 | 2750159.9774 | 1262156.9586 | 2750169.1576 | 1262153.7904
117 | 2750159.9774 | 1262156.9586 | 2750156.5118 | 1262158.1547 | 2750150.7023 | 1262160.401
118 | 2750169.5694 | 1262153.6483 | 2750169.1576 | 1262153.7904
119 | 2750146.7139 | 1262161.9431 | 2750146.7139 | 1262161.9431 | 2750150.7023 | 1262160.401
120 | 2750118.7744 | 1262163.2464 | 2750127.725 | 1262161.0602 | 2750138.2137 | 1262162.1275 | 2750146.7139 | 1262161.9431
121 | 2750118.7744 | 1262163.2464 | 2750090.2922 | 1262170.1861
122 | 2750118.7744 | 1262163.2464 | 2750115.7127 | 1262151.574
123 | 2750090.2922 | 1262170.1861 | 2750072.163 | 1262174.0408
124 | 2750104.9289 | 1262198.775 | 2750090.2922 | 1262170.1861
125 | 2750090.2922 | 1262170.1861 | 2750081.17 | 1262144.1064 | 2750079.1908 | 1262141.5622
126 | 2750117.5127 | 1262133.3845 | 2750113.3343 | 1262138.5169 | 2750113.9842 | 1262144.9843 | 2750115.7127 | 1262151.574
127 | 2750072.163 | 1262174.0408 | 2750049.638 | 1262178.8301 | 2750044.9944 | 1262180.1658
128 | 2750104.9289 | 1262198.775 | 2750086.9663 | 1262205.5705
129 | 2750104.9289 | 1262198.775 | 2750111.5693 | 1262197.6472
130 | 2750075.7681 | 1262137.1624 | 2750079.1908 | 1262141.5622
131 | 2750117.5127 | 1262133.3845 | 2750117.5127 | 1262133.3845 | 2750126.3884 | 1262130.2883
132 | 2750043.2488 | 1262180.6679 | 2750044.9944 | 1262180.1658
133 | 2750111.5693 | 1262197.6472 | 2750124.0057 | 1262195.5349
134 | 2750132.6099 | 1262128.1179 | 2750126.3884 | 1262130.2883
135 | 2750025.6194 | 1262185.7389 | 2750043.2488 | 1262180.6679
136 | 2750129.7081 | 1262194.5663 | 2750124.0057 | 1262195.5349
137 | 2750025.6194 | 1262185.7389 | 2750007.9982 | 1262159.1877
138 | 2750025.6194 | 1262185.7389 | 2750022.992 | 1262186.4952 | 2750007.0643 | 1262193.4089
139 | 2749997.9772 | 1262161.4433 | 2750007.9982 | 1262159.1877
140 | 2750002.6332 | 1262195.3322 | 2750007.0643 | 1262193.4089
141 | 2749988.3001 | 1262163.6215 | 2749997.9772 | 1262161.4433
142 | 2750002.6332 | 1262195.3322 | 2750008.3629 | 1262211.6383 | 2750009.0319 | 1262213.4653
143 | 2749973.1196 | 1262168.3943 | 2749985.3068 | 1262164.2952 | 2749988.3001 | 1262163.6215
144 | 2750009.0319 | 1262213.4653 | 2750009.9266 | 1262215.9089
145 | 2749968.58 | 1262169.9212 | 2749973.1196 | 1262168.3943
146 | 2750013.7316 | 1262239.1909 | 2750013.2834 | 1262225.0765 | 2750009.9266 | 1262215.9089
147 | 2750239.6565 | 1261765.9178 | 2750260.1921 | 1261783.7016 | 2750261.3595 | 1261789.081 | 2750266.6475 | 1261790.7281 | 2750282.8361 | 1261808.6906 | 2750286.577 | 1261813.9576 | 2750289.4539 | 1261818.8133
148 | 2750289.4539 | 1261818.8133 | 2750270.3769 | 1261827.4827
149 | 2750289.4539 | 1261818.8133 | 2750298.4248 | 1261833.9341 | 2750303.5489 | 1261843.3523
150 | 2750239.6565 | 1261765.9178 | 2750237.5187 | 1261764.3265
151 | 2750269.1956 | 1261828.0195 | 2750270.3769 | 1261827.4827
152 | 2750481.5152 | 1261991.8069 | 2750480.4345 | 1261982.966 | 2750480.2815 | 1261970.0269 | 2750479.8474 | 1261958.3597 | 2750479.3013 | 1261956.0325
153 | 2750452.7444 | 1262001.0709 | 2750452.8665 | 1262001.6168 | 2750454.2486 | 1262005.6534
154 | 2750452.5758 | 1262000.3169 | 2750452.7444 | 1262001.0709
155 | 2750424.3566 | 1261929.9311 | 2750409.3319 | 1261918.8285
156 | 2750430.0398 | 1261964.9788 | 2750430.5003 | 1261965.1063
157 | 2750441.8863 | 1261974.6538 | 2750441.0561 | 1261973.099 | 2750435.5625 | 1261966.5082 | 2750430.5003 | 1261965.1063
158 | 2750430.0398 | 1261964.9788 | 2750425.9209 | 1261963.8381 | 2750414.3771 | 1261960.1477
159 | 2750441.8863 | 1261974.6538 | 2750444.9809 | 1261980.4494
160 | 2750409.4776 | 1261958.5814 | 2750414.3771 | 1261960.1477
161 | 2750444.9809 | 1261980.4494 | 2750446.0713 | 1261982.4915 | 2750451.0527 | 1261993.507 | 2750452.5758 | 1262000.3169
162 | 2750308.8958 | 1261983.9675 | 2750308.9732 | 1261982.651 | 2750307.1288 | 1261960.0259 | 2750307.1505 | 1261955.0781
163 | 2750307.1979 | 1261944.2674 | 2750307.1505 | 1261955.0781
164 | 2750307.1979 | 1261944.2674 | 2750307.2139 | 1261940.6754 | 2750308.336 | 1261933.4349
165 | 2750307.1979 | 1261944.2674 | 2750328.3687 | 1261943.9722
166 | 2750328.3687 | 1261943.9722 | 2750347.5808 | 1261943.7042
167 | 2750347.5808 | 1261943.7042 | 2750347.5808 | 1261943.7042 | 2750348.3372 | 1261936.5261
168 | 2750314.8293 | 1261895.2679 | 2750312.5648 | 1261907.2878
169 | 2750314.8293 | 1261895.2679 | 2750308.0958 | 1261890.2918 | 2750304.0421 | 1261889.8693
170 | 2750314.8293 | 1261895.2679 | 2750315.5007 | 1261891.6925
171 | 2750348.3372 | 1261936.5261 | 2750349.3399 | 1261927.01 | 2750347.9568 | 1261919.8816
172 | 2750347.9568 | 1261919.8816 | 2750344.8746 | 1261903.9957
173 | 2750344.8746 | 1261903.9957 | 2750344.8746 | 1261903.9957 | 2750334.7483 | 1261895.1851 | 2750329.7493 | 1261894.278
174 | 2750315.5007 | 1261891.6925 | 2750329.7493 | 1261894.278
175 | 2750296.6818 | 1261889.1023 | 2750304.0421 | 1261889.8693
176 | 2750296.6818 | 1261889.1023 | 2750292.2841 | 1261888.644 | 2750274.1493 | 1261886.1586 | 2750266.7071 | 1261886.7707
177 | 2750254.576 | 1261892.5122 | 2750262.4778 | 1261887.1186 | 2750266.7071 | 1261886.7707
178 | 2750237.5187 | 1261764.3265 | 2750225.192 | 1261755.1508
179 | 2750241.2026 | 1261840.7407 | 2750269.1956 | 1261828.0195
180 | 2750254.576 | 1261892.5122 | 2750252.2598 | 1261890.5069 | 2750249.6572 | 1261884.9464 | 2750246.7189 | 1261879.0816
181 | 2750254.576 | 1261892.5122 | 2750255.3717 | 1261896.2028 | 2750257.5025 | 1261903.3683
182 | 2750246.7189 | 1261879.0816 | 2750237.0401 | 1261859.763
183 | 2750259.8364 | 1261911.2168 | 2750257.5025 | 1261903.3683
184 | 2750236.7585 | 1261859.2009 | 2750237.0401 | 1261859.763
185 | 2750260.801 | 1261921.3436 | 2750259.8441 | 1261911.2425 | 2750259.8364 | 1261911.2168
186 | 2750230.0492 | 1261845.8092 | 2750236.7585 | 1261859.2009
187 | 2750230.0492 | 1261845.8092 | 2750241.2026 | 1261840.7407
188 | 2750230.0492 | 1261845.8092 | 2750213.4121 | 1261853.3685
189 | 2750204.632 | 1261768.8907 | 2750209.3479 | 1261765.1473 | 2750217.9124 | 1261759.1922 | 2750225.192 | 1261755.1508 | 2750225.192 | 1261755.1508

## bus_geodata
| x | y | coords
0 | 2749628.3467 | 1262153.0279
1 | 2749618.1712 | 1262142.1313
2 | 2749661.9863 | 1262185.761
3 | 2749597.2794 | 1262160.691
4 | 2749898.6736 | 1262099.3899
5 | 2749955.3826 | 1262201.1852
6 | 2749963.3323 | 1262216.9018
7 | 2750000.7859 | 1262275.5323
8 | 2749976.6957 | 1262203.925
9 | 2750541.9994 | 1261331.8528
10 | 2750559.703 | 1261343.6986
11 | 2750531.0768 | 1261372.9884
12 | 2750581.3295 | 1261331.2827
13 | 2750552.2735 | 1261318.9467
14 | 2750503.8079 | 1261718.166
15 | 2750484.6457 | 1261716.0078
16 | 2750526.167 | 1261491.6246
17 | 2750543.7843 | 1261389.7062
18 | 2750518.4303 | 1261383.4771
19 | 2750521.4109 | 1261393.0575
20 | 2750459.5212 | 1261728.0664
21 | 2750521.8395 | 1261414.2057
22 | 2750521.8235 | 1261403.3994
23 | 2750520.058 | 1261430.1553
24 | 2750519.7649 | 1261463.6913
25 | 2750461.5051 | 1261927.9087
26 | 2750426.9378 | 1261926.425
27 | 2750472.2117 | 1261939.5336
28 | 2750405.6424 | 1261741.9782
29 | 2750394.9885 | 1261908.2293
30 | 2750424.6937 | 1261841.0148
31 | 2750405.9096 | 1261916.2995
32 | 2750388.0902 | 1261765.1663
33 | 2750234.6615 | 1262363.5177
34 | 2750230.8464 | 1262332.1941
35 | 2750250.5767 | 1262324.9784
36 | 2750230.3153 | 1262285.7785
37 | 2750253.3144 | 1262324.0412
38 | 2750186.7708 | 1262304.0578
39 | 2750219.9551 | 1262193.0782
40 | 2750278.5984 | 1262334.6095
41 | 2750201.6181 | 1262202.5163
42 | 2750224.5671 | 1262189.8699
43 | 2750068.2031 | 1262252.0641
44 | 2750315.8166 | 1262125.8571
45 | 2750336.6422 | 1262109.0147
46 | 2750313.1633 | 1262121.9969
47 | 2750332.2485 | 1262149.7663
48 | 2750216.1551 | 1262166.1214
49 | 2750824.8059 | 1262161.4668
50 | 2750816.479 | 1262139.1661
51 | 2750781.3101 | 1262044.9784
52 | 2750644.1817 | 1262043.1161
53 | 2750566.4063 | 1262046.2556
54 | 2750578.4401 | 1262053.3392
55 | 2750539.5813 | 1262053.6826
56 | 2750526.9287 | 1262053.5196
57 | 2750529.8953 | 1262045.0755
58 | 2750529.988 | 1262112.1673
59 | 2750490.0136 | 1262051.5555
60 | 2750337.297 | 1262157.1121
61 | 2750348.8283 | 1262191.801
62 | 2750369.5978 | 1262086.2819
63 | 2750300.6793 | 1262133.1842
64 | 2750328.5851 | 1262083.8284
65 | 2750294.0996 | 1262139.0805
66 | 2750403.9448 | 1262067.2718
67 | 2750375.295 | 1262046.8256
68 | 2750416.8447 | 1262062.5713
69 | 2750312.2767 | 1262082.9573
70 | 2750327.9088 | 1262077.8163
71 | 2750430.3251 | 1262064.1658
72 | 2750435.7727 | 1262062.3557
73 | 2750353.2374 | 1262038.7097
74 | 2750444.6401 | 1262052.1768
75 | 2750308.913 | 1262083.5075
76 | 2750320.4382 | 1262062.2731
77 | 2750452.2418 | 1262057.2455
78 | 2750468.9469 | 1262078.795
79 | 2750471.1984 | 1262053.7584
80 | 2750448.7771 | 1262050.6174
81 | 2750492.4082 | 1262107.7792
82 | 2750466.4884 | 1262032.116
83 | 2750460.1187 | 1262022.9741
84 | 2750483.1432 | 1262020.4029
85 | 2750456.2413 | 1262011.4735
86 | 2750487.4003 | 1262015.44
87 | 2750540.1 | 1262110.4914
88 | 2750554.0211 | 1262108.1842
89 | 2750557.9091 | 1262107.5399
90 | 2750305.7371 | 1262049.8682
91 | 2750302.4901 | 1262046.9729
92 | 2750296.5483 | 1262030.1384
93 | 2750350.4706 | 1262037.8196
94 | 2750306.6945 | 1262028.6725
95 | 2750343.7233 | 1262035.6488
96 | 2750307.4084 | 1262013.58
97 | 2750297.9968 | 1262088.0925
98 | 2750308.28 | 1261994.434
99 | 2750308.5459 | 1261989.9141
100 | 2750070.9994 | 1261918.8012
101 | 2750186.4915 | 1261865.6003
102 | 2750189.9769 | 1261864.0166
103 | 2750287.6371 | 1262096.5038
104 | 2750270.1625 | 1262114.1862
105 | 2750263.2937 | 1262121.1246
106 | 2750246.1138 | 1262139.6987
107 | 2750231.9543 | 1262147.7709
108 | 2750236.9263 | 1262130.4198
109 | 2750221.6077 | 1262158.6079
110 | 2750234.5001 | 1262112.567
111 | 2750044.4131 | 1262260.3455
112 | 2750159.9774 | 1262156.9586
113 | 2750169.1576 | 1262153.7904
114 | 2750150.7023 | 1262160.401
115 | 2750169.5694 | 1262153.6483
116 | 2750146.7139 | 1262161.9431
117 | 2750118.7744 | 1262163.2464
118 | 2750090.2922 | 1262170.1861
119 | 2750115.7127 | 1262151.5741
120 | 2750072.163 | 1262174.0408
121 | 2750104.9289 | 1262198.775
122 | 2750079.1908 | 1262141.5622
123 | 2750117.5127 | 1262133.3845
124 | 2750044.9944 | 1262180.1658
125 | 2750086.9663 | 1262205.5705
126 | 2750111.5693 | 1262197.6472
127 | 2750075.7681 | 1262137.1624
128 | 2750126.3884 | 1262130.2883
129 | 2750043.2488 | 1262180.6679
130 | 2750124.0057 | 1262195.5349
131 | 2750132.6099 | 1262128.1179
132 | 2750025.6194 | 1262185.7389
133 | 2750129.7081 | 1262194.5663
134 | 2750007.9982 | 1262159.1877
135 | 2750007.0643 | 1262193.4089
136 | 2749997.9772 | 1262161.4433
137 | 2750002.6332 | 1262195.3322
138 | 2749988.3001 | 1262163.6215
139 | 2750009.0319 | 1262213.4653
140 | 2749973.1196 | 1262168.3943
141 | 2750009.9266 | 1262215.9089
142 | 2749968.58 | 1262169.9212
143 | 2750013.7316 | 1262239.1909
144 | 2750289.4539 | 1261818.8133
145 | 2750239.6565 | 1261765.9178
146 | 2750270.3769 | 1261827.4827
147 | 2750303.5489 | 1261843.3523
148 | 2750481.5152 | 1261991.8069
149 | 2750479.3013 | 1261956.0325
150 | 2750454.2486 | 1262005.6534
151 | 2750452.7444 | 1262001.0709
152 | 2750424.3566 | 1261929.9311
153 | 2750409.3319 | 1261918.8285
154 | 2750430.5003 | 1261965.1063
155 | 2750430.0398 | 1261964.9788
156 | 2750441.8863 | 1261974.6538
157 | 2750414.3771 | 1261960.1477
158 | 2750444.9809 | 1261980.4494
159 | 2750409.4776 | 1261958.5814
160 | 2750452.5758 | 1262000.3169
161 | 2750308.8958 | 1261983.9675
162 | 2750307.1505 | 1261955.0781
163 | 2750307.1979 | 1261944.2674
164 | 2750308.336 | 1261933.4349
165 | 2750328.3687 | 1261943.9722
166 | 2750347.5808 | 1261943.7042
167 | 2750312.5648 | 1261907.2878
168 | 2750314.8293 | 1261895.2679
169 | 2750348.3372 | 1261936.5261
170 | 2750347.9568 | 1261919.8816
171 | 2750344.8746 | 1261903.9957
172 | 2750329.7493 | 1261894.278
173 | 2750304.0421 | 1261889.8693
174 | 2750315.5007 | 1261891.6925
175 | 2750296.6818 | 1261889.1023
176 | 2750266.7071 | 1261886.7707
177 | 2750237.5187 | 1261764.3265
178 | 2750269.1956 | 1261828.0195
179 | 2750254.576 | 1261892.5122
180 | 2750246.7189 | 1261879.0816
181 | 2750257.5025 | 1261903.3683
182 | 2750237.0402 | 1261859.763
183 | 2750259.8364 | 1261911.2168
184 | 2750236.7585 | 1261859.2009
185 | 2750260.801 | 1261921.3436
186 | 2750230.0492 | 1261845.8092
187 | 2750241.2026 | 1261840.7407
188 | 2750213.4121 | 1261853.3685
189 | 2750204.632 | 1261768.8907
190 | 2750225.192 | 1261755.1508
191 | 2750306.6945 | 1262028.6725

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1