## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3340-26_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3340-26_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_3340-26_0_5_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_3340-26_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3340-26_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3340-26_0_5_node_35 | 0.4 | n |  | TRUE
6 | bus_LV_3340-26_0_5_node_173 | 0.4 | n |  | TRUE
7 | bus_LV_3340-26_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_3340-26_0_5_node_69 | 0.4 | n |  | TRUE
9 | bus_LV_3340-26_0_5_node_70 | 0.4 | n |  | TRUE
10 | bus_LV_3340-26_0_5_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_3340-26_0_5_node_31 | 0.4 | n |  | TRUE
12 | bus_LV_3340-26_0_5_node_39 | 0.4 | n |  | TRUE
13 | bus_LV_3340-26_0_5_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_3340-26_0_5_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_3340-26_0_5_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_3340-26_0_5_node_104 | 0.4 | n |  | TRUE
17 | bus_LV_3340-26_0_5_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_3340-26_0_5_node_94 | 0.4 | n |  | TRUE
19 | bus_LV_3340-26_0_5_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_3340-26_0_5_node_92 | 0.4 | n |  | TRUE
21 | bus_LV_3340-26_0_5_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_3340-26_0_5_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_3340-26_0_5_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_3340-26_0_5_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_3340-26_0_5_node_154 | 0.4 | n |  | TRUE
26 | bus_LV_3340-26_0_5_node_160 | 0.4 | n |  | TRUE
27 | bus_LV_3340-26_0_5_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_3340-26_0_5_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_3340-26_0_5_node_88 | 0.4 | n |  | TRUE
30 | bus_LV_3340-26_0_5_node_107 | 0.4 | n |  | TRUE
31 | bus_LV_3340-26_0_5_node_105 | 0.4 | n |  | TRUE
32 | bus_LV_3340-26_0_5_node_13 | 0.4 | n |  | TRUE
33 | bus_LV_3340-26_0_5_node_145 | 0.4 | n |  | TRUE
34 | bus_LV_3340-26_0_5_node_139 | 0.4 | n |  | TRUE
35 | bus_LV_3340-26_0_5_node_135 | 0.4 | n |  | TRUE
36 | bus_LV_3340-26_0_5_node_14 | 0.4 | n |  | TRUE
37 | bus_LV_3340-26_0_5_node_93 | 0.4 | n |  | TRUE
38 | bus_LV_3340-26_0_5_node_91 | 0.4 | n |  | TRUE
39 | bus_LV_3340-26_0_5_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_3340-26_0_5_node_116 | 0.4 | n |  | TRUE
41 | bus_LV_3340-26_0_5_node_111 | 0.4 | n |  | TRUE
42 | bus_LV_3340-26_0_5_node_16 | 0.4 | n |  | TRUE
43 | bus_LV_3340-26_0_5_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_3340-26_0_5_node_23 | 0.4 | n |  | TRUE
45 | bus_LV_3340-26_0_5_node_77 | 0.4 | n |  | TRUE
46 | bus_LV_3340-26_0_5_node_98 | 0.4 | n |  | TRUE
47 | bus_LV_3340-26_0_5_node_97 | 0.4 | n |  | TRUE
48 | bus_LV_3340-26_0_5_node_129 | 0.4 | n |  | TRUE
49 | bus_LV_3340-26_0_5_node_20 | 0.4 | n |  | TRUE
50 | bus_LV_3340-26_0_5_node_126 | 0.4 | n |  | TRUE
51 | bus_LV_3340-26_0_5_node_102 | 0.4 | n |  | TRUE
52 | bus_LV_3340-26_0_5_node_21 | 0.4 | n |  | TRUE
53 | bus_LV_3340-26_0_5_node_84 | 0.4 | n |  | TRUE
54 | bus_LV_3340-26_0_5_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_3340-26_0_5_node_87 | 0.4 | n |  | TRUE
56 | bus_LV_3340-26_0_5_node_24 | 0.4 | n |  | TRUE
57 | bus_LV_3340-26_0_5_node_78 | 0.4 | n |  | TRUE
58 | bus_LV_3340-26_0_5_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_3340-26_0_5_node_26 | 0.4 | n |  | TRUE
60 | bus_LV_3340-26_0_5_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_3340-26_0_5_node_67 | 0.4 | n |  | TRUE
62 | bus_LV_3340-26_0_5_node_28 | 0.4 | n |  | TRUE
63 | bus_LV_3340-26_0_5_node_177 | 0.4 | n |  | TRUE
64 | bus_LV_3340-26_0_5_node_149 | 0.4 | n |  | TRUE
65 | bus_LV_3340-26_0_5_node_29 | 0.4 | n |  | TRUE
66 | bus_LV_3340-26_0_5_node_151 | 0.4 | n |  | TRUE
67 | bus_LV_3340-26_0_5_node_150 | 0.4 | n |  | TRUE
68 | bus_LV_3340-26_0_5_node_30 | 0.4 | n |  | TRUE
69 | bus_LV_3340-26_0_5_node_142 | 0.4 | n |  | TRUE
70 | bus_LV_3340-26_0_5_node_141 | 0.4 | n |  | TRUE
71 | bus_LV_3340-26_0_5_node_178 | 0.4 | n |  | TRUE
72 | bus_LV_3340-26_0_5_node_32 | 0.4 | n |  | TRUE
73 | bus_LV_3340-26_0_5_node_174 | 0.4 | n |  | TRUE
74 | bus_LV_3340-26_0_5_node_33 | 0.4 | n |  | TRUE
75 | bus_LV_3340-26_0_5_node_100 | 0.4 | n |  | TRUE
76 | bus_LV_3340-26_0_5_node_48 | 0.4 | n |  | TRUE
77 | bus_LV_3340-26_0_5_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_3340-26_0_5_node_103 | 0.4 | n |  | TRUE
79 | bus_LV_3340-26_0_5_node_37 | 0.4 | n |  | TRUE
80 | bus_LV_3340-26_0_5_node_175 | 0.4 | n |  | TRUE
81 | bus_LV_3340-26_0_5_node_152 | 0.4 | n |  | TRUE
82 | bus_LV_3340-26_0_5_node_153 | 0.4 | n |  | TRUE
83 | bus_LV_3340-26_0_5_node_161 | 0.4 | n |  | TRUE
84 | bus_LV_3340-26_0_5_node_176 | 0.4 | n |  | TRUE
85 | bus_LV_3340-26_0_5_node_157 | 0.4 | n |  | TRUE
86 | bus_LV_3340-26_0_5_node_156 | 0.4 | n |  | TRUE
87 | bus_LV_3340-26_0_5_node_159 | 0.4 | n |  | TRUE
88 | bus_LV_3340-26_0_5_node_109 | 0.4 | n |  | TRUE
89 | bus_LV_3340-26_0_5_node_106 | 0.4 | n |  | TRUE
90 | bus_LV_3340-26_0_5_node_138 | 0.4 | n |  | TRUE
91 | bus_LV_3340-26_0_5_node_134 | 0.4 | n |  | TRUE
92 | bus_LV_3340-26_0_5_node_95 | 0.4 | n |  | TRUE
93 | bus_LV_3340-26_0_5_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_3340-26_0_5_node_110 | 0.4 | n |  | TRUE
95 | bus_LV_3340-26_0_5_node_96 | 0.4 | n |  | TRUE
96 | bus_LV_3340-26_0_5_node_131 | 0.4 | n |  | TRUE
97 | bus_LV_3340-26_0_5_node_127 | 0.4 | n |  | TRUE
98 | bus_LV_3340-26_0_5_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_3340-26_0_5_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_3340-26_0_5_node_41 | 0.4 | n |  | TRUE
101 | bus_LV_3340-26_0_5_node_140 | 0.4 | n |  | TRUE
102 | bus_LV_3340-26_0_5_node_79 | 0.4 | n |  | TRUE
103 | bus_LV_3340-26_0_5_node_71 | 0.4 | n |  | TRUE
104 | bus_LV_3340-26_0_5_node_155 | 0.4 | n |  | TRUE
105 | bus_LV_3340-26_0_5_node_147 | 0.4 | n |  | TRUE
106 | bus_LV_3340-26_0_5_node_143 | 0.4 | n |  | TRUE
107 | bus_LV_3340-26_0_5_node_144 | 0.4 | n |  | TRUE
108 | bus_LV_3340-26_0_5_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_3340-26_0_5_node_56 | 0.4 | n |  | TRUE
110 | bus_LV_3340-26_0_5_node_58 | 0.4 | n |  | TRUE
111 | bus_LV_3340-26_0_5_node_83 | 0.4 | n |  | TRUE
112 | bus_LV_3340-26_0_5_node_165 | 0.4 | n |  | TRUE
113 | bus_LV_3340-26_0_5_node_57 | 0.4 | n |  | TRUE
114 | bus_LV_3340-26_0_5_node_168 | 0.4 | n |  | TRUE
115 | bus_LV_3340-26_0_5_node_166 | 0.4 | n |  | TRUE
116 | bus_LV_3340-26_0_5_node_60 | 0.4 | n |  | TRUE
117 | bus_LV_3340-26_0_5_node_46 | 0.4 | n |  | TRUE
118 | bus_LV_3340-26_0_5_node_50 | 0.4 | n |  | TRUE
119 | bus_LV_3340-26_0_5_node_55 | 0.4 | n |  | TRUE
120 | bus_LV_3340-26_0_5_node_38 | 0.4 | n |  | TRUE
121 | bus_LV_3340-26_0_5_node_40 | 0.4 | n |  | TRUE
122 | bus_LV_3340-26_0_5_node_65 | 0.4 | n |  | TRUE
123 | bus_LV_3340-26_0_5_node_66 | 0.4 | n |  | TRUE
124 | bus_LV_3340-26_0_5_node_61 | 0.4 | n |  | TRUE
125 | bus_LV_3340-26_0_5_node_80 | 0.4 | n |  | TRUE
126 | bus_LV_3340-26_0_5_node_51 | 0.4 | n |  | TRUE
127 | bus_LV_3340-26_0_5_node_44 | 0.4 | n |  | TRUE
128 | bus_LV_3340-26_0_5_node_45 | 0.4 | n |  | TRUE
129 | bus_LV_3340-26_0_5_node_47 | 0.4 | n |  | TRUE
130 | bus_LV_3340-26_0_5_node_49 | 0.4 | n |  | TRUE
131 | bus_LV_3340-26_0_5_node_52 | 0.4 | n |  | TRUE
132 | bus_LV_3340-26_0_5_node_53 | 0.4 | n |  | TRUE
133 | bus_LV_3340-26_0_5_node_54 | 0.4 | n |  | TRUE
134 | bus_LV_3340-26_0_5_node_63 | 0.4 | n |  | TRUE
135 | bus_LV_3340-26_0_5_node_64 | 0.4 | n |  | TRUE
136 | bus_LV_3340-26_0_5_node_76 | 0.4 | n |  | TRUE
137 | bus_LV_3340-26_0_5_node_73 | 0.4 | n |  | TRUE
138 | bus_LV_3340-26_0_5_node_169 | 0.4 | n |  | TRUE
139 | bus_LV_3340-26_0_5_node_167 | 0.4 | n |  | TRUE
140 | bus_LV_3340-26_0_5_node_164 | 0.4 | n |  | TRUE
141 | bus_LV_3340-26_0_5_node_162 | 0.4 | n |  | TRUE
142 | bus_LV_3340-26_0_5_node_163 | 0.4 | n |  | TRUE
143 | bus_LV_3340-26_0_5_node_74 | 0.4 | n |  | TRUE
144 | bus_LV_3340-26_0_5_node_75 | 0.4 | n |  | TRUE
145 | bus_LV_3340-26_0_5_node_81 | 0.4 | n |  | TRUE
146 | bus_LV_3340-26_0_5_node_82 | 0.4 | n |  | TRUE
147 | bus_LV_3340-26_0_5_node_89 | 0.4 | n |  | TRUE
148 | bus_LV_3340-26_0_5_node_90 | 0.4 | n |  | TRUE
149 | bus_LV_3340-26_0_5_node_99 | 0.4 | n |  | TRUE
150 | bus_LV_3340-26_0_5_node_125 | 0.4 | n |  | TRUE
151 | bus_LV_3340-26_0_5_node_123 | 0.4 | n |  | TRUE
152 | bus_LV_3340-26_0_5_node_108 | 0.4 | n |  | TRUE
153 | bus_LV_3340-26_0_5_node_112 | 0.4 | n |  | TRUE
154 | bus_LV_3340-26_0_5_node_114 | 0.4 | n |  | TRUE
155 | bus_LV_3340-26_0_5_node_115 | 0.4 | n |  | TRUE
156 | bus_LV_3340-26_0_5_node_117 | 0.4 | n |  | TRUE
157 | bus_LV_3340-26_0_5_node_118 | 0.4 | n |  | TRUE
158 | bus_LV_3340-26_0_5_node_132 | 0.4 | n |  | TRUE
159 | bus_LV_3340-26_0_5_node_133 | 0.4 | n |  | TRUE
160 | bus_LV_3340-26_0_5_node_119 | 0.4 | n |  | TRUE
161 | bus_LV_3340-26_0_5_node_120 | 0.4 | n |  | TRUE
162 | bus_LV_3340-26_0_5_node_121 | 0.4 | n |  | TRUE
163 | bus_LV_3340-26_0_5_node_122 | 0.4 | n |  | TRUE
164 | bus_LV_3340-26_0_5_node_124 | 0.4 | n |  | TRUE
165 | bus_LV_3340-26_0_5_node_128 | 0.4 | n |  | TRUE
166 | bus_LV_3340-26_0_5_node_130 | 0.4 | n |  | TRUE
167 | bus_LV_3340-26_0_5_node_172 | 0.4 | n |  | TRUE
168 | bus_LV_3340-26_0_5_node_146 | 0.4 | n |  | TRUE
169 | bus_LV_3340-26_0_5_node_136 | 0.4 | n |  | TRUE
170 | bus_LV_3340-26_0_5_node_137 | 0.4 | n |  | TRUE
171 | bus_LV_3340-26_0_5_node_148 | 0.4 | n |  | TRUE
172 | bus_LV_3340-26_0_5_node_158 | 0.4 | n |  | TRUE
173 | bus_LV_3340-26_0_5_node_170 | 0.4 | n |  | TRUE
174 | bus_LV_3340-26_0_5_node_171 | 0.4 | n |  | TRUE
175 | bus_MV_585_0_node_187 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3340-26_0_5_load_0 | 0 | 0.012365 | 0.0030989 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3340-26_0_5_load_35 | 5 | 0.012902 | 0.0032336 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3340-26_0_5_load_173 | 6 | 0.0094426 | 0.0023665 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3340-26_0_5_load_69 | 8 | 0.014209 | 0.003561 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3340-26_0_5_load_70 | 9 | 0.010721 | 0.0026869 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3340-26_0_5_load_39 | 12 | 0.0093072 | 0.0023326 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3340-26_0_5_load_104 | 16 | 0.002035 | 0.00051001 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3340-26_0_5_load_94 | 18 | 0.0057942 | 0.0014522 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3340-26_0_5_load_92 | 20 | 0.007864 | 0.0019709 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3340-26_0_5_load_36 | 23 | 0.0043916 | 0.0011006 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3340-26_0_5_load_160 | 26 | 0.0027589 | 0.00069145 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3340-26_0_5_load_88 | 29 | 0.009802 | 0.0024566 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3340-26_0_5_load_107 | 30 | 0.0017807 | 0.00044629 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3340-26_0_5_load_105 | 31 | 0.0018533 | 0.00046449 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3340-26_0_5_load_145 | 33 | 0.0051268 | 0.0012849 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3340-26_0_5_load_139 | 34 | 0.0037035 | 0.00092818 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3340-26_0_5_load_135 | 35 | 0.0025462 | 0.00063815 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3340-26_0_5_load_93 | 37 | 0.009221 | 0.002311 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3340-26_0_5_load_91 | 38 | 0.0041744 | 0.0010462 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3340-26_0_5_load_116 | 40 | 0.0018529 | 0.00046439 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3340-26_0_5_load_77 | 45 | 0.0077061 | 0.0019313 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3340-26_0_5_load_98 | 46 | 0.010584 | 0.0026526 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3340-26_0_5_load_97 | 47 | 0.0015431 | 0.00038675 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3340-26_0_5_load_129 | 48 | 0.0079765 | 0.0019991 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3340-26_0_5_load_126 | 50 | 0.00053849 | 0.00013496 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3340-26_0_5_load_102 | 51 | 0.0012102 | 0.00030331 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3340-26_0_5_load_72 | 54 | 0.0034868 | 0.00087387 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3340-26_0_5_load_87 | 55 | 0.012933 | 0.0032413 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3340-26_0_5_load_43 | 58 | 0.0046984 | 0.0011775 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3340-26_0_5_load_67 | 61 | 0.005991 | 0.0015015 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3340-26_0_5_load_177 | 63 | 0.010787 | 0.0027036 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3340-26_0_5_load_150 | 67 | 0.015672 | 0.0039277 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3340-26_0_5_load_141 | 70 | 0.0078323 | 0.001963 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3340-26_0_5_load_178 | 71 | 0.0055293 | 0.0013858 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3340-26_0_5_load_174 | 73 | 0.0016571 | 0.00041531 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3340-26_0_5_load_100 | 75 | 0.0010651 | 0.00026693 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3340-26_0_5_load_48 | 76 | 0.0060534 | 0.0015171 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3340-26_0_5_load_103 | 78 | 0.0058478 | 0.0014656 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3340-26_0_5_load_37 | 79 | 0.0066004 | 0.0016542 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3340-26_0_5_load_175 | 80 | 0.019022 | 0.0047675 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3340-26_0_5_load_161 | 83 | 0.0096847 | 0.0024272 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3340-26_0_5_load_176 | 84 | 0.011038 | 0.0027665 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3340-26_0_5_load_157 | 85 | 0.0057019 | 0.001429 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3340-26_0_5_load_156 | 86 | 0.005764 | 0.0014446 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3340-26_0_5_load_159 | 87 | 0.0018712 | 0.00046897 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3340-26_0_5_load_109 | 88 | 0.0016232 | 0.00040681 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3340-26_0_5_load_138 | 90 | 0.0038265 | 0.00095902 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3340-26_0_5_load_134 | 91 | 0.0035776 | 0.00089663 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3340-26_0_5_load_95 | 92 | 0.0037106 | 0.00092995 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3340-26_0_5_load_113 | 93 | 0.0031615 | 0.00079234 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3340-26_0_5_load_110 | 94 | 0.0030011 | 0.00075214 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3340-26_0_5_load_96 | 95 | 0.0038435 | 0.00096327 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3340-26_0_5_load_131 | 96 | 0.0035972 | 0.00090155 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3340-26_0_5_load_127 | 97 | 0.00069925 | 0.00017525 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3340-26_0_5_load_85 | 98 | 0.0044937 | 0.0011262 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3340-26_0_5_load_86 | 99 | 0.0059914 | 0.0015016 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3340-26_0_5_load_140 | 101 | 0.0016902 | 0.00042359 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3340-26_0_5_load_79 | 102 | 0.015528 | 0.0038916 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3340-26_0_5_load_71 | 103 | 0.0024381 | 0.00061104 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3340-26_0_5_load_155 | 104 | 0.010874 | 0.0027252 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3340-26_0_5_load_143 | 106 | 0.009791 | 0.0024539 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3340-26_0_5_load_101 | 108 | 0.0039464 | 0.00098905 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3340-26_0_5_load_83 | 111 | 0.0020251 | 0.00050754 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3340-26_0_5_load_165 | 112 | 0.0012579 | 0.00031526 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3340-26_0_5_load_168 | 114 | 0.0013203 | 0.00033091 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3340-26_0_5_load_166 | 115 | 0.0018605 | 0.0004663 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3340-26_0_5_load_55 | 119 | 0.0085074 | 0.0021322 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3340-26_0_5_load_65 | 122 | 0.0034957 | 0.00087612 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3340-26_0_5_load_66 | 123 | 0.0051557 | 0.0012921 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3340-26_0_5_load_51 | 126 | 0.0055101 | 0.001381 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3340-26_0_5_load_44 | 127 | 0.0062296 | 0.0015613 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3340-26_0_5_load_45 | 128 | 0.0053228 | 0.001334 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3340-26_0_5_load_49 | 130 | 0.0058228 | 0.0014593 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3340-26_0_5_load_52 | 131 | 0.0051928 | 0.0013014 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3340-26_0_5_load_54 | 133 | 0.0060687 | 0.001521 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3340-26_0_5_load_64 | 135 | 0.0021198 | 0.00053127 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3340-26_0_5_load_76 | 136 | 0.0027716 | 0.00069462 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3340-26_0_5_load_73 | 137 | 0.0057265 | 0.0014352 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3340-26_0_5_load_169 | 138 | 0.0013457 | 0.00033725 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3340-26_0_5_load_167 | 139 | 0.0025895 | 0.000649 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3340-26_0_5_load_164 | 140 | 0.001878 | 0.00047068 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3340-26_0_5_load_162 | 141 | 0.0014671 | 0.0003677 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3340-26_0_5_load_163 | 142 | 0.0013371 | 0.00033511 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3340-26_0_5_load_74 | 143 | 0.0032974 | 0.0008264 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3340-26_0_5_load_75 | 144 | 0.0032286 | 0.00080916 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3340-26_0_5_load_81 | 145 | 0.0026225 | 0.00065726 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3340-26_0_5_load_82 | 146 | 0.0033392 | 0.00083687 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3340-26_0_5_load_89 | 147 | 0.003358 | 0.00084159 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3340-26_0_5_load_99 | 149 | 0.0096419 | 0.0024165 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3340-26_0_5_load_125 | 150 | 0.0038677 | 0.00096934 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3340-26_0_5_load_123 | 151 | 0.011206 | 0.0028086 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3340-26_0_5_load_108 | 152 | 0.0029634 | 0.00074271 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3340-26_0_5_load_114 | 154 | 0.0028048 | 0.00070295 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3340-26_0_5_load_115 | 155 | 0.0034925 | 0.00087529 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3340-26_0_5_load_117 | 156 | 0.0022434 | 0.00056224 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3340-26_0_5_load_118 | 157 | 0.0032213 | 0.00080734 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3340-26_0_5_load_132 | 158 | 0.0025626 | 0.00064225 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3340-26_0_5_load_133 | 159 | 0.0041132 | 0.0010309 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3340-26_0_5_load_119 | 160 | 0.003326 | 0.00083357 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3340-26_0_5_load_120 | 161 | 0.002924 | 0.00073281 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3340-26_0_5_load_122 | 163 | 0.0029144 | 0.00073042 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3340-26_0_5_load_124 | 164 | 0.0047738 | 0.0011964 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3340-26_0_5_load_128 | 165 | 0.00043055 | 0.00010791 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3340-26_0_5_load_130 | 166 | 0.0039825 | 0.00099811 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3340-26_0_5_load_172 | 167 | 0.0028757 | 0.00072073 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3340-26_0_5_load_136 | 169 | 0.0055098 | 0.0013809 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3340-26_0_5_load_137 | 170 | 0.0036291 | 0.00090953 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3340-26_0_5_load_148 | 171 | 0.0096041 | 0.002407 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3340-26_0_5_load_158 | 172 | 0.0090227 | 0.0022613 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_3340-26_0_5_load_170 | 173 | 0.0013862 | 0.00034741 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_3340-26_0_5_load_171 | 174 | 0.0012938 | 0.00032427 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3340-26_0_5_line_0 |  | 0 | 1 | 0.011433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3340-26_0_5_line_1 |  | 1 | 5 | 0.022757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3340-26_0_5_line_2 |  | 1 | 2 | 0.023347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_3340-26_0_5_line_3 |  | 2 | 3 | 0.13554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_3340-26_0_5_line_4 |  | 2 | 4 | 0.14756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_3340-26_0_5_line_5 |  | 3 | 6 | 0.031719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3340-26_0_5_line_6 |  | 4 | 7 | 0.032337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_3340-26_0_5_line_7 |  | 4 | 8 | 0.01639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_3340-26_0_5_line_8 |  | 7 | 9 | 0.018887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_3340-26_0_5_line_9 |  | 9 | 77 | 0.020568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_3340-26_0_5_line_10 |  | 10 | 11 | 0.19568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_3340-26_0_5_line_11 |  | 10 | 12 | 0.038384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_3340-26_0_5_line_12 |  | 11 | 71 | 0.005895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_3340-26_0_5_line_13 |  | 12 | 21 | 0.061465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_3340-26_0_5_line_14 |  | 13 | 14 | 0.0098275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_3340-26_0_5_line_15 |  | 13 | 15 | 0.009191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_3340-26_0_5_line_16 |  | 13 | 16 | 0.044552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_3340-26_0_5_line_17 |  | 14 | 39 | 0.006786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_3340-26_0_5_line_18 |  | 15 | 30 | 0.020282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_3340-26_0_5_line_19 |  | 15 | 31 | 0.0098514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_3340-26_0_5_line_20 |  | 16 | 78 | 0.023799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_3340-26_0_5_line_21 |  | 17 | 18 | 0.024393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3340-26_0_5_line_22 |  | 17 | 19 | 0.037044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_3340-26_0_5_line_23 |  | 17 | 20 | 0.060753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_3340-26_0_5_line_24 |  | 19 | 46 | 0.045631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_3340-26_0_5_line_25 |  | 19 | 22 | 0.030727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_3340-26_0_5_line_26 |  | 19 | 47 | 0.13685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_3340-26_0_5_line_27 |  | 20 | 38 | 0.01512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_3340-26_0_5_line_28 |  | 21 | 22 | 0.008491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_3340-26_0_5_line_29 |  | 21 | 23 | 0.02142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_3340-26_0_5_line_30 |  | 22 | 58 | 0.005681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_3340-26_0_5_line_31 |  | 23 | 79 | 0.01225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_3340-26_0_5_line_32 |  | 24 | 25 | 0.081821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_3340-26_0_5_line_33 |  | 24 | 26 | 0.059676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_3340-26_0_5_line_34 |  | 25 | 80 | 0.00748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_3340-26_0_5_line_35 |  | 25 | 81 | 0.019655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_3340-26_0_5_line_36 |  | 26 | 87 | 0.024181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_3340-26_0_5_line_37 |  | 27 | 28 | 0.016729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_3340-26_0_5_line_38 |  | 27 | 29 | 0.0084843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_3340-26_0_5_line_39 |  | 28 | 48 | 0.033734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_3340-26_0_5_line_40 |  | 28 | 49 | 0.040612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_3340-26_0_5_line_41 |  | 28 | 50 | 0.013772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_3340-26_0_5_line_42 |  | 29 | 55 | 0.018361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_3340-26_0_5_line_43 |  | 30 | 88 | 0.022797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3340-26_0_5_line_44 |  | 31 | 89 | 0.015238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_3340-26_0_5_line_45 |  | 32 | 33 | 0.01864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_3340-26_0_5_line_46 |  | 32 | 34 | 0.010435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_3340-26_0_5_line_47 |  | 32 | 35 | 0.016104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_3340-26_0_5_line_48 |  | 34 | 90 | 0.0070398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_3340-26_0_5_line_49 |  | 35 | 91 | 0.021534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_3340-26_0_5_line_50 |  | 36 | 37 | 0.018365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_3340-26_0_5_line_51 |  | 36 | 38 | 0.010992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_3340-26_0_5_line_52 |  | 37 | 92 | 0.038927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_3340-26_0_5_line_53 |  | 39 | 40 | 0.041613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_3340-26_0_5_line_54 |  | 39 | 41 | 0.016816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_3340-26_0_5_line_55 |  | 40 | 87 | 0.0077006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_3340-26_0_5_line_56 |  | 41 | 93 | 0.031409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_3340-26_0_5_line_57 |  | 41 | 94 | 0.0015107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_3340-26_0_5_line_58 |  | 42 | 43 | 0.011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_3340-26_0_5_line_59 |  | 42 | 44 | 0.018505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_3340-26_0_5_line_60 |  | 42 | 45 | 0.0094953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_3340-26_0_5_line_61 |  | 43 | 58 | 0.0084928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_3340-26_0_5_line_62 |  | 44 | 55 | 0.0070413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_3340-26_0_5_line_63 |  | 45 | 56 | 0.025091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_3340-26_0_5_line_64 |  | 47 | 95 | 0.015168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_3340-26_0_5_line_65 |  | 48 | 96 | 0.0049527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_3340-26_0_5_line_66 |  | 49 | 51 | 0.03829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_3340-26_0_5_line_67 |  | 50 | 97 | 0.0064904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_3340-26_0_5_line_68 |  | 51 | 78 | 0.047573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_3340-26_0_5_line_69 |  | 52 | 53 | 0.01547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_3340-26_0_5_line_70 |  | 52 | 54 | 0.0094148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_3340-26_0_5_line_71 |  | 53 | 98 | 0.013106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_3340-26_0_5_line_72 |  | 53 | 99 | 0.015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_3340-26_0_5_line_73 |  | 54 | 100 | 0.014256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_3340-26_0_5_line_74 |  | 56 | 57 | 0.033658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3340-26_0_5_line_75 |  | 57 | 102 | 0.015091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3340-26_0_5_line_76 |  | 57 | 103 | 0.022034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3340-26_0_5_line_77 |  | 59 | 60 | 0.10294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_3340-26_0_5_line_78 |  | 59 | 61 | 0.027273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_3340-26_0_5_line_79 |  | 60 | 76 | 0.058406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_3340-26_0_5_line_80 |  | 61 | 77 | 0.017839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_3340-26_0_5_line_81 |  | 62 | 63 | 0.002154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_3340-26_0_5_line_82 |  | 62 | 64 | 0.035717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_3340-26_0_5_line_83 |  | 64 | 104 | 0.002141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_3340-26_0_5_line_84 |  | 64 | 105 | 0.012152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_3340-26_0_5_line_85 |  | 65 | 66 | 0.081513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_3340-26_0_5_line_86 |  | 65 | 67 | 0.020308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_3340-26_0_5_line_87 |  | 66 | 85 | 0.0057985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_3340-26_0_5_line_88 |  | 66 | 86 | 0.0065589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_3340-26_0_5_line_89 |  | 67 | 105 | 0.030905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_3340-26_0_5_line_90 |  | 68 | 69 | 0.03647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_3340-26_0_5_line_91 |  | 68 | 70 | 0.01418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_3340-26_0_5_line_92 |  | 69 | 106 | 0.013044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_3340-26_0_5_line_93 |  | 69 | 107 | 0.036525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_3340-26_0_5_line_94 |  | 72 | 73 | 0.001759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3340-26_0_5_line_95 |  | 72 | 74 | 0.048842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_3340-26_0_5_line_96 |  | 74 | 75 | 0.015522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_3340-26_0_5_line_97 |  | 75 | 108 | 0.030361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_3340-26_0_5_line_98 |  | 76 | 117 | 0.023642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_3340-26_0_5_line_99 |  | 79 | 120 | 0.036465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_3340-26_0_5_line_100 |  | 81 | 84 | 0.044581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_3340-26_0_5_line_101 |  | 81 | 82 | 0.019331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_3340-26_0_5_line_102 |  | 82 | 83 | 0.055667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_3340-26_0_5_line_103 |  | 85 | 172 | 0.010578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_3340-26_0_5_line_104 |  | 88 | 101 | 0.0087552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3340-26_0_5_line_105 |  | 89 | 152 | 0.032732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_3340-26_0_5_line_106 |  | 90 | 170 | 0.0098349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_3340-26_0_5_line_107 |  | 91 | 166 | 0.0015781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_3340-26_0_5_line_108 |  | 92 | 150 | 0.001508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_3340-26_0_5_line_109 |  | 94 | 153 | 0.022205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_3340-26_0_5_line_110 |  | 96 | 167 | 0.0016191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_3340-26_0_5_line_111 |  | 97 | 165 | 0.018863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_3340-26_0_5_line_112 |  | 98 | 116 | 0.022968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_3340-26_0_5_line_113 |  | 99 | 148 | 0.01947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_3340-26_0_5_line_114 |  | 100 | 120 | 0.014915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_3340-26_0_5_line_115 |  | 105 | 168 | 0.05901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_3340-26_0_5_line_116 |  | 107 | 171 | 0.011764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_3340-26_0_5_line_117 |  | 107 | 168 | 0.008424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_3340-26_0_5_line_118 |  | 108 | 116 | 0.018532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_3340-26_0_5_line_119 |  | 109 | 110 | 0.11098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_3340-26_0_5_line_120 |  | 109 | 111 | 0.083744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_3340-26_0_5_line_121 |  | 110 | 112 | 0.037723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_3340-26_0_5_line_122 |  | 110 | 113 | 0.06056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_3340-26_0_5_line_123 |  | 111 | 136 | 0.017653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_3340-26_0_5_line_124 |  | 112 | 140 | 0.0065795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_3340-26_0_5_line_125 |  | 113 | 114 | 0.0093689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_3340-26_0_5_line_126 |  | 113 | 115 | 0.011066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_3340-26_0_5_line_127 |  | 114 | 138 | 0.002772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_3340-26_0_5_line_128 |  | 115 | 139 | 0.013992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_3340-26_0_5_line_129 |  | 117 | 130 | 0.02627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_3340-26_0_5_line_130 |  | 117 | 118 | 0.00373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_3340-26_0_5_line_131 |  | 117 | 127 | 0.019338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_3340-26_0_5_line_132 |  | 118 | 119 | 0.034287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_3340-26_0_5_line_133 |  | 119 | 134 | 0.031001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_3340-26_0_5_line_134 |  | 120 | 121 | 0.014459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_3340-26_0_5_line_135 |  | 121 | 122 | 0.003591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_3340-26_0_5_line_136 |  | 121 | 123 | 0.01945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_3340-26_0_5_line_137 |  | 121 | 124 | 0.021371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_3340-26_0_5_line_138 |  | 123 | 125 | 0.015534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_3340-26_0_5_line_139 |  | 124 | 126 | 0.018554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_3340-26_0_5_line_140 |  | 125 | 144 | 0.02188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_3340-26_0_5_line_141 |  | 128 | 129 | 0.021228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_3340-26_0_5_line_142 |  | 129 | 131 | 0.030201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_3340-26_0_5_line_143 |  | 129 | 132 | 0.003781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_3340-26_0_5_line_144 |  | 130 | 133 | 0.023289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
145 | LV_3340-26_0_5_line_145 |  | 132 | 134 | 0.02337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_3340-26_0_5_line_146 |  | 132 | 135 | 0.0064133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
147 | LV_3340-26_0_5_line_147 |  | 134 | 136 | 0.01312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
148 | LV_3340-26_0_5_line_148 |  | 135 | 137 | 0.0074293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_3340-26_0_5_line_149 |  | 137 | 143 | 0.017455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_3340-26_0_5_line_150 |  | 138 | 173 | 0.0068936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
151 | LV_3340-26_0_5_line_151 |  | 140 | 142 | 0.0052774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
152 | LV_3340-26_0_5_line_152 |  | 141 | 142 | 0.0054037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
153 | LV_3340-26_0_5_line_153 |  | 143 | 144 | 0.0010425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_3340-26_0_5_line_154 |  | 145 | 146 | 0.012789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_3340-26_0_5_line_155 |  | 146 | 147 | 0.009998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
156 | LV_3340-26_0_5_line_156 |  | 147 | 148 | 0.0068934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
157 | LV_3340-26_0_5_line_157 |  | 148 | 149 | 0.024385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
158 | LV_3340-26_0_5_line_158 |  | 150 | 151 | 0.020221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
159 | LV_3340-26_0_5_line_159 |  | 151 | 162 | 0.019214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
160 | LV_3340-26_0_5_line_160 |  | 153 | 154 | 0.0052238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
161 | LV_3340-26_0_5_line_161 |  | 153 | 155 | 0.02273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
162 | LV_3340-26_0_5_line_162 |  | 154 | 156 | 0.02087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
163 | LV_3340-26_0_5_line_163 |  | 155 | 157 | 0.0012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
164 | LV_3340-26_0_5_line_164 |  | 156 | 158 | 0.0085055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
165 | LV_3340-26_0_5_line_165 |  | 158 | 159 | 0.017729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
166 | LV_3340-26_0_5_line_166 |  | 159 | 168 | 0.016339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
167 | LV_3340-26_0_5_line_167 |  | 160 | 161 | 0.0049389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_3340-26_0_5_line_168 |  | 160 | 162 | 0.014472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
169 | LV_3340-26_0_5_line_169 |  | 161 | 163 | 0.023154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
170 | LV_3340-26_0_5_line_170 |  | 162 | 164 | 0.007563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
171 | LV_3340-26_0_5_line_171 |  | 165 | 166 | 0.0048284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
172 | LV_3340-26_0_5_line_172 |  | 169 | 170 | 0.02428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
173 | LV_3340-26_0_5_line_173 |  | 173 | 174 | 0.0067689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3340-26_0_5_trafo_24 | 0.63 MVA 20/0.4 kV | 175 | 56 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2704558.3975 | 1232359.7767 | 2704563.0228 | 1232370.2326
1 | 2704579.1932 | 1232350.4021 | 2704558.3975 | 1232359.7767
2 | 2704536.5753 | 1232351.3088 | 2704558.3975 | 1232359.7767
3 | 2704512.2191 | 1232405.0766 | 2704480.6046 | 1232393.1453 | 2704485.4599 | 1232372.0147 | 2704490.1059 | 1232354.1718 | 2704494.305 | 1232337.622 | 2704516.2197 | 1232342.9891 | 2704536.5753 | 1232351.3088
4 | 2704536.5753 | 1232351.3088 | 2704516.2197 | 1232342.9891 | 2704494.305 | 1232337.622 | 2704500.0876 | 1232311.5707 | 2704503.6416 | 1232312.3226 | 2704504.9961 | 1232312.3909 | 2704540.8644 | 1232319.3268 | 2704574.9932 | 1232326.121
5 | 2704512.2191 | 1232405.0766 | 2704533.5937 | 1232413.1474 | 2704541.9594 | 1232416.3413
6 | 2704580.7187 | 1232294.2978 | 2704577.5619 | 1232311.4218 | 2704574.9932 | 1232326.121
7 | 2704574.9932 | 1232326.121 | 2704591.1027 | 1232329.1404
8 | 2704580.7187 | 1232294.2978 | 2704599.1373 | 1232298.4787
9 | 2704618.4692 | 1232304.8811 | 2704612.7413 | 1232301.5667 | 2704599.1373 | 1232298.4787
10 | 2704499.0171 | 1232508.9005 | 2704494.9107 | 1232511.5748 | 2704507.167 | 1232526.9352 | 2704511.0882 | 1232533.4979 | 2704507.7099 | 1232535.251 | 2704489.6959 | 1232569.9382 | 2704480.9996 | 1232584.6965 | 2704477.3399 | 1232590.3921 | 2704470.6997 | 1232598.4815 | 2704457.6576 | 1232608.8601 | 2704441.7734 | 1232613.7625 | 2704434.7583 | 1232622.5014 | 2704431.8933 | 1232626.076 | 2704429.7254 | 1232628.7732 | 2704420.3807 | 1232649.8361 | 2704415.7216 | 1232659.4059
11 | 2704499.0171 | 1232508.9005 | 2704503.8071 | 1232515.1561 | 2704522.3458 | 1232539.3822
12 | 2704419.6735 | 1232663.7897 | 2704415.7216 | 1232659.4059
13 | 2704558.6499 | 1232588.9761 | 2704549.0635 | 1232575.5529 | 2704527.8454 | 1232546.5691 | 2704522.3458 | 1232539.3822
14 | 2704708.9263 | 1232804.3503 | 2704705.3732 | 1232807.0009 | 2704700.8605 | 1232809.9569
15 | 2704713.9171 | 1232812.0774 | 2704708.9263 | 1232804.3503
16 | 2704708.9263 | 1232804.3503 | 2704684.251 | 1232767.2559
17 | 2704704.5312 | 1232815.6704 | 2704700.8605 | 1232809.9569
18 | 2704713.9171 | 1232812.0774 | 2704725.0495 | 1232829.0313
19 | 2704713.9171 | 1232812.0774 | 2704723.1255 | 1232808.5766
20 | 2704684.251 | 1232767.2559 | 2704671.0696 | 1232747.4402
21 | 2704543.2001 | 1232643.6345 | 2704559.2366 | 1232651.5892 | 2704563.0535 | 1232656.8403
22 | 2704543.2001 | 1232643.6345 | 2704539.7015 | 1232641.8939 | 2704545.0594 | 1232626.6321 | 2704549.428 | 1232614.6555 | 2704545.5411 | 1232613.0304
23 | 2704543.2001 | 1232643.6345 | 2704534.8299 | 1232667.8278 | 2704526.4887 | 1232690.8095 | 2704522.8976 | 1232700.8934
24 | 2704545.5411 | 1232613.0304 | 2704516.86 | 1232601.0281 | 2704522.6279 | 1232587.6809
25 | 2704545.5411 | 1232613.0304 | 2704549.428 | 1232614.6555 | 2704554.6422 | 1232610.5663 | 2704560.0737 | 1232608.338 | 2704558.5948 | 1232602.8634 | 2704563.3878 | 1232596.0314
26 | 2704545.5411 | 1232613.0304 | 2704544.54 | 1232615.6925 | 2704542.3615 | 1232618.99 | 2704539.9956 | 1232622.1731 | 2704537.6207 | 1232626.3011 | 2704532.6445 | 1232640.1018 | 2704531.8709 | 1232644.4692 | 2704531.5211 | 1232648.4216 | 2704531.4491 | 1232652.5123 | 2704516.3995 | 1232696.0694 | 2704504.6909 | 1232727.9432 | 2704501.0093 | 1232735.3173 | 2704497.8452 | 1232740.2656
27 | 2704517.8433 | 1232715.1437 | 2704518.3545 | 1232713.6504 | 2704522.8976 | 1232700.8934
28 | 2704558.6499 | 1232588.9761 | 2704563.3878 | 1232596.0314
29 | 2704558.6499 | 1232588.9761 | 2704562.5673 | 1232578.9708 | 2704568.8088 | 1232570.3108
30 | 2704563.3878 | 1232596.0314 | 2704566.5233 | 1232591.2941
31 | 2704576.9494 | 1232561.1611 | 2704569.0882 | 1232569.9231 | 2704568.8088 | 1232570.3108
32 | 2704700.9472 | 1232937.7994 | 2704714.3581 | 1232939.5592 | 2704730.3988 | 1232941.2097 | 2704745.5362 | 1232935.2497 | 2704757.7394 | 1232935.4983 | 2704763.5373 | 1232939.1032 | 2704773.3972 | 1232930.0924 | 2704775.991 | 1232927.7252
33 | 2704775.991 | 1232927.7252 | 2704770.6019 | 1232921.1252 | 2704764.3112 | 1232910.2506 | 2704753.554 | 1232888.1221 | 2704745.865 | 1232876.4379
34 | 2704700.9472 | 1232937.7994 | 2704701.7447 | 1232930.3634
35 | 2704700.9472 | 1232937.7994 | 2704697.3357 | 1232937.3244 | 2704686.1681 | 1232935.8933 | 2704682.8814 | 1232935.4684 | 2704681.4618 | 1232935.2321
36 | 2704732.4185 | 1232856.3415 | 2704737.9256 | 1232864.3732 | 2704745.865 | 1232876.4379
37 | 2704591.0031 | 1232650.5027 | 2704594.6424 | 1232655.8597 | 2704601.0981 | 1232663.846
38 | 2704591.0031 | 1232650.5027 | 2704586.363 | 1232643.3997
39 | 2704601.0981 | 1232663.846 | 2704580.5946 | 1232676.0389 | 2704577.4327 | 1232685.3985
40 | 2704601.0981 | 1232663.846 | 2704606.3023 | 1232660.7575 | 2704621.4859 | 1232683.1638 | 2704623.5139 | 1232675.9496
41 | 2704601.0981 | 1232663.846 | 2704606.4341 | 1232669.1884 | 2704610.0873 | 1232674.2235
42 | 2704576.3216 | 1232628.0281 | 2704586.363 | 1232643.3997
43 | 2704725.0495 | 1232829.0313 | 2704737.5624 | 1232848.0874
44 | 2704737.3691 | 1232803.1616 | 2704723.1255 | 1232808.5766
45 | 2704648.9777 | 1232731.6954 | 2704659.277 | 1232747.2311
46 | 2704648.9777 | 1232731.6954 | 2704640.4946 | 1232737.7729 | 2704640.4946 | 1232737.7729
47 | 2704648.9777 | 1232731.6954 | 2704639.9936 | 1232718.3308
48 | 2704637.8311 | 1232744.2894 | 2704640.4946 | 1232737.7729
49 | 2704627.9802 | 1232700.4596 | 2704639.9936 | 1232718.3308
50 | 2704514.2829 | 1232725.5433 | 2704523.4028 | 1232729.7513 | 2704530.1795 | 1232734.58
51 | 2704514.2829 | 1232725.5433 | 2704517.8433 | 1232715.1437
52 | 2704565.5722 | 1232748.8917 | 2704543.2756 | 1232743.9114 | 2704530.1795 | 1232734.58
53 | 2704704.5312 | 1232815.6704 | 2704728.0637 | 1232849.9905
54 | 2704704.5312 | 1232815.6704 | 2704693.541 | 1232821.7814 | 2704689.395 | 1232822.8425
55 | 2704732.4185 | 1232856.3415 | 2704728.0637 | 1232849.9905
56 | 2704689.395 | 1232822.8425 | 2704689.4157 | 1232827.6799 | 2704680.854 | 1232852.837
57 | 2704689.395 | 1232822.8425 | 2704687.895 | 1232823.022
58 | 2704571.1694 | 1232598.4034 | 2704577.3088 | 1232607.585
59 | 2704572.4708 | 1232622.1331 | 2704572.1263 | 1232609.006 | 2704577.3088 | 1232607.585
60 | 2704577.3088 | 1232607.585 | 2704584.1455 | 1232608.5616 | 2704586.0066 | 1232610.3615
61 | 2704571.1694 | 1232598.4034 | 2704566.5233 | 1232591.2941
62 | 2704572.4708 | 1232622.1331 | 2704576.3216 | 1232628.0281
63 | 2704604.0426 | 1232627.8039 | 2704586.0066 | 1232610.3615
64 | 2704487.8992 | 1232751.6616 | 2704493.15 | 1232746.4209 | 2704496.882 | 1232741.7719 | 2704497.8452 | 1232740.2656
65 | 2704575.8476 | 1232690.0907 | 2704577.4327 | 1232685.3985
66 | 2704623.5139 | 1232675.9496 | 2704644.7208 | 1232707.83
67 | 2704613.8827 | 1232679.4881 | 2704613.5765 | 1232679.0326 | 2704610.0873 | 1232674.2235
68 | 2704644.7208 | 1232707.83 | 2704671.0696 | 1232747.4402
69 | 2704649.8022 | 1232555.4992 | 2704634.8977 | 1232551.2003
70 | 2704634.8977 | 1232551.2003 | 2704626.4584 | 1232547.027
71 | 2704649.8022 | 1232555.4992 | 2704662.5483 | 1232558.5476
72 | 2704649.8022 | 1232555.4992 | 2704654.9883 | 1232541.3143
73 | 2704613.6799 | 1232540.7079 | 2704626.4584 | 1232547.027
74 | 2704604.0426 | 1232627.8039 | 2704610.8719 | 1232601.2485 | 2704609.9885 | 1232595.0728
75 | 2704609.9885 | 1232595.0728 | 2704618.5909 | 1232582.6592
76 | 2704609.9885 | 1232595.0728 | 2704596.7248 | 1232585.7657 | 2704594.6677 | 1232583.8836 | 2704592.4191 | 1232581.8337
77 | 2704622.1727 | 1232266.1837 | 2704622.6844 | 1232258.6315 | 2704623.6685 | 1232244.0378 | 2704626.0413 | 1232245.2027 | 2704646.4116 | 1232254.8463 | 2704651.3902 | 1232257.2802 | 2704696.5132 | 1232278.8687
78 | 2704622.1727 | 1232266.1837 | 2704624.4949 | 1232266.7806 | 2704629.108 | 1232271.0428 | 2704630.1149 | 1232277.0873 | 2704628.9142 | 1232283.3375 | 2704626.2519 | 1232288.8288
79 | 2704696.5132 | 1232278.8687 | 2704694.2339 | 1232284.4328 | 2704687.3035 | 1232302.9358 | 2704680.0935 | 1232323.9802 | 2704677.2936 | 1232333.9851
80 | 2704618.4692 | 1232304.8811 | 2704626.2519 | 1232288.8288
81 | 2704541.4053 | 1232858.3538 | 2704541.9645 | 1232856.2731
82 | 2704574.2906 | 1232864.6258 | 2704573.7429 | 1232866.9179 | 2704541.4053 | 1232858.3538
83 | 2704574.2906 | 1232864.6258 | 2704574.7892 | 1232862.5441
84 | 2704574.2906 | 1232864.6258 | 2704586.0725 | 1232867.7354
85 | 2704583.504 | 1232914.2587 | 2704605.7845 | 1232918.9432 | 2704609.4377 | 1232919.6302 | 2704620.4653 | 1232921.7036 | 2704626.2499 | 1232895.5412 | 2704624.4804 | 1232894.9652 | 2704625.306 | 1232891.9441 | 2704627.0549 | 1232885.5256 | 2704628.4638 | 1232880.3465
86 | 2704583.504 | 1232914.2587 | 2704589.5391 | 1232894.8686
87 | 2704628.4638 | 1232880.3465 | 2704630.8788 | 1232880.8227 | 2704631.4206 | 1232880.5876 | 2704633.5118 | 1232879.6682 | 2704633.9317 | 1232879.4754
88 | 2704628.4638 | 1232880.3465 | 2704626.094 | 1232879.8822 | 2704625.8499 | 1232879.5554 | 2704624.3985 | 1232877.684 | 2704623.5618 | 1232876.6018
89 | 2704586.0725 | 1232867.7354 | 2704590.3849 | 1232870.1242 | 2704593.1373 | 1232875.5212 | 2704593.5476 | 1232880.61 | 2704589.7892 | 1232894.0651 | 2704589.5391 | 1232894.8686
90 | 2704562.043 | 1232798.9163 | 2704529.4441 | 1232782.375
91 | 2704529.4441 | 1232782.375 | 2704524.9102 | 1232795.8102
92 | 2704556.8041 | 1232810.8665 | 2704562.043 | 1232798.9163
93 | 2704594.6866 | 1232815.492 | 2704562.043 | 1232798.9163
94 | 2704632.5605 | 1232639.17 | 2704632.0839 | 1232640.8628
95 | 2704632.5605 | 1232639.17 | 2704637.1459 | 1232623.0607 | 2704642.0718 | 1232622.447 | 2704647.2416 | 1232623.0384 | 2704651.0087 | 1232621.1366 | 2704662.9366 | 1232623.2927 | 2704667.8191 | 1232626.0029
96 | 2704667.8191 | 1232626.0029 | 2704671.9318 | 1232611.0353
97 | 2704671.9318 | 1232611.0353 | 2704679.9759 | 1232581.7596
98 | 2704670.8898 | 1232356.7429 | 2704672.7949 | 1232350.0603 | 2704677.2936 | 1232333.9851
99 | 2704600.6373 | 1232533.4618 | 2704592.5413 | 1232543.7827 | 2704576.9494 | 1232561.1611
100 | 2704681.4618 | 1232935.2321 | 2704690.79 | 1232895.3663 | 2704687.2622 | 1232894.4368
101 | 2704667.0034 | 1232940.4815 | 2704670.0466 | 1232937.1103 | 2704677.8366 | 1232938.9711 | 2704680.4135 | 1232939.2834 | 2704681.4618 | 1232935.2321
102 | 2704667.0034 | 1232940.4815 | 2704658.1367 | 1232950.2994 | 2704633.62 | 1232945.3196 | 2704616.7391 | 1232941.0173
103 | 2704632.8786 | 1232871.7622 | 2704636.2086 | 1232872.7437 | 2704633.9317 | 1232879.4754
104 | 2704742.3679 | 1232855.4058 | 2704737.5624 | 1232848.0874
105 | 2704737.3691 | 1232803.1616 | 2704723.2919 | 1232781.6196 | 2704721.2069 | 1232777.4575 | 2704720.6478 | 1232775.1819
106 | 2704634.1101 | 1232753.3933 | 2704637.8311 | 1232744.2894
107 | 2704627.9802 | 1232700.4596 | 2704627.0998 | 1232699.1499
108 | 2704565.5722 | 1232748.8917 | 2704567.0439 | 1232749.2204
109 | 2704665.7693 | 1232823.994 | 2704677.3283 | 1232824.2867 | 2704687.895 | 1232823.022
110 | 2704575.3294 | 1232691.6247 | 2704575.8476 | 1232690.0907
111 | 2704613.8827 | 1232679.4881 | 2704624.4061 | 1232695.1427
112 | 2704684.8859 | 1232563.8899 | 2704662.5483 | 1232558.5476
113 | 2704661.6738 | 1232523.0282 | 2704654.9883 | 1232541.3143
114 | 2704600.6373 | 1232533.4618 | 2704604.6114 | 1232536.156 | 2704610.6917 | 1232539.2319 | 2704613.6799 | 1232540.7079
115 | 2704602.2151 | 1232819.3163 | 2704601.8211 | 1232822.7675 | 2704601.1817 | 1232825.1024 | 2704599.7743 | 1232826.3231 | 2704598.4583 | 1232827.9456 | 2704598.0022 | 1232830.1948 | 2704598.2696 | 1232833.502 | 2704598.7777 | 1232836.0462 | 2704598.1465 | 1232837.9143 | 2704596.8147 | 1232840.0035 | 2704595.3542 | 1232842.0905 | 2704594.856 | 1232844.15 | 2704599.5961 | 1232849.3484 | 2704598.9517 | 1232854.9746 | 2704598.4391 | 1232857.423 | 2704596.8902 | 1232860.2312 | 2704592.9528 | 1232863.2086 | 2704589.2288 | 1232866.9682 | 2704586.0725 | 1232867.7354
116 | 2704589.6375 | 1232826.1223 | 2704594.6866 | 1232815.492
117 | 2704602.2151 | 1232819.3163 | 2704594.6866 | 1232815.492
118 | 2704684.8859 | 1232563.8899 | 2704679.9759 | 1232581.7596
119 | 2704751.4735 | 1232489.0398 | 2704749.2997 | 1232480.4617 | 2704752.2437 | 1232468.1265 | 2704753.8251 | 1232466.0639 | 2704758.2438 | 1232460.2929 | 2704769.1613 | 1232454.9146 | 2704780.2938 | 1232451.9419 | 2704784.2672 | 1232450.8111 | 2704785.8275 | 1232450.3716 | 2704779.7741 | 1232425.5906 | 2704776.9092 | 1232411.9632 | 2704776.1547 | 1232408.3694 | 2704769.2748 | 1232409.8271
120 | 2704769.2748 | 1232409.8271 | 2704736.7398 | 1232417.0592 | 2704722.9399 | 1232418.3949 | 2704711.2867 | 1232418.2451 | 2704686.3907 | 1232418.1647
121 | 2704751.4735 | 1232489.0398 | 2704727.3892 | 1232489.071 | 2704724.0728 | 1232502.3001
122 | 2704719.6893 | 1232460.5806 | 2704747.8369 | 1232460.3429 | 2704753.8251 | 1232466.0639 | 2704752.2437 | 1232468.1265 | 2704749.2997 | 1232480.4617 | 2704751.4735 | 1232489.0398
123 | 2704686.3907 | 1232418.1647 | 2704683.478 | 1232418.1553 | 2704668.7495 | 1232418.7547
124 | 2704724.0728 | 1232502.3001 | 2704722.4729 | 1232508.6821
125 | 2704719.6893 | 1232460.5806 | 2704715.4363 | 1232452.2327 | 2704715.4363 | 1232452.2327
126 | 2704719.6893 | 1232460.5806 | 2704717.5986 | 1232471.4477
127 | 2704715.4363 | 1232452.2327 | 2704716.1501 | 1232449.5542
128 | 2704712.6381 | 1232482.5062 | 2704715.4956 | 1232482.3787 | 2704717.5986 | 1232471.4477
129 | 2704670.8898 | 1232356.7429 | 2704644.6283 | 1232356.08
130 | 2704674.6296 | 1232356.831 | 2704670.8898 | 1232356.7429
131 | 2704670.8898 | 1232356.7429 | 2704666.9616 | 1232370.3506 | 2704665.4972 | 1232375.3137
132 | 2704674.6296 | 1232356.831 | 2704665.122 | 1232389.7734
133 | 2704655.6402 | 1232419.2882 | 2704665.0794 | 1232389.9211 | 2704665.122 | 1232389.7734
134 | 2704600.6373 | 1232533.4618 | 2704608.2982 | 1232521.1873
135 | 2704611.4015 | 1232523.01 | 2704608.2982 | 1232521.1873
136 | 2704608.2982 | 1232521.1873 | 2704618.4715 | 1232504.7206 | 2704618.5127 | 1232504.6358
137 | 2704614.5689 | 1232504.4184 | 2704605.0958 | 1232519.3963 | 2704608.2982 | 1232521.1873
138 | 2704625.3005 | 1232490.6635 | 2704618.5127 | 1232504.6358
139 | 2704614.5689 | 1232504.4184 | 2704619.7526 | 1232494.3353 | 2704622.6412 | 1232487.722
140 | 2704625.3005 | 1232490.6635 | 2704627.8354 | 1232484.7704 | 2704632.9217 | 1232474.1964 | 2704634.4176 | 1232470.7789
141 | 2704643.6936 | 1232439.671 | 2704650.3316 | 1232423.131 | 2704651.4203 | 1232419.9041
142 | 2704643.6936 | 1232439.671 | 2704615.6649 | 1232428.4248
143 | 2704647.2132 | 1232441.0785 | 2704643.6936 | 1232439.671
144 | 2704635.6837 | 1232377.5833 | 2704644.6283 | 1232356.08
145 | 2704647.2132 | 1232441.0785 | 2704651.5504 | 1232430.9027 | 2704655.6402 | 1232419.2882
146 | 2704647.2132 | 1232441.0785 | 2704644.6972 | 1232446.9777
147 | 2704655.6402 | 1232419.2882 | 2704668.7495 | 1232418.7547
148 | 2704644.6972 | 1232446.9777 | 2704643.5793 | 1232449.5987 | 2704641.7839 | 1232453.8119
149 | 2704634.8357 | 1232469.8238 | 2704639.5581 | 1232459.0351 | 2704641.7839 | 1232453.8119
150 | 2704716.1501 | 1232449.5542 | 2704717.9253 | 1232442.8931
151 | 2704721.1897 | 1232513.8011 | 2704722.4729 | 1232508.6821
152 | 2704719.8757 | 1232519.0426 | 2704721.1897 | 1232513.8011
153 | 2704634.8357 | 1232469.8238 | 2704634.4176 | 1232470.7789
154 | 2704644.2141 | 1232502.0459 | 2704647.9094 | 1232504.7387 | 2704653.8139 | 1232510.4519
155 | 2704660.999 | 1232517.4043 | 2704653.8139 | 1232510.4519
156 | 2704661.6738 | 1232523.0282 | 2704663.2195 | 1232519.5528 | 2704660.999 | 1232517.4043
157 | 2704661.6738 | 1232523.0282 | 2704667.1258 | 1232522.2236 | 2704676.3163 | 1232522.43 | 2704676.7728 | 1232525.7516 | 2704679.92 | 1232526.3742 | 2704681.3621 | 1232529.2017
158 | 2704586.779 | 1232753.6284 | 2704567.0439 | 1232749.2204
159 | 2704597.5481 | 1232769.541 | 2704586.779 | 1232753.6284
160 | 2704665.7693 | 1232823.994 | 2704660.8136 | 1232822.3421
161 | 2704665.7693 | 1232823.994 | 2704660.0098 | 1232845.9827
162 | 2704660.8136 | 1232822.3421 | 2704641.0149 | 1232815.7425
163 | 2704659.7043 | 1232847.1492 | 2704660.0098 | 1232845.9827
164 | 2704632.946 | 1232813.0528 | 2704641.0149 | 1232815.7425
165 | 2704617.0831 | 1232819.5452 | 2704629.2544 | 1232816.1119 | 2704632.4164 | 1232812.8763 | 2704632.946 | 1232813.0528
166 | 2704602.2151 | 1232819.3163 | 2704609.0531 | 1232822.7837 | 2704615.3037 | 1232820.0471 | 2704617.0831 | 1232819.5452
167 | 2704585.124 | 1232776.9624 | 2704580.8839 | 1232779.4951
168 | 2704597.5481 | 1232769.541 | 2704585.124 | 1232776.9624
169 | 2704563.0318 | 1232778.8853 | 2704566.7713 | 1232785.0001 | 2704568.5835 | 1232785.7326 | 2704569.5122 | 1232785.8935 | 2704571.0198 | 1232785.4307 | 2704574.457 | 1232783.3341 | 2704580.8839 | 1232779.4951
170 | 2704597.5481 | 1232769.541 | 2704601.7923 | 1232775.8093
171 | 2704627.0998 | 1232699.1499 | 2704624.4061 | 1232695.1427
172 | 2704634.1101 | 1232753.3933 | 2704633.3876 | 1232755.1609 | 2704652.4178 | 1232766.921
173 | 2704717.9253 | 1232442.8931 | 2704719.6685 | 1232436.3524

## bus_geodata
| x | y | coords
0 | 2704563.0228 | 1232370.2326
1 | 2704558.3975 | 1232359.7767
2 | 2704536.5753 | 1232351.3088
3 | 2704512.2191 | 1232405.0766
4 | 2704574.9932 | 1232326.121
5 | 2704579.1932 | 1232350.4021
6 | 2704541.9594 | 1232416.3413
7 | 2704580.7187 | 1232294.2978
8 | 2704591.1027 | 1232329.1404
9 | 2704599.1373 | 1232298.4787
10 | 2704499.0171 | 1232508.9005
11 | 2704415.7216 | 1232659.4059
12 | 2704522.3458 | 1232539.3822
13 | 2704708.9263 | 1232804.3503
14 | 2704700.8605 | 1232809.9569
15 | 2704713.9171 | 1232812.0774
16 | 2704684.251 | 1232767.2559
17 | 2704543.2001 | 1232643.6345
18 | 2704563.0535 | 1232656.8403
19 | 2704545.5411 | 1232613.0304
20 | 2704522.8976 | 1232700.8934
21 | 2704558.6499 | 1232588.9761
22 | 2704563.3878 | 1232596.0314
23 | 2704568.8088 | 1232570.3108
24 | 2704775.991 | 1232927.7252
25 | 2704700.9472 | 1232937.7994
26 | 2704745.865 | 1232876.4379
27 | 2704591.0031 | 1232650.5027
28 | 2704601.0981 | 1232663.846
29 | 2704586.363 | 1232643.3997
30 | 2704725.0495 | 1232829.0313
31 | 2704723.1255 | 1232808.5766
32 | 2704648.9777 | 1232731.6954
33 | 2704659.277 | 1232747.2311
34 | 2704640.4946 | 1232737.7729
35 | 2704639.9936 | 1232718.3308
36 | 2704514.2829 | 1232725.5433
37 | 2704530.1795 | 1232734.58
38 | 2704517.8433 | 1232715.1437
39 | 2704704.5312 | 1232815.6704
40 | 2704728.0637 | 1232849.9905
41 | 2704689.395 | 1232822.8425
42 | 2704577.3088 | 1232607.585
43 | 2704571.1694 | 1232598.4034
44 | 2704572.4708 | 1232622.1331
45 | 2704586.0066 | 1232610.3615
46 | 2704522.6279 | 1232587.6809
47 | 2704497.8452 | 1232740.2656
48 | 2704577.4327 | 1232685.3985
49 | 2704623.5139 | 1232675.9496
50 | 2704610.0873 | 1232674.2235
51 | 2704644.7208 | 1232707.83
52 | 2704634.8977 | 1232551.2003
53 | 2704649.8022 | 1232555.4992
54 | 2704626.4584 | 1232547.027
55 | 2704576.3216 | 1232628.0281
56 | 2704604.0426 | 1232627.8039
57 | 2704609.9885 | 1232595.0728
58 | 2704566.5233 | 1232591.2941
59 | 2704622.1727 | 1232266.1837
60 | 2704696.5132 | 1232278.8687
61 | 2704626.2519 | 1232288.8288
62 | 2704541.4053 | 1232858.3538
63 | 2704541.9645 | 1232856.2731
64 | 2704574.2906 | 1232864.6258
65 | 2704583.504 | 1232914.2587
66 | 2704628.4638 | 1232880.3465
67 | 2704589.5391 | 1232894.8685
68 | 2704529.4441 | 1232782.375
69 | 2704562.043 | 1232798.9163
70 | 2704524.9102 | 1232795.8102
71 | 2704419.6735 | 1232663.7897
72 | 2704632.5605 | 1232639.17
73 | 2704632.0839 | 1232640.8628
74 | 2704667.8191 | 1232626.0029
75 | 2704671.9318 | 1232611.0353
76 | 2704677.2936 | 1232333.9851
77 | 2704618.4692 | 1232304.8811
78 | 2704671.0696 | 1232747.4402
79 | 2704576.9494 | 1232561.1611
80 | 2704701.7447 | 1232930.3634
81 | 2704681.4618 | 1232935.2321
82 | 2704667.0034 | 1232940.4815
83 | 2704616.7391 | 1232941.0173
84 | 2704687.2622 | 1232894.4368
85 | 2704633.9317 | 1232879.4754
86 | 2704623.5618 | 1232876.6018
87 | 2704732.4185 | 1232856.3415
88 | 2704737.5624 | 1232848.0874
89 | 2704737.3691 | 1232803.1616
90 | 2704637.8311 | 1232744.2894
91 | 2704627.9802 | 1232700.4596
92 | 2704565.5722 | 1232748.8917
93 | 2704680.854 | 1232852.837
94 | 2704687.895 | 1232823.022
95 | 2704487.8992 | 1232751.6616
96 | 2704575.8476 | 1232690.0907
97 | 2704613.8827 | 1232679.4881
98 | 2704662.5483 | 1232558.5476
99 | 2704654.9883 | 1232541.3143
100 | 2704613.6799 | 1232540.7079
101 | 2704742.3679 | 1232855.4058
102 | 2704618.5909 | 1232582.6592
103 | 2704592.4191 | 1232581.8337
104 | 2704574.7892 | 1232862.5441
105 | 2704586.0725 | 1232867.7354
106 | 2704556.8041 | 1232810.8665
107 | 2704594.6866 | 1232815.492
108 | 2704679.9759 | 1232581.7596
109 | 2704769.2748 | 1232409.8271
110 | 2704751.4735 | 1232489.0398
111 | 2704686.3907 | 1232418.1647
112 | 2704724.0728 | 1232502.3001
113 | 2704719.6893 | 1232460.5806
114 | 2704715.4363 | 1232452.2327
115 | 2704717.5986 | 1232471.4477
116 | 2704684.8859 | 1232563.8899
117 | 2704670.8898 | 1232356.7429
118 | 2704674.6296 | 1232356.831
119 | 2704665.122 | 1232389.7734
120 | 2704600.6373 | 1232533.4618
121 | 2704608.2982 | 1232521.1873
122 | 2704611.4015 | 1232523.01
123 | 2704618.5127 | 1232504.6358
124 | 2704614.5689 | 1232504.4184
125 | 2704625.3005 | 1232490.6635
126 | 2704622.6412 | 1232487.722
127 | 2704665.4972 | 1232375.3137
128 | 2704651.4203 | 1232419.9041
129 | 2704643.6936 | 1232439.671
130 | 2704644.6283 | 1232356.08
131 | 2704615.6649 | 1232428.4248
132 | 2704647.2132 | 1232441.0785
133 | 2704635.6837 | 1232377.5833
134 | 2704655.6402 | 1232419.2882
135 | 2704644.6972 | 1232446.9777
136 | 2704668.7495 | 1232418.7547
137 | 2704641.7839 | 1232453.8119
138 | 2704716.1501 | 1232449.5542
139 | 2704712.6381 | 1232482.5062
140 | 2704722.4729 | 1232508.6821
141 | 2704719.8757 | 1232519.0426
142 | 2704721.1897 | 1232513.8011
143 | 2704634.8357 | 1232469.8238
144 | 2704634.4176 | 1232470.7789
145 | 2704644.2141 | 1232502.0459
146 | 2704653.8139 | 1232510.4519
147 | 2704660.999 | 1232517.4043
148 | 2704661.6738 | 1232523.0282
149 | 2704681.3621 | 1232529.2017
150 | 2704567.0439 | 1232749.2204
151 | 2704586.779 | 1232753.6284
152 | 2704720.6478 | 1232775.1819
153 | 2704665.7693 | 1232823.994
154 | 2704660.8136 | 1232822.3421
155 | 2704660.0098 | 1232845.9827
156 | 2704641.0149 | 1232815.7425
157 | 2704659.7043 | 1232847.1492
158 | 2704632.946 | 1232813.0528
159 | 2704617.0831 | 1232819.5452
160 | 2704585.124 | 1232776.9624
161 | 2704580.8839 | 1232779.4951
162 | 2704597.5481 | 1232769.541
163 | 2704563.0318 | 1232778.8853
164 | 2704601.7923 | 1232775.8093
165 | 2704624.4061 | 1232695.1427
166 | 2704627.0998 | 1232699.1499
167 | 2704575.3294 | 1232691.6247
168 | 2704602.2151 | 1232819.3163
169 | 2704652.4178 | 1232766.921
170 | 2704634.1101 | 1232753.3933
171 | 2704589.6375 | 1232826.1223
172 | 2704632.8786 | 1232871.7622
173 | 2704717.9253 | 1232442.8931
174 | 2704719.6685 | 1232436.3524
175 | 2704599.7741 | 1232640.1159

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1