## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3340-35_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3340-35_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3340-35_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3340-35_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_3340-35_0_4_node_92 | 0.4 | n |  | TRUE
5 | bus_LV_3340-35_0_4_node_37 | 0.4 | n |  | TRUE
6 | bus_LV_3340-35_0_4_node_60 | 0.4 | n |  | TRUE
7 | bus_LV_3340-35_0_4_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_3340-35_0_4_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_3340-35_0_4_node_95 | 0.4 | n |  | TRUE
10 | bus_LV_3340-35_0_4_node_86 | 0.4 | n |  | TRUE
11 | bus_LV_3340-35_0_4_node_47 | 0.4 | n |  | TRUE
12 | bus_LV_3340-35_0_4_node_87 | 0.4 | n |  | TRUE
13 | bus_LV_3340-35_0_4_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_3340-35_0_4_node_53 | 0.4 | n |  | TRUE
15 | bus_LV_3340-35_0_4_node_61 | 0.4 | n |  | TRUE
16 | bus_LV_3340-35_0_4_node_50 | 0.4 | n |  | TRUE
17 | bus_LV_3340-35_0_4_node_51 | 0.4 | n |  | TRUE
18 | bus_LV_3340-35_0_4_node_49 | 0.4 | n |  | TRUE
19 | bus_LV_3340-35_0_4_node_5 | 0.4 | n |  | TRUE
20 | bus_LV_3340-35_0_4_node_6 | 0.4 | n |  | TRUE
21 | bus_LV_3340-35_0_4_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_3340-35_0_4_node_8 | 0.4 | n |  | TRUE
23 | bus_LV_3340-35_0_4_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_3340-35_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_3340-35_0_4_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_3340-35_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_3340-35_0_4_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_3340-35_0_4_node_10 | 0.4 | n |  | TRUE
29 | bus_LV_3340-35_0_4_node_11 | 0.4 | n |  | TRUE
30 | bus_LV_3340-35_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_3340-35_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_3340-35_0_4_node_90 | 0.4 | n |  | TRUE
33 | bus_LV_3340-35_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_3340-35_0_4_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_3340-35_0_4_node_42 | 0.4 | n |  | TRUE
36 | bus_LV_3340-35_0_4_node_14 | 0.4 | n |  | TRUE
37 | bus_LV_3340-35_0_4_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_3340-35_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_3340-35_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_3340-35_0_4_node_39 | 0.4 | n |  | TRUE
41 | bus_LV_3340-35_0_4_node_16 | 0.4 | n |  | TRUE
42 | bus_LV_3340-35_0_4_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_3340-35_0_4_node_18 | 0.4 | n |  | TRUE
44 | bus_LV_3340-35_0_4_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_3340-35_0_4_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_3340-35_0_4_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_3340-35_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_3340-35_0_4_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_3340-35_0_4_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_3340-35_0_4_node_28 | 0.4 | n |  | TRUE
51 | bus_LV_3340-35_0_4_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_3340-35_0_4_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_3340-35_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_3340-35_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_3340-35_0_4_node_85 | 0.4 | n |  | TRUE
56 | bus_LV_3340-35_0_4_node_89 | 0.4 | n |  | TRUE
57 | bus_LV_3340-35_0_4_node_40 | 0.4 | n |  | TRUE
58 | bus_LV_3340-35_0_4_node_41 | 0.4 | n |  | TRUE
59 | bus_LV_3340-35_0_4_node_91 | 0.4 | n |  | TRUE
60 | bus_LV_3340-35_0_4_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_3340-35_0_4_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_3340-35_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_3340-35_0_4_node_81 | 0.4 | n |  | TRUE
64 | bus_LV_3340-35_0_4_node_84 | 0.4 | n |  | TRUE
65 | bus_LV_3340-35_0_4_node_54 | 0.4 | n |  | TRUE
66 | bus_LV_3340-35_0_4_node_55 | 0.4 | n |  | TRUE
67 | bus_LV_3340-35_0_4_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_3340-35_0_4_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_3340-35_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_3340-35_0_4_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_3340-35_0_4_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_3340-35_0_4_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_3340-35_0_4_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_3340-35_0_4_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_3340-35_0_4_node_98 | 0.4 | n |  | TRUE
76 | bus_LV_3340-35_0_4_node_96 | 0.4 | n |  | TRUE
77 | bus_LV_3340-35_0_4_node_80 | 0.4 | n |  | TRUE
78 | bus_LV_3340-35_0_4_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_3340-35_0_4_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_3340-35_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_3340-35_0_4_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_3340-35_0_4_node_66 | 0.4 | n |  | TRUE
83 | bus_LV_3340-35_0_4_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_3340-35_0_4_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_3340-35_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_3340-35_0_4_node_97 | 0.4 | n |  | TRUE
87 | bus_LV_3340-35_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_3340-35_0_4_node_94 | 0.4 | n |  | TRUE
89 | bus_LV_3340-35_0_4_node_73 | 0.4 | n |  | TRUE
90 | bus_LV_3340-35_0_4_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_3340-35_0_4_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_3340-35_0_4_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_3340-35_0_4_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_3340-35_0_4_node_79 | 0.4 | n |  | TRUE
95 | bus_MV_585_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3340-35_0_4_load_0 | 0 | 0.011498 | 0.0028816 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3340-35_0_4_load_92 | 4 | 0.0040609 | 0.0010178 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3340-35_0_4_load_60 | 6 | 0.011462 | 0.0028726 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3340-35_0_4_load_36 | 7 | 0.0055759 | 0.0013975 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3340-35_0_4_load_95 | 9 | 0.011327 | 0.0028389 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3340-35_0_4_load_87 | 12 | 0.002626 | 0.00065815 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3340-35_0_4_load_51 | 17 | 0.00020511 | 5.1405e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3340-35_0_4_load_5 | 19 | 0.0081568 | 0.0020443 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3340-35_0_4_load_6 | 20 | 0.0076186 | 0.0019094 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3340-35_0_4_load_8 | 22 | 0.0019875 | 0.00049812 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3340-35_0_4_load_15 | 27 | 0.0073558 | 0.0018435 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3340-35_0_4_load_35 | 31 | 0.010703 | 0.0026823 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3340-35_0_4_load_90 | 32 | 0.012847 | 0.0032198 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3340-35_0_4_load_25 | 33 | 0.0044071 | 0.0011045 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3340-35_0_4_load_38 | 34 | 0.012996 | 0.0032571 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3340-35_0_4_load_42 | 35 | 0.0076102 | 0.0019073 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3340-35_0_4_load_14 | 36 | 0.007612 | 0.0019078 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3340-35_0_4_load_19 | 37 | 0.0081751 | 0.0020489 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3340-35_0_4_load_24 | 39 | 0.0033542 | 0.00084064 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3340-35_0_4_load_16 | 41 | 0.0033774 | 0.00084647 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3340-35_0_4_load_43 | 42 | 0.0081139 | 0.0020335 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3340-35_0_4_load_18 | 43 | 0.0090527 | 0.0022688 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3340-35_0_4_load_22 | 45 | 0.0094602 | 0.0023709 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3340-35_0_4_load_29 | 47 | 0.0053491 | 0.0013406 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3340-35_0_4_load_26 | 49 | 0.006454 | 0.0016175 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3340-35_0_4_load_30 | 51 | 0.011349 | 0.0028442 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3340-35_0_4_load_85 | 55 | 0.011051 | 0.0027697 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3340-35_0_4_load_89 | 56 | 0.0088925 | 0.0022287 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3340-35_0_4_load_40 | 57 | 0.0036955 | 0.00092618 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3340-35_0_4_load_91 | 59 | 0.005207 | 0.001305 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3340-35_0_4_load_44 | 60 | 0.013677 | 0.0034278 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3340-35_0_4_load_46 | 61 | 0.0016421 | 0.00041155 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3340-35_0_4_load_48 | 62 | 0.00025116 | 6.2946e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3340-35_0_4_load_84 | 64 | 0.0078368 | 0.0019641 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3340-35_0_4_load_54 | 65 | 0.0034799 | 0.00087215 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3340-35_0_4_load_55 | 66 | 0.0054947 | 0.0013771 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3340-35_0_4_load_58 | 69 | 0.0024805 | 0.00062166 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3340-35_0_4_load_71 | 70 | 0.0013829 | 0.00034658 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3340-35_0_4_load_67 | 72 | 0.0046795 | 0.0011728 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3340-35_0_4_load_98 | 75 | 0.011752 | 0.0029454 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3340-35_0_4_load_96 | 76 | 0.0072955 | 0.0018284 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3340-35_0_4_load_62 | 78 | 0.0014425 | 0.00036152 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3340-35_0_4_load_63 | 79 | 0.0025335 | 0.00063496 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3340-35_0_4_load_64 | 80 | 0.0018036 | 0.00045202 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3340-35_0_4_load_75 | 85 | 0.0054619 | 0.0013689 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3340-35_0_4_load_97 | 86 | 0.011646 | 0.0029188 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3340-35_0_4_load_74 | 87 | 0.0022895 | 0.0005738 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3340-35_0_4_load_94 | 88 | 0.0014241 | 0.00035692 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3340-35_0_4_load_93 | 90 | 0.0014722 | 0.00036897 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3340-35_0_4_load_76 | 91 | 0.0032494 | 0.00081438 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3340-35_0_4_load_77 | 92 | 0.0040557 | 0.0010164 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3340-35_0_4_load_78 | 93 | 0.0035979 | 0.00090171 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3340-35_0_4_load_79 | 94 | 0.0046005 | 0.001153 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 34 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3340-35_0_4_line_0 |  | 0 | 1 | 0.015443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3340-35_0_4_line_1 |  | 1 | 2 | 0.046339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_3340-35_0_4_line_2 |  | 1 | 3 | 0.028843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_3340-35_0_4_line_3 |  | 2 | 4 | 0.020237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3340-35_0_4_line_4 |  | 2 | 5 | 0.012661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_3340-35_0_4_line_5 |  | 3 | 6 | 0.075954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_3340-35_0_4_line_6 |  | 5 | 7 | 0.0067349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_3340-35_0_4_line_7 |  | 6 | 14 | 0.036158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_3340-35_0_4_line_8 |  | 7 | 50 | 0.021086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_3340-35_0_4_line_9 |  | 8 | 9 | 0.038824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3340-35_0_4_line_10 |  | 8 | 10 | 0.009314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3340-35_0_4_line_11 |  | 10 | 55 | 0.025938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3340-35_0_4_line_12 |  | 11 | 12 | 0.012978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3340-35_0_4_line_13 |  | 11 | 13 | 0.009152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3340-35_0_4_line_14 |  | 13 | 60 | 0.022518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3340-35_0_4_line_15 |  | 13 | 58 | 0.003886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3340-35_0_4_line_16 |  | 14 | 15 | 0.01799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_3340-35_0_4_line_17 |  | 14 | 16 | 0.009214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3340-35_0_4_line_18 |  | 15 | 63 | 0.038242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_3340-35_0_4_line_19 |  | 15 | 64 | 0.025336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3340-35_0_4_line_20 |  | 16 | 17 | 0.036072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3340-35_0_4_line_21 |  | 16 | 18 | 0.045566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3340-35_0_4_line_22 |  | 18 | 62 | 0.0088509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3340-35_0_4_line_23 |  | 19 | 20 | 0.016974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3340-35_0_4_line_24 |  | 19 | 21 | 0.018176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3340-35_0_4_line_25 |  | 20 | 22 | 0.0045828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3340-35_0_4_line_26 |  | 21 | 23 | 0.034327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3340-35_0_4_line_27 |  | 21 | 24 | 0.034133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_3340-35_0_4_line_28 |  | 21 | 25 | 0.029388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_3340-35_0_4_line_29 |  | 23 | 26 | 0.034875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3340-35_0_4_line_30 |  | 23 | 27 | 0.017917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3340-35_0_4_line_31 |  | 24 | 30 | 0.033574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_3340-35_0_4_line_32 |  | 24 | 33 | 0.012161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3340-35_0_4_line_33 |  | 25 | 34 | 0.018637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_3340-35_0_4_line_34 |  | 26 | 35 | 0.016672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3340-35_0_4_line_35 |  | 27 | 36 | 0.017403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3340-35_0_4_line_36 |  | 28 | 29 | 0.037005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3340-35_0_4_line_37 |  | 28 | 30 | 0.003464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3340-35_0_4_line_38 |  | 28 | 31 | 0.020306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3340-35_0_4_line_39 |  | 29 | 32 | 0.000393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3340-35_0_4_line_40 |  | 30 | 37 | 0.020614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_3340-35_0_4_line_41 |  | 31 | 38 | 0.0030009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3340-35_0_4_line_42 |  | 33 | 39 | 0.025556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3340-35_0_4_line_43 |  | 34 | 40 | 0.018793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3340-35_0_4_line_44 |  | 35 | 42 | 0.017935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3340-35_0_4_line_45 |  | 36 | 41 | 0.0039031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3340-35_0_4_line_46 |  | 37 | 43 | 0.031168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_3340-35_0_4_line_47 |  | 38 | 52 | 0.044434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3340-35_0_4_line_48 |  | 40 | 57 | 0.018421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3340-35_0_4_line_49 |  | 40 | 58 | 0.022781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3340-35_0_4_line_50 |  | 43 | 44 | 0.0084066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_3340-35_0_4_line_51 |  | 44 | 45 | 0.044283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3340-35_0_4_line_52 |  | 44 | 46 | 0.011657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_3340-35_0_4_line_53 |  | 46 | 47 | 0.01261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_3340-35_0_4_line_54 |  | 47 | 48 | 0.011006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_3340-35_0_4_line_55 |  | 48 | 50 | 0.004344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_3340-35_0_4_line_56 |  | 48 | 49 | 0.043206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3340-35_0_4_line_57 |  | 51 | 52 | 0.050194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3340-35_0_4_line_58 |  | 51 | 53 | 0.005061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3340-35_0_4_line_59 |  | 53 | 54 | 0.026164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3340-35_0_4_line_60 |  | 54 | 55 | 0.017114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3340-35_0_4_line_61 |  | 55 | 56 | 0.043203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3340-35_0_4_line_62 |  | 58 | 59 | 0.019349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3340-35_0_4_line_63 |  | 60 | 61 | 0.047234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3340-35_0_4_line_64 |  | 63 | 74 | 0.011957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_3340-35_0_4_line_65 |  | 63 | 75 | 0.005622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3340-35_0_4_line_66 |  | 65 | 66 | 0.025676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3340-35_0_4_line_67 |  | 66 | 67 | 0.010732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3340-35_0_4_line_68 |  | 67 | 68 | 0.018233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3340-35_0_4_line_69 |  | 68 | 71 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3340-35_0_4_line_70 |  | 68 | 72 | 0.002559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3340-35_0_4_line_71 |  | 69 | 70 | 0.0098103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3340-35_0_4_line_72 |  | 70 | 73 | 0.029589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3340-35_0_4_line_73 |  | 71 | 88 | 0.007535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3340-35_0_4_line_74 |  | 71 | 89 | 0.006415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3340-35_0_4_line_75 |  | 72 | 83 | 0.040005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3340-35_0_4_line_76 |  | 73 | 89 | 0.020298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3340-35_0_4_line_77 |  | 74 | 76 | 0.011236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3340-35_0_4_line_78 |  | 74 | 77 | 0.032569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_3340-35_0_4_line_79 |  | 77 | 84 | 0.0092101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_3340-35_0_4_line_80 |  | 77 | 94 | 0.018286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3340-35_0_4_line_81 |  | 78 | 79 | 0.02702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3340-35_0_4_line_82 |  | 78 | 80 | 0.00061712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3340-35_0_4_line_83 |  | 79 | 81 | 0.014046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3340-35_0_4_line_84 |  | 80 | 82 | 0.048926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3340-35_0_4_line_85 |  | 81 | 83 | 0.039008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3340-35_0_4_line_86 |  | 82 | 84 | 0.030432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3340-35_0_4_line_87 |  | 82 | 85 | 0.019478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3340-35_0_4_line_88 |  | 84 | 86 | 0.008605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3340-35_0_4_line_89 |  | 85 | 87 | 0.00027615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3340-35_0_4_line_90 |  | 87 | 91 | 0.01852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3340-35_0_4_line_91 |  | 89 | 90 | 0.006804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3340-35_0_4_line_92 |  | 92 | 93 | 0.0088266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3340-35_0_4_line_93 |  | 93 | 94 | 0.008738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3340-35_0_4_trafo_38 | 0.63 MVA 20/0.4 kV | 95 | 34 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2705238.0192 | 1231526.1842 | 2705249.6744 | 1231536.3159
1 | 2705228.5517 | 1231561.1986 | 2705218.1376 | 1231548.3046 | 2705224.5161 | 1231541.857 | 2705230.8887 | 1231534.8868 | 2705238.0192 | 1231526.1842
2 | 2705238.0192 | 1231526.1842 | 2705236.6838 | 1231525.0264 | 2705242.9904 | 1231515.3752 | 2705250.2031 | 1231501.6036
3 | 2705239.3688 | 1231547.0683 | 2705241.2193 | 1231548.6467 | 2705228.5517 | 1231561.1986
4 | 2705237.6368 | 1231570.0105 | 2705230.6213 | 1231563.6704 | 2705228.5517 | 1231561.1986
5 | 2705250.2031 | 1231501.6036 | 2705255.9807 | 1231491.4538 | 2705265.1146 | 1231474.4249 | 2705272.059 | 1231461.2712 | 2705282.8567 | 1231440.9805 | 2705286.1913 | 1231434.7212
6 | 2705237.6368 | 1231570.0105 | 2705242.8123 | 1231574.3201
7 | 2705303.5127 | 1231402.9843 | 2705293.9832 | 1231420.0951 | 2705286.1913 | 1231434.7212
8 | 2705260.7258 | 1231585.3307 | 2705251.981 | 1231580.8281 | 2705244.2131 | 1231575.4865 | 2705242.8123 | 1231574.3201
9 | 2705213.2645 | 1231636.5626 | 2705232.7958 | 1231602.983
10 | 2705213.2645 | 1231636.5626 | 2705221.0821 | 1231641.6603
11 | 2705221.0821 | 1231641.6603 | 2705227.8635 | 1231645.8168 | 2705241.9895 | 1231651.8381 | 2705244.5123 | 1231652.574
12 | 2705295.8724 | 1231516.946 | 2705291.4972 | 1231529.1666
13 | 2705295.8724 | 1231516.946 | 2705300.5614 | 1231518.6414 | 2705302.7442 | 1231519.4251 | 2705304.4354 | 1231520.1667
14 | 2705304.4354 | 1231520.1667 | 2705306.894 | 1231513.0827 | 2705307.9653 | 1231513.3241 | 2705312.5056 | 1231500.1635
15 | 2705304.4354 | 1231520.1667 | 2705307.9979 | 1231521.7421
16 | 2705303.5127 | 1231402.9843 | 2705310.4165 | 1231402.3839 | 2705321.4768 | 1231402.3353
17 | 2705294.3393 | 1231403.8447 | 2705298.6574 | 1231403.3986 | 2705303.5127 | 1231402.9843
18 | 2705321.4768 | 1231402.3353 | 2705342.6349 | 1231423.1925 | 2705346.3098 | 1231427.4052 | 2705345.7133 | 1231430.2857
19 | 2705321.4768 | 1231402.3353 | 2705343.8861 | 1231390.5147
20 | 2705294.3393 | 1231403.8447 | 2705280.3446 | 1231430.1389 | 2705277.3812 | 1231435.6819
21 | 2705294.3393 | 1231403.8447 | 2705284.1475 | 1231404.8984 | 2705249.4472 | 1231412.145
22 | 2705249.4472 | 1231412.145 | 2705240.7828 | 1231413.9526
23 | 2705404.2301 | 1231532.2708 | 2705396.1087 | 1231547.1758
24 | 2705387.4124 | 1231563.1359 | 2705396.1087 | 1231547.1758
25 | 2705406.4228 | 1231528.2466 | 2705404.2301 | 1231532.2708
26 | 2705387.4124 | 1231563.1359 | 2705416.0709 | 1231582.1583
27 | 2705371.3527 | 1231582.8551 | 2705377.6117 | 1231572.9029 | 2705381.0793 | 1231567.438 | 2705381.4062 | 1231565.6647 | 2705380.8998 | 1231559.1953 | 2705387.4124 | 1231563.1359
28 | 2705362.2612 | 1231547.9343 | 2705380.8998 | 1231559.1953 | 2705387.4124 | 1231563.1359
29 | 2705416.0709 | 1231582.1583 | 2705421.2924 | 1231586.2873 | 2705443.4333 | 1231603.782
30 | 2705416.0709 | 1231582.1583 | 2705425.4865 | 1231566.9147
31 | 2705356.5933 | 1231612.9718 | 2705358.8625 | 1231607.5968 | 2705362.1215 | 1231599.8042 | 2705366.2263 | 1231591.7264 | 2705371.3527 | 1231582.8551
32 | 2705371.3527 | 1231582.8551 | 2705363.0729 | 1231578.1937 | 2705360.6375 | 1231577.1262
33 | 2705362.2612 | 1231547.9343 | 2705345.7015 | 1231539.3835
34 | 2705443.4333 | 1231603.782 | 2705453.2241 | 1231590.2877
35 | 2705434.6319 | 1231552.1083 | 2705425.4865 | 1231566.9147
36 | 2705359.9561 | 1231613.8431 | 2705368.5467 | 1231595.4259 | 2705369.9452 | 1231593.0267 | 2705383.8488 | 1231592.7951
37 | 2705356.5933 | 1231612.9718 | 2705359.9561 | 1231613.8431
38 | 2705359.9561 | 1231613.8431 | 2705353.0577 | 1231632.9414
39 | 2705384.2428 | 1231592.791 | 2705383.8488 | 1231592.7951
40 | 2705356.5933 | 1231612.9718 | 2705336.6335 | 1231607.8194
41 | 2705352.0382 | 1231635.7638 | 2705353.0577 | 1231632.9414
42 | 2705341.213 | 1231568.8358 | 2705345.7108 | 1231570.9806 | 2705344.8683 | 1231573.2118 | 2705353.7137 | 1231577.1604 | 2705355.5115 | 1231574.8794 | 2705360.6375 | 1231577.1262
43 | 2705328.782 | 1231531.2063 | 2705343.8414 | 1231538.423 | 2705345.7015 | 1231539.3835
44 | 2705453.2241 | 1231590.2877 | 2705463.7566 | 1231575.7712
45 | 2705436.6831 | 1231548.7875 | 2705434.6319 | 1231552.1083
46 | 2705306.4552 | 1231600.0292 | 2705336.6335 | 1231607.8194
47 | 2705352.0382 | 1231635.7638 | 2705339.5867 | 1231678.4198
48 | 2705328.782 | 1231531.2063 | 2705322.4457 | 1231548.5071
49 | 2705307.9979 | 1231521.7421 | 2705328.782 | 1231531.2063
50 | 2705298.3154 | 1231597.928 | 2705306.4552 | 1231600.0292
51 | 2705298.3154 | 1231597.928 | 2705291.4195 | 1231625.4489 | 2705304.1501 | 1231628.9992 | 2705304.9538 | 1231626.3893
52 | 2705287.1189 | 1231594.5717 | 2705298.3154 | 1231597.928
53 | 2705287.1189 | 1231594.5717 | 2705277.6657 | 1231591.5798 | 2705275.1377 | 1231590.6471
54 | 2705264.8121 | 1231586.8375 | 2705275.1377 | 1231590.6471
55 | 2705264.8121 | 1231586.8375 | 2705260.7258 | 1231585.3307
56 | 2705264.8121 | 1231586.8375 | 2705257.494 | 1231603.1425 | 2705257.8943 | 1231608.7649 | 2705256.025 | 1231614.6585 | 2705268.9593 | 1231618.5742
57 | 2705339.5867 | 1231678.4198 | 2705291.0049 | 1231665.801
58 | 2705286.1064 | 1231664.5287 | 2705291.0049 | 1231665.801
59 | 2705260.9417 | 1231657.3666 | 2705281.2601 | 1231663.1641 | 2705286.1064 | 1231664.5287
60 | 2705260.9417 | 1231657.3666 | 2705244.5123 | 1231652.574
61 | 2705244.5123 | 1231652.574 | 2705228.2017 | 1231692.5803
62 | 2705307.9979 | 1231521.7421 | 2705301.5767 | 1231539.9977
63 | 2705298.2199 | 1231475.523 | 2705299.3561 | 1231472.1072 | 2705311.7498 | 1231476.3076 | 2705310.6164 | 1231479.5678 | 2705313.1388 | 1231480.4242 | 2705312.6266 | 1231481.9719 | 2705318.0425 | 1231484.1139 | 2705312.5056 | 1231500.1635
64 | 2705354.2874 | 1231431.6053 | 2705346.3098 | 1231427.4052 | 2705345.7133 | 1231430.2857
65 | 2705344.5779 | 1231435.792 | 2705345.7133 | 1231430.2857
66 | 2705422.5063 | 1231426.9757 | 2705447.0805 | 1231434.4158
67 | 2705457.3524 | 1231437.5258 | 2705447.0805 | 1231434.4158
68 | 2705457.3524 | 1231437.5258 | 2705474.9276 | 1231442.5635
69 | 2705474.9276 | 1231442.5635 | 2705479.3897 | 1231430.5892 | 2705478.8935 | 1231425.6878
70 | 2705474.9276 | 1231442.5635 | 2705477.1472 | 1231443.8372
71 | 2705443.6417 | 1231408.1381 | 2705434.0771 | 1231410.3204
72 | 2705472.4893 | 1231401.556 | 2705443.6417 | 1231408.1381
73 | 2705471.3487 | 1231426.121 | 2705478.8935 | 1231425.6878
74 | 2705478.8935 | 1231425.6878 | 2705478.0139 | 1231419.3341
75 | 2705513.5845 | 1231460.3517 | 2705477.1472 | 1231443.8372
76 | 2705472.4893 | 1231401.556 | 2705476.6895 | 1231403.9101 | 2705477.4706 | 1231411.5408 | 2705478.0139 | 1231419.3341
77 | 2705359.4563 | 1231421.6227 | 2705354.2874 | 1231431.6053
78 | 2705354.2874 | 1231431.6053 | 2705361.7244 | 1231435.5401 | 2705367.9752 | 1231438.4419 | 2705381.1274 | 1231443.4454 | 2705379.9311 | 1231446.4042
79 | 2705386.7794 | 1231445.5138 | 2705381.1274 | 1231443.4454 | 2705379.9311 | 1231446.4042
80 | 2705379.9311 | 1231446.4042 | 2705373.37 | 1231463.473
81 | 2705461.3413 | 1231474.6459 | 2705471.8075 | 1231478.7911 | 2705485.5336 | 1231486.5414
82 | 2705460.7675 | 1231474.4187 | 2705461.3413 | 1231474.6459
83 | 2705497.7559 | 1231493.4625 | 2705497.2838 | 1231493.1761 | 2705485.5336 | 1231486.5414
84 | 2705415.137 | 1231456.7695 | 2705439.9745 | 1231466.1836 | 2705460.7675 | 1231474.4187
85 | 2705497.7559 | 1231493.4625 | 2705499.9721 | 1231488.0977 | 2705503.1569 | 1231479.8036 | 2705503.3455 | 1231478.9952 | 2705504.1064 | 1231475.8174 | 2705505.0808 | 1231470.8532 | 2705509.7999 | 1231470.0029 | 2705513.5845 | 1231460.3517
86 | 2705386.7794 | 1231445.5138 | 2705415.137 | 1231456.7695
87 | 2705415.137 | 1231456.7695 | 2705408.4906 | 1231475.0784
88 | 2705389.6578 | 1231437.4032 | 2705386.7794 | 1231445.5138
89 | 2705408.3964 | 1231475.338 | 2705408.4906 | 1231475.0784
90 | 2705415.7107 | 1231485.9127 | 2705405.6597 | 1231482.8767 | 2705408.3964 | 1231475.338
91 | 2705471.1982 | 1231419.669 | 2705478.0139 | 1231419.3341
92 | 2705378.5883 | 1231474.4802 | 2705370.2348 | 1231471.6292 | 2705370.2348 | 1231471.6292
93 | 2705373.37 | 1231463.473 | 2705370.2348 | 1231471.6292

## bus_geodata
| x | y | coords
0 | 2705249.6744 | 1231536.3159
1 | 2705238.0192 | 1231526.1842
2 | 2705228.5517 | 1231561.1986
3 | 2705250.2031 | 1231501.6036
4 | 2705239.3688 | 1231547.0683
5 | 2705237.6368 | 1231570.0105
6 | 2705286.1913 | 1231434.7212
7 | 2705242.8123 | 1231574.3201
8 | 2705213.2644 | 1231636.5626
9 | 2705232.7958 | 1231602.983
10 | 2705221.0821 | 1231641.6603
11 | 2705295.8724 | 1231516.946
12 | 2705291.4972 | 1231529.1666
13 | 2705304.4354 | 1231520.1667
14 | 2705303.5127 | 1231402.9843
15 | 2705321.4768 | 1231402.3353
16 | 2705294.3393 | 1231403.8447
17 | 2705277.3812 | 1231435.6819
18 | 2705249.4472 | 1231412.145
19 | 2705396.1087 | 1231547.1758
20 | 2705404.2301 | 1231532.2708
21 | 2705387.4124 | 1231563.1359
22 | 2705406.4228 | 1231528.2466
23 | 2705416.0709 | 1231582.1583
24 | 2705371.3527 | 1231582.8551
25 | 2705362.2612 | 1231547.9343
26 | 2705443.4333 | 1231603.782
27 | 2705425.4865 | 1231566.9147
28 | 2705359.9561 | 1231613.8431
29 | 2705383.8488 | 1231592.7951
30 | 2705356.5933 | 1231612.9718
31 | 2705353.0577 | 1231632.9414
32 | 2705384.2428 | 1231592.791
33 | 2705360.6375 | 1231577.1262
34 | 2705345.7015 | 1231539.3835
35 | 2705453.2241 | 1231590.2877
36 | 2705434.6319 | 1231552.1083
37 | 2705336.6335 | 1231607.8194
38 | 2705352.0382 | 1231635.7638
39 | 2705341.213 | 1231568.8358
40 | 2705328.782 | 1231531.2063
41 | 2705436.6831 | 1231548.7875
42 | 2705463.7566 | 1231575.7712
43 | 2705306.4552 | 1231600.0292
44 | 2705298.3154 | 1231597.928
45 | 2705304.9538 | 1231626.3893
46 | 2705287.1189 | 1231594.5717
47 | 2705275.1377 | 1231590.6471
48 | 2705264.8121 | 1231586.8375
49 | 2705268.9593 | 1231618.5742
50 | 2705260.7258 | 1231585.3307
51 | 2705291.0049 | 1231665.801
52 | 2705339.5867 | 1231678.4198
53 | 2705286.1064 | 1231664.5287
54 | 2705260.9417 | 1231657.3666
55 | 2705244.5123 | 1231652.574
56 | 2705228.2017 | 1231692.5803
57 | 2705322.4457 | 1231548.5071
58 | 2705307.9979 | 1231521.7421
59 | 2705301.5767 | 1231539.9977
60 | 2705312.5056 | 1231500.1635
61 | 2705298.2199 | 1231475.523
62 | 2705240.7828 | 1231413.9526
63 | 2705345.7133 | 1231430.2857
64 | 2705343.8861 | 1231390.5147
65 | 2705422.5063 | 1231426.9757
66 | 2705447.0805 | 1231434.4158
67 | 2705457.3524 | 1231437.5258
68 | 2705474.9276 | 1231442.5635
69 | 2705434.0771 | 1231410.3204
70 | 2705443.6417 | 1231408.1381
71 | 2705478.8935 | 1231425.6878
72 | 2705477.1472 | 1231443.8372
73 | 2705472.4893 | 1231401.556
74 | 2705354.2874 | 1231431.6053
75 | 2705344.5779 | 1231435.792
76 | 2705359.4563 | 1231421.6227
77 | 2705379.9311 | 1231446.4042
78 | 2705461.3413 | 1231474.6459
79 | 2705485.5336 | 1231486.5414
80 | 2705460.7675 | 1231474.4187
81 | 2705497.7559 | 1231493.4625
82 | 2705415.137 | 1231456.7695
83 | 2705513.5845 | 1231460.3517
84 | 2705386.7794 | 1231445.5138
85 | 2705408.4906 | 1231475.0784
86 | 2705389.6578 | 1231437.4032
87 | 2705408.3964 | 1231475.338
88 | 2705471.3487 | 1231426.121
89 | 2705478.0139 | 1231419.3341
90 | 2705471.1982 | 1231419.669
91 | 2705415.7107 | 1231485.9127
92 | 2705378.5883 | 1231474.4802
93 | 2705370.2348 | 1231471.6292
94 | 2705373.37 | 1231463.473
95 | 2705362.2612 | 1231547.9343

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1