## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3408-22_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3408-22_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3408-22_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3408-22_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3408-22_0_4_node_26 | 0.4 | n |  | TRUE
5 | bus_LV_3408-22_0_4_node_25 | 0.4 | n |  | TRUE
6 | bus_LV_3408-22_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_3408-22_0_4_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_3408-22_0_4_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_3408-22_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_3408-22_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_3408-22_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_3408-22_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_3408-22_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_3408-22_0_4_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_3408-22_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_3408-22_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_3408-22_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_3408-22_0_4_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_3408-22_0_4_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_3408-22_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_3408-22_0_4_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_3408-22_0_4_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_3408-22_0_4_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_3408-22_0_4_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_3408-22_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_3408-22_0_4_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_3408-22_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_3408-22_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_3408-22_0_4_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_3408-22_0_4_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_3408-22_0_4_node_40 | 0.4 | n |  | TRUE
32 | bus_LV_3408-22_0_4_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_3408-22_0_4_node_42 | 0.4 | n |  | TRUE
34 | bus_LV_3408-22_0_4_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_3408-22_0_4_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_3408-22_0_4_node_74 | 0.4 | n |  | TRUE
37 | bus_LV_3408-22_0_4_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_3408-22_0_4_node_77 | 0.4 | n |  | TRUE
39 | bus_LV_3408-22_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_3408-22_0_4_node_38 | 0.4 | n |  | TRUE
41 | bus_LV_3408-22_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_3408-22_0_4_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_3408-22_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_3408-22_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_3408-22_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_3408-22_0_4_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_3408-22_0_4_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_3408-22_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_3408-22_0_4_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_3408-22_0_4_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_3408-22_0_4_node_63 | 0.4 | n |  | TRUE
52 | bus_LV_3408-22_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_3408-22_0_4_node_78 | 0.4 | n |  | TRUE
54 | bus_LV_3408-22_0_4_node_76 | 0.4 | n |  | TRUE
55 | bus_LV_3408-22_0_4_node_79 | 0.4 | n |  | TRUE
56 | bus_LV_3408-22_0_4_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_3408-22_0_4_node_73 | 0.4 | n |  | TRUE
58 | bus_LV_3408-22_0_4_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_3408-22_0_4_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_3408-22_0_4_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_3408-22_0_4_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_3408-22_0_4_node_65 | 0.4 | n |  | TRUE
63 | bus_LV_3408-22_0_4_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_3408-22_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_3408-22_0_4_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_3408-22_0_4_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_3408-22_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_3408-22_0_4_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_3408-22_0_4_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_3408-22_0_4_node_57 | 0.4 | n |  | TRUE
71 | bus_LV_3408-22_0_4_node_58 | 0.4 | n |  | TRUE
72 | bus_LV_3408-22_0_4_node_59 | 0.4 | n |  | TRUE
73 | bus_LV_3408-22_0_4_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_3408-22_0_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_3408-22_0_4_node_66 | 0.4 | n |  | TRUE
76 | bus_LV_3408-22_0_4_node_80 | 0.4 | n |  | TRUE
77 | bus_LV_3408-22_0_4_node_81 | 0.4 | n |  | TRUE
78 | bus_LV_3408-22_0_4_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_3408-22_0_4_node_82 | 0.4 | n |  | TRUE
80 | bus_LV_3408-22_0_4_node_83 | 0.4 | n |  | TRUE
81 | bus_MV_588_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3408-22_0_4_load_0 | 0 | 0.033243 | 0.0083314 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3408-22_0_4_load_26 | 4 | 0.0060497 | 0.0015162 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3408-22_0_4_load_25 | 5 | 0.01259 | 0.0031554 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3408-22_0_4_load_27 | 7 | 0.0087297 | 0.0021879 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3408-22_0_4_load_4 | 8 | 0.0029106 | 0.00072947 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3408-22_0_4_load_5 | 9 | 0.002655 | 0.00066542 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3408-22_0_4_load_6 | 10 | 0.0077216 | 0.0019352 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3408-22_0_4_load_15 | 12 | 0.0034551 | 0.00086593 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3408-22_0_4_load_7 | 14 | 0.0094265 | 0.0023625 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3408-22_0_4_load_9 | 15 | 0.0051717 | 0.0012961 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3408-22_0_4_load_20 | 18 | 0.0071834 | 0.0018003 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3408-22_0_4_load_21 | 20 | 0.0043768 | 0.0010969 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3408-22_0_4_load_14 | 21 | 0.0058738 | 0.0014721 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3408-22_0_4_load_30 | 23 | 0.0067386 | 0.0016888 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3408-22_0_4_load_23 | 24 | 0.014554 | 0.0036476 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3408-22_0_4_load_16 | 27 | 0.0033415 | 0.00083747 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3408-22_0_4_load_69 | 29 | 0.0014547 | 0.00036458 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3408-22_0_4_load_43 | 32 | 0.0079531 | 0.0019932 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3408-22_0_4_load_39 | 34 | 0.0075654 | 0.0018961 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3408-22_0_4_load_74 | 36 | 0.014231 | 0.0035667 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3408-22_0_4_load_77 | 38 | 0.012016 | 0.0030115 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3408-22_0_4_load_35 | 41 | 0.0089418 | 0.002241 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3408-22_0_4_load_28 | 43 | 0.0089483 | 0.0022426 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3408-22_0_4_load_31 | 45 | 0.0045477 | 0.0011398 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3408-22_0_4_load_37 | 48 | 0.007039 | 0.0017641 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3408-22_0_4_load_46 | 49 | 0.0050977 | 0.0012776 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3408-22_0_4_load_49 | 50 | 0.0010917 | 0.00027361 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3408-22_0_4_load_63 | 51 | 0.001124 | 0.0002817 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3408-22_0_4_load_47 | 52 | 0.0029722 | 0.00074491 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3408-22_0_4_load_78 | 53 | 0.015775 | 0.0039535 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3408-22_0_4_load_79 | 55 | 0.016244 | 0.0040712 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3408-22_0_4_load_73 | 57 | 0.014385 | 0.0036052 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3408-22_0_4_load_61 | 59 | 0.0055797 | 0.0013984 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3408-22_0_4_load_62 | 60 | 0.00097857 | 0.00024525 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3408-22_0_4_load_67 | 63 | 0.0012382 | 0.00031032 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3408-22_0_4_load_50 | 64 | 0.0019041 | 0.00047722 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3408-22_0_4_load_54 | 67 | 0.0062036 | 0.0015548 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3408-22_0_4_load_55 | 68 | 0.0013199 | 0.0003308 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3408-22_0_4_load_56 | 69 | 0.0012755 | 0.00031968 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3408-22_0_4_load_58 | 71 | 0.0011245 | 0.00028182 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3408-22_0_4_load_59 | 72 | 0.0023987 | 0.00060118 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3408-22_0_4_load_60 | 73 | 0.0011245 | 0.00028182 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3408-22_0_4_load_81 | 77 | 0.0010899 | 0.00027316 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3408-22_0_4_load_72 | 78 | 0.0023991 | 0.00060126 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3408-22_0_4_load_82 | 79 | 0.0015229 | 0.00038167 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3408-22_0_4_load_83 | 80 | 0.0010919 | 0.00027367 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 33 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3408-22_0_4_line_0 |  | 0 | 1 | 0.061196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3408-22_0_4_line_1 |  | 1 | 2 | 0.16416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3408-22_0_4_line_2 |  | 2 | 3 | 0.025635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3408-22_0_4_line_3 |  | 3 | 4 | 0.037854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3408-22_0_4_line_4 |  | 4 | 7 | 0.059577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3408-22_0_4_line_5 |  | 5 | 6 | 0.024547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3408-22_0_4_line_6 |  | 6 | 20 | 0.032039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3408-22_0_4_line_7 |  | 7 | 43 | 0.0087066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3408-22_0_4_line_8 |  | 8 | 9 | 0.0051261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3408-22_0_4_line_9 |  | 9 | 10 | 0.028064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3408-22_0_4_line_10 |  | 10 | 11 | 0.014774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3408-22_0_4_line_11 |  | 11 | 12 | 0.040946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3408-22_0_4_line_12 |  | 11 | 13 | 0.056695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3408-22_0_4_line_13 |  | 12 | 22 | 0.013726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3408-22_0_4_line_14 |  | 13 | 15 | 0.018028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3408-22_0_4_line_15 |  | 13 | 14 | 0.017539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3408-22_0_4_line_16 |  | 15 | 16 | 0.016642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3408-22_0_4_line_17 |  | 16 | 21 | 0.017196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3408-22_0_4_line_18 |  | 17 | 18 | 0.0050586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3408-22_0_4_line_19 |  | 17 | 19 | 0.045567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3408-22_0_4_line_20 |  | 18 | 22 | 0.054668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3408-22_0_4_line_21 |  | 19 | 23 | 0.024435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3408-22_0_4_line_22 |  | 19 | 24 | 0.025889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3408-22_0_4_line_23 |  | 20 | 25 | 0.022222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3408-22_0_4_line_24 |  | 22 | 26 | 0.021933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3408-22_0_4_line_25 |  | 24 | 25 | 0.0041357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3408-22_0_4_line_26 |  | 25 | 30 | 0.022386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3408-22_0_4_line_27 |  | 26 | 28 | 0.004738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3408-22_0_4_line_28 |  | 26 | 27 | 0.02359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3408-22_0_4_line_29 |  | 28 | 29 | 0.007111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3408-22_0_4_line_30 |  | 30 | 31 | 0.043504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3408-22_0_4_line_31 |  | 30 | 32 | 0.017769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3408-22_0_4_line_32 |  | 31 | 33 | 0.064949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_3408-22_0_4_line_33 |  | 31 | 34 | 0.0066746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_3408-22_0_4_line_34 |  | 32 | 42 | 0.029479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3408-22_0_4_line_35 |  | 33 | 35 | 0.049051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3408-22_0_4_line_36 |  | 33 | 36 | 0.008374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3408-22_0_4_line_37 |  | 34 | 40 | 0.0020052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_3408-22_0_4_line_38 |  | 35 | 53 | 0.023654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3408-22_0_4_line_39 |  | 35 | 54 | 0.052286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3408-22_0_4_line_40 |  | 37 | 38 | 0.006074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3408-22_0_4_line_41 |  | 37 | 39 | 0.012146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3408-22_0_4_line_42 |  | 39 | 44 | 0.045286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3408-22_0_4_line_43 |  | 39 | 43 | 0.019231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3408-22_0_4_line_44 |  | 40 | 41 | 0.034768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_3408-22_0_4_line_45 |  | 41 | 44 | 0.038503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3408-22_0_4_line_46 |  | 42 | 56 | 0.077086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3408-22_0_4_line_47 |  | 44 | 45 | 0.017358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3408-22_0_4_line_48 |  | 45 | 46 | 0.0030655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3408-22_0_4_line_49 |  | 46 | 47 | 0.030611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3408-22_0_4_line_50 |  | 46 | 48 | 0.034137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3408-22_0_4_line_51 |  | 47 | 49 | 0.010605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3408-22_0_4_line_52 |  | 49 | 52 | 0.010409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3408-22_0_4_line_53 |  | 50 | 51 | 0.0070817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3408-22_0_4_line_54 |  | 51 | 65 | 0.0034169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3408-22_0_4_line_55 |  | 52 | 58 | 0.010107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3408-22_0_4_line_56 |  | 54 | 55 | 0.004276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3408-22_0_4_line_57 |  | 56 | 57 | 0.029962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3408-22_0_4_line_58 |  | 58 | 59 | 0.021422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3408-22_0_4_line_59 |  | 58 | 60 | 0.01076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3408-22_0_4_line_60 |  | 58 | 61 | 0.048215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3408-22_0_4_line_61 |  | 59 | 62 | 0.037255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3408-22_0_4_line_62 |  | 60 | 63 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3408-22_0_4_line_63 |  | 61 | 64 | 0.016243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3408-22_0_4_line_64 |  | 62 | 75 | 0.048597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3408-22_0_4_line_65 |  | 63 | 72 | 0.0012591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3408-22_0_4_line_66 |  | 64 | 66 | 0.0075613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3408-22_0_4_line_67 |  | 65 | 74 | 0.0098776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3408-22_0_4_line_68 |  | 65 | 73 | 0.013937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3408-22_0_4_line_69 |  | 66 | 67 | 0.012978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3408-22_0_4_line_70 |  | 68 | 69 | 0.00046387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3408-22_0_4_line_71 |  | 68 | 70 | 0.012804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3408-22_0_4_line_72 |  | 69 | 71 | 0.0082604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3408-22_0_4_line_73 |  | 70 | 72 | 0.0028364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3408-22_0_4_line_74 |  | 71 | 73 | 0.017244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3408-22_0_4_line_75 |  | 74 | 76 | 0.00439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3408-22_0_4_line_76 |  | 74 | 77 | 0.004139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3408-22_0_4_line_77 |  | 75 | 78 | 0.059783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3408-22_0_4_line_78 |  | 76 | 79 | 0.008673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3408-22_0_4_line_79 |  | 76 | 80 | 0.004139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3408-22_0_4_trafo_42 | 0.63 MVA 20/0.4 kV | 81 | 33 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2727986.7241 | 1256996.3818 | 2727925.5633 | 1256998.4592
1 | 2727986.7241 | 1256996.3818 | 2727991.6608 | 1256986.8132 | 2727998.1244 | 1256973.2742 | 2728006.6387 | 1256959.4347 | 2728009.167 | 1256954.4961 | 2728027.9604 | 1256882.5823 | 2728034.2604 | 1256858.4859 | 2728035.3872 | 1256854.173 | 2728034.5645 | 1256841.2992
2 | 2728059.3894 | 1256847.9755 | 2728034.5645 | 1256841.2992
3 | 2728059.3894 | 1256847.9755 | 2728078.4595 | 1256850.4235 | 2728087.2577 | 1256846.8328 | 2728089.9581 | 1256838.1173
4 | 2728089.9581 | 1256838.1173 | 2728090.9886 | 1256834.7916 | 2728103.9808 | 1256801.9544 | 2728106.8467 | 1256793.9759 | 2728115.6498 | 1256785.3803
5 | 2728017.2373 | 1256752.3892 | 2728013.2255 | 1256776.6062
6 | 2728017.2373 | 1256752.3892 | 2728018.0009 | 1256747.7794 | 2728022.7516 | 1256720.8283
7 | 2728121.8793 | 1256779.2978 | 2728115.6498 | 1256785.3803
8 | 2727855.6312 | 1256754.3435 | 2727860.7453 | 1256754.6933
9 | 2727873.2191 | 1256737.2963 | 2727870.8191 | 1256737.4562 | 2727868.4661 | 1256755.2213 | 2727860.7453 | 1256754.6933
10 | 2727887.9605 | 1256736.3143 | 2727873.2191 | 1256737.2963
11 | 2727887.9605 | 1256736.3143 | 2727891.3513 | 1256695.5093
12 | 2727905.4748 | 1256774.1043 | 2727909.1395 | 1256738.9409 | 2727887.9605 | 1256736.3143
13 | 2727892.488 | 1256681.8299 | 2727891.3513 | 1256695.5093
14 | 2727905.4748 | 1256774.1043 | 2727923.4285 | 1256775.7359
15 | 2727905.4748 | 1256774.1043 | 2727888.0301 | 1256772.2891
16 | 2727940.0024 | 1256777.242 | 2727923.4285 | 1256775.7359
17 | 2727940.0024 | 1256777.242 | 2727957.0914 | 1256779.569
18 | 2727951.8133 | 1256688.4288 | 2727946.7728 | 1256688.0024
19 | 2727951.8133 | 1256688.4288 | 2727966.3219 | 1256690.0883 | 2727997.0849 | 1256693.6119
20 | 2727892.488 | 1256681.8299 | 2727902.5338 | 1256683.6931 | 2727927.0846 | 1256686.337 | 2727946.7728 | 1256688.0024
21 | 2727997.0849 | 1256693.6119 | 2728000.0012 | 1256669.3532
22 | 2727997.0849 | 1256693.6119 | 2727998.6727 | 1256693.7909 | 2728014.1026 | 1256696.1043 | 2728022.5762 | 1256698.0283
23 | 2728026.6092 | 1256698.944 | 2728022.7516 | 1256720.8283
24 | 2727873.5934 | 1256671.2346 | 2727877.65 | 1256674.8143 | 2727881.298 | 1256677.4065 | 2727885.1599 | 1256679.5252 | 2727888.1751 | 1256680.6802 | 2727892.488 | 1256681.8299
25 | 2728026.6092 | 1256698.944 | 2728022.5762 | 1256698.0283
26 | 2728026.6092 | 1256698.944 | 2728042.5545 | 1256703.5818 | 2728048.0369 | 1256705.4132
27 | 2727870.4951 | 1256667.6422 | 2727873.5934 | 1256671.2346
28 | 2727873.5934 | 1256671.2346 | 2727867.3805 | 1256678.7627 | 2727866.1555 | 1256681.3385 | 2727863.127 | 1256691.8898
29 | 2727870.4951 | 1256667.6422 | 2727867.0837 | 1256663.1756 | 2727866.3018 | 1256661.9064
30 | 2728048.0369 | 1256705.4132 | 2728074.9292 | 1256714.1916 | 2728082.5472 | 1256716.3361 | 2728089.5728 | 1256718.3232
31 | 2728048.0369 | 1256705.4132 | 2728050.1608 | 1256687.7717
32 | 2728060.1329 | 1256755.4419 | 2728075.3705 | 1256757.9181 | 2728076.4909 | 1256751.8147 | 2728081.4046 | 1256721.0267 | 2728082.5472 | 1256716.3361 | 2728089.5728 | 1256718.3232
33 | 2728089.5728 | 1256718.3232 | 2728096.1697 | 1256719.3383
34 | 2728053.6843 | 1256658.5043 | 2728050.1608 | 1256687.7717
35 | 2728060.1329 | 1256755.4419 | 2728055.8284 | 1256781.4387 | 2728062.0717 | 1256789.937 | 2728074.0692 | 1256791.8871
36 | 2728061.3758 | 1256747.1613 | 2728060.1329 | 1256755.4419
37 | 2728098.1517 | 1256719.6433 | 2728096.1697 | 1256719.3383
38 | 2728094.4681 | 1256786.9796 | 2728093.5797 | 1256790.7304 | 2728083.2162 | 1256793.0972 | 2728074.0692 | 1256791.8871
39 | 2728041.1704 | 1256809.6915 | 2728058.1045 | 1256812.5492 | 2728062.0717 | 1256789.937 | 2728074.0692 | 1256791.8871
40 | 2728126.7172 | 1256752.5131 | 2728125.9229 | 1256758.5347
41 | 2728125.9229 | 1256758.5347 | 2728135.6389 | 1256765.8626
42 | 2728135.6389 | 1256765.8626 | 2728163.3041 | 1256737.903 | 2728168.2004 | 1256734.4059
43 | 2728135.6389 | 1256765.8626 | 2728121.8793 | 1256779.2978
44 | 2728098.1517 | 1256719.6433 | 2728124.9847 | 1256725.2289 | 2728132.3443 | 1256725.1418
45 | 2728168.2004 | 1256734.4059 | 2728164.3433 | 1256730.3298 | 2728148.55 | 1256724.9498 | 2728132.3443 | 1256725.1418
46 | 2728053.6843 | 1256658.5043 | 2728067.1345 | 1256654.3471 | 2728075.0233 | 1256650.9591 | 2728098.2539 | 1256654.6539 | 2728128.8845 | 1256658.7203
47 | 2728168.2004 | 1256734.4059 | 2728171.1679 | 1256733.5805 | 2728174.5177 | 1256733.5641 | 2728185.3568 | 1256734.9541
48 | 2728188.3974 | 1256735.344 | 2728185.3568 | 1256734.9541
49 | 2728218.8502 | 1256739.2402 | 2728188.3974 | 1256735.344
50 | 2728178.8543 | 1256762.1614 | 2728185.2278 | 1256762.9001 | 2728188.3974 | 1256735.344
51 | 2728218.8502 | 1256739.2402 | 2728229.3693 | 1256740.5869
52 | 2728229.3693 | 1256740.5869 | 2728238.9288 | 1256741.8107 | 2728239.6998 | 1256741.7935
53 | 2728214.0758 | 1256761.3768 | 2728212.751 | 1256768.3335
54 | 2728212.1118 | 1256771.6901 | 2728212.751 | 1256768.3335
55 | 2728249.8047 | 1256741.5683 | 2728239.6998 | 1256741.7935
56 | 2728041.7525 | 1256805.4559 | 2728041.1704 | 1256809.6915
57 | 2728128.8845 | 1256658.7203 | 2728144.8161 | 1256660.1664 | 2728152.2343 | 1256660.3939 | 2728158.7691 | 1256659.2676
58 | 2728249.8047 | 1256741.5683 | 2728271.1509 | 1256739.7624
59 | 2728249.8047 | 1256741.5683 | 2728251.4685 | 1256745.5524 | 2728250.8153 | 1256751.9621
60 | 2728238.1512 | 1256694.8629 | 2728238.5338 | 1256699.8312 | 2728241.4974 | 1256710.6717 | 2728242.9866 | 1256716.0978 | 2728249.8047 | 1256741.5683
61 | 2728307.8471 | 1256743.283 | 2728292.6141 | 1256739.2048 | 2728277.4279 | 1256739.2313 | 2728271.1509 | 1256739.7624
62 | 2728250.8153 | 1256751.9621 | 2728250.3569 | 1256756.4603 | 2728250.8547 | 1256770.2753
63 | 2728238.1512 | 1256694.8629 | 2728221.9951 | 1256693.1888
64 | 2728339.1612 | 1256779.4497 | 2728336.1609 | 1256772.7453 | 2728310.07 | 1256748.6137 | 2728307.8471 | 1256743.283
65 | 2728250.8547 | 1256770.2753 | 2728250.9 | 1256771.5336
66 | 2728214.4891 | 1256692.2925 | 2728216.8424 | 1256692.6549 | 2728221.9951 | 1256693.1888
67 | 2728202.4388 | 1256769.6899 | 2728207.2227 | 1256770.6833 | 2728212.1118 | 1256771.6901
68 | 2728212.1118 | 1256771.6901 | 2728211.3421 | 1256775.5324 | 2728212.4135 | 1256776.5677 | 2728220.7954 | 1256778.142
69 | 2728214.4891 | 1256692.2925 | 2728213.9591 | 1256696.2068 | 2728211.9716 | 1256698.1099 | 2728205.7099 | 1256697.4293
70 | 2728238.046 | 1256771.5078 | 2728238.499 | 1256771.6078
71 | 2728251.0021 | 1256774.3681 | 2728238.499 | 1256771.6078
72 | 2728238.046 | 1256771.5078 | 2728233.2386 | 1256770.4465 | 2728231.9621 | 1256770.1742 | 2728231.5625 | 1256772.1665
73 | 2728251.0021 | 1256774.3681 | 2728250.9 | 1256771.5336
74 | 2728231.5625 | 1256772.1665 | 2728230.0168 | 1256779.8741 | 2728220.7954 | 1256778.142
75 | 2728202.4388 | 1256769.6899 | 2728198.1281 | 1256768.7958
76 | 2728203.281 | 1256765.6379 | 2728202.4388 | 1256769.6899
77 | 2728339.1612 | 1256779.4497 | 2728338.9246 | 1256783.7484 | 2728336.2526 | 1256792.5095 | 2728331.969 | 1256797.321 | 2728325.3093 | 1256797.955 | 2728316.5875 | 1256792.7946 | 2728294.7904 | 1256784.9486
78 | 2728198.1281 | 1256768.7958 | 2728193.6746 | 1256767.8763 | 2728194.5168 | 1256763.8242
79 | 2728198.9703 | 1256764.7437 | 2728198.1281 | 1256768.7958

## bus_geodata
| x | y | coords
0 | 2727925.5633 | 1256998.4592
1 | 2727986.7241 | 1256996.3818
2 | 2728034.5645 | 1256841.2992
3 | 2728059.3894 | 1256847.9755
4 | 2728089.9581 | 1256838.1173
5 | 2728013.2255 | 1256776.6062
6 | 2728017.2373 | 1256752.3892
7 | 2728115.6498 | 1256785.3803
8 | 2727855.6312 | 1256754.3435
9 | 2727860.7453 | 1256754.6933
10 | 2727873.2191 | 1256737.2963
11 | 2727887.9605 | 1256736.3143
12 | 2727891.3513 | 1256695.5093
13 | 2727905.4748 | 1256774.1043
14 | 2727888.0301 | 1256772.2891
15 | 2727923.4285 | 1256775.7359
16 | 2727940.0024 | 1256777.242
17 | 2727951.8133 | 1256688.4288
18 | 2727946.7728 | 1256688.0024
19 | 2727997.0849 | 1256693.6119
20 | 2728022.7516 | 1256720.8283
21 | 2727957.0914 | 1256779.569
22 | 2727892.488 | 1256681.8299
23 | 2728000.0012 | 1256669.3532
24 | 2728022.5762 | 1256698.0283
25 | 2728026.6092 | 1256698.944
26 | 2727873.5934 | 1256671.2346
27 | 2727863.127 | 1256691.8898
28 | 2727870.4951 | 1256667.6422
29 | 2727866.3018 | 1256661.9064
30 | 2728048.0369 | 1256705.4132
31 | 2728089.5728 | 1256718.3232
32 | 2728050.1608 | 1256687.7717
33 | 2728060.1329 | 1256755.4419
34 | 2728096.1697 | 1256719.3383
35 | 2728074.0692 | 1256791.8871
36 | 2728061.3758 | 1256747.1613
37 | 2728125.9229 | 1256758.5347
38 | 2728126.7172 | 1256752.5131
39 | 2728135.6389 | 1256765.8626
40 | 2728098.1517 | 1256719.6433
41 | 2728132.3443 | 1256725.1418
42 | 2728053.6843 | 1256658.5043
43 | 2728121.8793 | 1256779.2978
44 | 2728168.2004 | 1256734.4059
45 | 2728185.3568 | 1256734.9541
46 | 2728188.3974 | 1256735.344
47 | 2728218.8502 | 1256739.2402
48 | 2728178.8543 | 1256762.1614
49 | 2728229.3693 | 1256740.5869
50 | 2728214.0758 | 1256761.3768
51 | 2728212.751 | 1256768.3335
52 | 2728239.6998 | 1256741.7935
53 | 2728094.4681 | 1256786.9796
54 | 2728041.1704 | 1256809.6915
55 | 2728041.7525 | 1256805.4559
56 | 2728128.8845 | 1256658.7203
57 | 2728158.7691 | 1256659.2676
58 | 2728249.8047 | 1256741.5683
59 | 2728271.1509 | 1256739.7624
60 | 2728250.8153 | 1256751.9621
61 | 2728238.1512 | 1256694.8629
62 | 2728307.8471 | 1256743.283
63 | 2728250.8547 | 1256770.2753
64 | 2728221.9951 | 1256693.1888
65 | 2728212.1118 | 1256771.6901
66 | 2728214.4891 | 1256692.2925
67 | 2728205.7099 | 1256697.4293
68 | 2728238.499 | 1256771.6078
69 | 2728238.046 | 1256771.5078
70 | 2728251.0021 | 1256774.3681
71 | 2728231.5625 | 1256772.1665
72 | 2728250.9 | 1256771.5336
73 | 2728220.7954 | 1256778.142
74 | 2728202.4388 | 1256769.6899
75 | 2728339.1612 | 1256779.4497
76 | 2728198.1281 | 1256768.7958
77 | 2728203.281 | 1256765.6379
78 | 2728294.7904 | 1256784.9486
79 | 2728194.5168 | 1256763.8242
80 | 2728198.9703 | 1256764.7437
81 | 2728061.3758 | 1256747.1613

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1