## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_351-208_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_351-208_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_351-208_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_351-208_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_351-208_0_4_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_351-208_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_351-208_0_4_node_79 | 0.4 | n |  | TRUE
7 | bus_LV_351-208_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_351-208_0_4_node_42 | 0.4 | n |  | TRUE
9 | bus_LV_351-208_0_4_node_83 | 0.4 | n |  | TRUE
10 | bus_LV_351-208_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_351-208_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_351-208_0_4_node_72 | 0.4 | n |  | TRUE
13 | bus_LV_351-208_0_4_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_351-208_0_4_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_351-208_0_4_node_30 | 0.4 | n |  | TRUE
16 | bus_LV_351-208_0_4_node_84 | 0.4 | n |  | TRUE
17 | bus_LV_351-208_0_4_node_76 | 0.4 | n |  | TRUE
18 | bus_LV_351-208_0_4_node_75 | 0.4 | n |  | TRUE
19 | bus_LV_351-208_0_4_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_351-208_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_351-208_0_4_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_351-208_0_4_node_71 | 0.4 | n |  | TRUE
23 | bus_LV_351-208_0_4_node_69 | 0.4 | n |  | TRUE
24 | bus_LV_351-208_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_351-208_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_351-208_0_4_node_10 | 0.4 | n |  | TRUE
27 | bus_LV_351-208_0_4_node_11 | 0.4 | n |  | TRUE
28 | bus_LV_351-208_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_351-208_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_351-208_0_4_node_58 | 0.4 | n |  | TRUE
31 | bus_LV_351-208_0_4_node_66 | 0.4 | n |  | TRUE
32 | bus_LV_351-208_0_4_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_351-208_0_4_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_351-208_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_351-208_0_4_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_351-208_0_4_node_47 | 0.4 | n |  | TRUE
37 | bus_LV_351-208_0_4_node_38 | 0.4 | n |  | TRUE
38 | bus_LV_351-208_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_351-208_0_4_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_351-208_0_4_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_351-208_0_4_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_351-208_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_351-208_0_4_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_351-208_0_4_node_67 | 0.4 | n |  | TRUE
45 | bus_LV_351-208_0_4_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_351-208_0_4_node_53 | 0.4 | n |  | TRUE
47 | bus_LV_351-208_0_4_node_51 | 0.4 | n |  | TRUE
48 | bus_LV_351-208_0_4_node_62 | 0.4 | n |  | TRUE
49 | bus_LV_351-208_0_4_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_351-208_0_4_node_87 | 0.4 | n |  | TRUE
51 | bus_LV_351-208_0_4_node_56 | 0.4 | n |  | TRUE
52 | bus_LV_351-208_0_4_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_351-208_0_4_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_351-208_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_351-208_0_4_node_32 | 0.4 | n |  | TRUE
56 | bus_LV_351-208_0_4_node_33 | 0.4 | n |  | TRUE
57 | bus_LV_351-208_0_4_node_34 | 0.4 | n |  | TRUE
58 | bus_LV_351-208_0_4_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_351-208_0_4_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_351-208_0_4_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_351-208_0_4_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_351-208_0_4_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_351-208_0_4_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_351-208_0_4_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_351-208_0_4_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_351-208_0_4_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_351-208_0_4_node_82 | 0.4 | n |  | TRUE
68 | bus_LV_351-208_0_4_node_77 | 0.4 | n |  | TRUE
69 | bus_LV_351-208_0_4_node_78 | 0.4 | n |  | TRUE
70 | bus_LV_351-208_0_4_node_86 | 0.4 | n |  | TRUE
71 | bus_LV_351-208_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_351-208_0_4_node_50 | 0.4 | n |  | TRUE
73 | bus_LV_351-208_0_4_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_351-208_0_4_node_80 | 0.4 | n |  | TRUE
75 | bus_LV_351-208_0_4_node_81 | 0.4 | n |  | TRUE
76 | bus_LV_351-208_0_4_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_351-208_0_4_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_351-208_0_4_node_63 | 0.4 | n |  | TRUE
79 | bus_LV_351-208_0_4_node_85 | 0.4 | n |  | TRUE
80 | bus_LV_351-208_0_4_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_351-208_0_4_node_73 | 0.4 | n |  | TRUE
82 | bus_MV_593_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_351-208_0_4_load_0 | 0 | 0.056575 | 0.014179 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_351-208_0_4_load_27 | 4 | 0.02144 | 0.0053735 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_351-208_0_4_load_79 | 6 | 0.0028328 | 0.00070996 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_351-208_0_4_load_42 | 8 | 0.0091688 | 0.0022979 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_351-208_0_4_load_83 | 9 | 0.0091705 | 0.0022983 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_351-208_0_4_load_72 | 12 | 0.0063885 | 0.0016011 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_351-208_0_4_load_14 | 14 | 0.005526 | 0.0013849 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_351-208_0_4_load_30 | 15 | 0.0033537 | 0.00084052 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_351-208_0_4_load_84 | 16 | 0.010299 | 0.0025811 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_351-208_0_4_load_74 | 19 | 0.0067873 | 0.0017011 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_351-208_0_4_load_71 | 22 | 0.0086949 | 0.0021792 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_351-208_0_4_load_69 | 23 | 0.007625 | 0.001911 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_351-208_0_4_load_29 | 25 | 0.0055463 | 0.00139 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_351-208_0_4_load_10 | 26 | 0.0096382 | 0.0024156 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_351-208_0_4_load_11 | 27 | 0.0049365 | 0.0012372 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_351-208_0_4_load_13 | 28 | 0.01088 | 0.0027267 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_351-208_0_4_load_66 | 31 | 0.011887 | 0.0029792 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_351-208_0_4_load_39 | 32 | 0.0063036 | 0.0015798 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_351-208_0_4_load_24 | 33 | 0.010905 | 0.0027331 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_351-208_0_4_load_57 | 35 | 0.0080461 | 0.0020165 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_351-208_0_4_load_38 | 37 | 0.0038878 | 0.00097438 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_351-208_0_4_load_17 | 38 | 0.033347 | 0.0083574 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_351-208_0_4_load_18 | 39 | 0.0044537 | 0.0011162 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_351-208_0_4_load_26 | 41 | 0.005139 | 0.001288 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_351-208_0_4_load_67 | 44 | 0.0042056 | 0.001054 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_351-208_0_4_load_53 | 46 | 0.0036155 | 0.00090612 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_351-208_0_4_load_51 | 47 | 0.013187 | 0.0033049 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_351-208_0_4_load_62 | 48 | 0.0031746 | 0.00079562 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_351-208_0_4_load_54 | 49 | 0.0046333 | 0.0011612 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_351-208_0_4_load_87 | 50 | 0.0031598 | 0.00079193 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_351-208_0_4_load_56 | 51 | 0.0026807 | 0.00067184 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_351-208_0_4_load_49 | 52 | 0.010904 | 0.0027328 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_351-208_0_4_load_60 | 53 | 0.0034836 | 0.00087306 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_351-208_0_4_load_55 | 54 | 0.0039434 | 0.00098832 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_351-208_0_4_load_32 | 55 | 0.0078598 | 0.0019699 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_351-208_0_4_load_33 | 56 | 0.0062405 | 0.001564 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_351-208_0_4_load_34 | 57 | 0.0053803 | 0.0013484 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_351-208_0_4_load_35 | 58 | 0.006292 | 0.0015769 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_351-208_0_4_load_36 | 59 | 0.008357 | 0.0020945 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_351-208_0_4_load_37 | 60 | 0.0089025 | 0.0022312 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_351-208_0_4_load_46 | 61 | 0.010235 | 0.0025652 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_351-208_0_4_load_40 | 62 | 0.0039704 | 0.00099508 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_351-208_0_4_load_41 | 63 | 0.0037903 | 0.00094993 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_351-208_0_4_load_43 | 64 | 0.0091413 | 0.002291 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_351-208_0_4_load_44 | 65 | 0.0029891 | 0.00074915 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_351-208_0_4_load_45 | 66 | 0.0091377 | 0.0022901 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_351-208_0_4_load_78 | 69 | 0.0096205 | 0.0024111 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_351-208_0_4_load_86 | 70 | 0.011958 | 0.002997 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_351-208_0_4_load_48 | 71 | 0.022121 | 0.0055442 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_351-208_0_4_load_50 | 72 | 0.02209 | 0.0055362 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_351-208_0_4_load_52 | 73 | 0.0086368 | 0.0021646 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_351-208_0_4_load_80 | 74 | 0.0063267 | 0.0015856 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_351-208_0_4_load_81 | 75 | 0.020101 | 0.0050377 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_351-208_0_4_load_59 | 76 | 0.0058494 | 0.001466 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_351-208_0_4_load_61 | 77 | 0.010928 | 0.0027388 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_351-208_0_4_load_63 | 78 | 0.0085866 | 0.002152 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_351-208_0_4_load_85 | 79 | 0.0055308 | 0.0013862 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_351-208_0_4_load_68 | 80 | 0.0033851 | 0.0008484 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_351-208_0_4_load_73 | 81 | 0.0078727 | 0.0019731 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_351-208_0_4_line_0 |  | 0 | 1 | 0.043803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_351-208_0_4_line_1 |  | 1 | 2 | 0.088688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_351-208_0_4_line_2 |  | 2 | 3 | 0.075721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_351-208_0_4_line_3 |  | 2 | 4 | 0.045786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_351-208_0_4_line_4 |  | 3 | 5 | 0.12534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_351-208_0_4_line_5 |  | 3 | 6 | 0.058866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_351-208_0_4_line_6 |  | 5 | 14 | 0.010145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_351-208_0_4_line_7 |  | 5 | 15 | 0.0092111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_351-208_0_4_line_8 |  | 7 | 8 | 0.0073447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_351-208_0_4_line_9 |  | 7 | 9 | 0.0084513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_351-208_0_4_line_10 |  | 8 | 20 | 0.025595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_351-208_0_4_line_11 |  | 9 | 17 | 0.011232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_351-208_0_4_line_12 |  | 10 | 11 | 0.040533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_351-208_0_4_line_13 |  | 10 | 12 | 0.071006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_351-208_0_4_line_14 |  | 11 | 13 | 0.070502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_351-208_0_4_line_15 |  | 12 | 21 | 0.0042102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_351-208_0_4_line_16 |  | 13 | 16 | 0.10326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_351-208_0_4_line_17 |  | 14 | 24 | 0.012204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_351-208_0_4_line_18 |  | 15 | 25 | 0.010842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_351-208_0_4_line_19 |  | 17 | 18 | 0.0044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_351-208_0_4_line_20 |  | 18 | 19 | 0.012388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_351-208_0_4_line_21 |  | 18 | 68 | 0.023411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_351-208_0_4_line_22 |  | 20 | 32 | 0.012453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_351-208_0_4_line_23 |  | 20 | 24 | 0.035891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_351-208_0_4_line_24 |  | 21 | 81 | 0.023207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_351-208_0_4_line_25 |  | 21 | 80 | 0.01092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_351-208_0_4_line_26 |  | 22 | 23 | 0.0032129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_351-208_0_4_line_27 |  | 23 | 80 | 0.021245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_351-208_0_4_line_28 |  | 24 | 28 | 0.01528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_351-208_0_4_line_29 |  | 24 | 29 | 0.033834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_351-208_0_4_line_30 |  | 24 | 26 | 0.047392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_351-208_0_4_line_31 |  | 26 | 27 | 0.027628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_351-208_0_4_line_32 |  | 29 | 30 | 0.004228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_351-208_0_4_line_33 |  | 29 | 31 | 0.027898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_351-208_0_4_line_34 |  | 30 | 35 | 0.023408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_351-208_0_4_line_35 |  | 30 | 36 | 0.00582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_351-208_0_4_line_36 |  | 32 | 37 | 0.019537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_351-208_0_4_line_37 |  | 33 | 34 | 0.0147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_351-208_0_4_line_38 |  | 34 | 40 | 0.003808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_351-208_0_4_line_39 |  | 34 | 41 | 0.025546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_351-208_0_4_line_40 |  | 34 | 39 | 0.012237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_351-208_0_4_line_41 |  | 35 | 40 | 0.01545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_351-208_0_4_line_42 |  | 36 | 69 | 0.0074211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_351-208_0_4_line_43 |  | 36 | 61 | 0.032711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_351-208_0_4_line_44 |  | 37 | 62 | 0.0060889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_351-208_0_4_line_45 |  | 38 | 39 | 0.045138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_351-208_0_4_line_46 |  | 40 | 49 | 0.0090897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_351-208_0_4_line_47 |  | 41 | 50 | 0.0035993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_351-208_0_4_line_48 |  | 42 | 43 | 0.068098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_351-208_0_4_line_49 |  | 42 | 44 | 0.042989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_351-208_0_4_line_50 |  | 43 | 48 | 0.059274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_351-208_0_4_line_51 |  | 43 | 45 | 0.037593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_351-208_0_4_line_52 |  | 44 | 51 | 0.022523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_351-208_0_4_line_53 |  | 45 | 46 | 0.098693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_351-208_0_4_line_54 |  | 45 | 47 | 0.019089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_351-208_0_4_line_55 |  | 47 | 52 | 0.04545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_351-208_0_4_line_56 |  | 48 | 53 | 0.015706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_351-208_0_4_line_57 |  | 49 | 54 | 0.019138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_351-208_0_4_line_58 |  | 51 | 54 | 0.021125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_351-208_0_4_line_59 |  | 52 | 71 | 0.0021605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_351-208_0_4_line_60 |  | 53 | 76 | 0.065362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_351-208_0_4_line_61 |  | 55 | 56 | 0.013068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_351-208_0_4_line_62 |  | 55 | 57 | 0.021633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_351-208_0_4_line_63 |  | 56 | 58 | 0.0028911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_351-208_0_4_line_64 |  | 57 | 59 | 0.011861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_351-208_0_4_line_65 |  | 58 | 60 | 0.018253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_351-208_0_4_line_66 |  | 59 | 61 | 0.056597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_351-208_0_4_line_67 |  | 62 | 63 | 0.0023372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_351-208_0_4_line_68 |  | 64 | 65 | 0.013938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_351-208_0_4_line_69 |  | 65 | 66 | 0.0019641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_351-208_0_4_line_70 |  | 66 | 67 | 0.010856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_351-208_0_4_line_71 |  | 67 | 68 | 0.006495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_351-208_0_4_line_72 |  | 68 | 81 | 0.017417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_351-208_0_4_line_73 |  | 69 | 70 | 0.020237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_351-208_0_4_line_74 |  | 71 | 72 | 0.061019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_351-208_0_4_line_75 |  | 72 | 73 | 0.003556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_351-208_0_4_line_76 |  | 73 | 74 | 0.052923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_351-208_0_4_line_77 |  | 74 | 75 | 0.003791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_351-208_0_4_line_78 |  | 76 | 77 | 0.04645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_351-208_0_4_line_79 |  | 77 | 78 | 0.027211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_351-208_0_4_line_80 |  | 78 | 79 | 0.011555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_351-208_0_4_trafo_66 | 0.63 MVA 20/0.4 kV | 82 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2600488.5686 | 1198133.3752 | 2600473.1174 | 1198138.7548 | 2600472.3331 | 1198139.0771 | 2600471.6782 | 1198139.544 | 2600471.008 | 1198140.4555 | 2600470.1246 | 1198141.7784 | 2600465.6693 | 1198148.6818 | 2600464.5194 | 1198150.3937 | 2600463.9177 | 1198151.1608 | 2600460.1254 | 1198153.0727 | 2600455.9749 | 1198158.2752 | 2600455.4217 | 1198158.9997
1 | 2600488.5686 | 1198133.3752 | 2600489.3225 | 1198133.1195 | 2600490.1602 | 1198132.7527 | 2600490.9369 | 1198132.3637 | 2600522.099 | 1198111.3547 | 2600525.4269 | 1198109.1205 | 2600523.4776 | 1198107.3638 | 2600521.6806 | 1198106.0852 | 2600519.1296 | 1198105.1179 | 2600530.6437 | 1198102.9064 | 2600533.8269 | 1198101.6838 | 2600536.3933 | 1198099.8163 | 2600541.4653 | 1198094.3138 | 2600542.2573 | 1198093.4579 | 2600547.8322 | 1198085.1539
2 | 2600516.1471 | 1198071.0105 | 2600522.2157 | 1198079.0042 | 2600522.5506 | 1198081.2832 | 2600521.1339 | 1198084.0401 | 2600519.3137 | 1198086.797 | 2600517.8972 | 1198089.2093 | 2600516.6177 | 1198090.9546 | 2600516.3511 | 1198092.6999 | 2600518.5128 | 1198105.1845 | 2600519.1296 | 1198105.1179 | 2600530.6437 | 1198102.9064 | 2600533.8269 | 1198101.6838 | 2600536.3933 | 1198099.8163 | 2600541.4653 | 1198094.3138 | 2600542.2573 | 1198093.4579 | 2600547.8322 | 1198085.1539
3 | 2600547.8322 | 1198085.1539 | 2600550.0025 | 1198084.4537 | 2600556.1403 | 1198083.8427 | 2600557.7395 | 1198083.476 | 2600559.4453 | 1198082.7646 | 2600585.3256 | 1198060.9492
4 | 2600433.5163 | 1198066.9361 | 2600431.0107 | 1198071.2383 | 2600429.8912 | 1198073.0169 | 2600427.7435 | 1198076.1963 | 2600425.8016 | 1198078.7642 | 2600424.0043 | 1198081.0987 | 2600422.2832 | 1198083.0329 | 2600431.3294 | 1198089.6037 | 2600432.3955 | 1198089.4036 | 2600436.3782 | 1198089.3594 | 2600440.9624 | 1198090.0823 | 2600445.2725 | 1198091.1498 | 2600449.7043 | 1198092.3285 | 2600453.0549 | 1198093.8184 | 2600456.8929 | 1198091.9621 | 2600459.2689 | 1198091.7399 | 2600461.7132 | 1198092.8184 | 2600466.0232 | 1198094.8197 | 2600472.2065 | 1198095.8985 | 2600478.3138 | 1198095.8322 | 2600483.5606 | 1198094.4652 | 2600488.5867 | 1198091.7418 | 2600498.1441 | 1198084.7944 | 2600516.1471 | 1198071.0105
5 | 2600516.1471 | 1198071.0105 | 2600522.4375 | 1198065.8082 | 2600524.9507 | 1198062.8735 | 2600526.0322 | 1198060.5168 | 2600526.535 | 1198057.9377 | 2600526.68 | 1198053.9244 | 2600526.3911 | 1198047.2542 | 2600526.7492 | 1198044.8196 | 2600527.5413 | 1198043.5301 | 2600529.6279 | 1198041.8849 | 2600545.019 | 1198030.3133 | 2600549.0091 | 1198027.2359
6 | 2600433.5163 | 1198066.9361 | 2600438.2422 | 1198057.9589
7 | 2600433.5163 | 1198066.9361 | 2600434.6738 | 1198067.5699 | 2600441.6014 | 1198071.3492
8 | 2600400.7243 | 1198095.1493 | 2600406.7087 | 1198090.8912
9 | 2600400.7243 | 1198095.1493 | 2600393.884 | 1198100.1126
10 | 2600424.85 | 1198073.1167 | 2600422.9004 | 1198075.9848 | 2600421.1716 | 1198078.2748 | 2600418.5062 | 1198081.2874 | 2600415.8712 | 1198083.7885 | 2600411.3477 | 1198087.5903 | 2600406.7087 | 1198090.8912
11 | 2600385.3337 | 1198107.3772 | 2600386.7882 | 1198105.8987 | 2600392.911 | 1198100.8186 | 2600393.884 | 1198100.1126
12 | 2600296.593 | 1198185.4149 | 2600264.7862 | 1198166.248 | 2600261.8849 | 1198164.4803
13 | 2600296.593 | 1198185.4149 | 2600334.4418 | 1198125.6512 | 2600334.5891 | 1198125.4302
14 | 2600210.7515 | 1198124.6132 | 2600210.9571 | 1198126.1028 | 2600211.3607 | 1198127.5147 | 2600210.7591 | 1198128.7042 | 2600208.8324 | 1198132.484 | 2600233.7786 | 1198147.526 | 2600261.8849 | 1198164.4803
15 | 2600336.9244 | 1198121.9271 | 2600334.5891 | 1198125.4302
16 | 2600210.7515 | 1198124.6132 | 2600211.0257 | 1198123.0679 | 2600211.772 | 1198121.4448 | 2600215.2903 | 1198115.4417 | 2600220.3621 | 1198107.6932 | 2600226.5228 | 1198100.2672 | 2600234.5036 | 1198092.5189 | 2600240.253 | 1198087.9944 | 2600245.0582 | 1198084.6927 | 2600287.797 | 1198059.1965
17 | 2600443.9273 | 1198047.1596 | 2600438.2422 | 1198057.9589
18 | 2600451.1195 | 1198076.5417 | 2600441.6014 | 1198071.3492
19 | 2600385.3337 | 1198107.3772 | 2600381.5872 | 1198105.0536
20 | 2600381.5872 | 1198105.0536 | 2600377.3454 | 1198110.4451 | 2600374.0022 | 1198114.8473
21 | 2600381.5872 | 1198105.0536 | 2600369.8452 | 1198097.6268 | 2600364.3854 | 1198094.0468 | 2600361.9106 | 1198092.2902
22 | 2600424.85 | 1198073.1167 | 2600414.1954 | 1198066.6694
23 | 2600424.85 | 1198073.1167 | 2600430.5238 | 1198063.3229 | 2600437.5153 | 1198050.1163 | 2600440.3179 | 1198045.3028 | 2600443.9273 | 1198047.1596
24 | 2600336.9244 | 1198121.9271 | 2600349.249 | 1198102.2634
25 | 2600336.9244 | 1198121.9271 | 2600327.7278 | 1198116.0399
26 | 2600319.1292 | 1198096.2904 | 2600319.1292 | 1198096.2904 | 2600320.2943 | 1198096.7796 | 2600321.5441 | 1198098.2755
27 | 2600327.7278 | 1198116.0399 | 2600323.9336 | 1198113.611 | 2600322.6391 | 1198111.3986 | 2600321.4666 | 1198108.208 | 2600321.0326 | 1198105.5621 | 2600321.284 | 1198103.6611 | 2600322.3882 | 1198101.6379 | 2600322.8833 | 1198100.5262 | 2600322.4493 | 1198099.3589 | 2600321.5441 | 1198098.2755
28 | 2600443.9273 | 1198047.1596 | 2600446.4177 | 1198042.9575 | 2600452.4126 | 1198034.4648
29 | 2600443.9273 | 1198047.1596 | 2600440.3179 | 1198045.3028 | 2600446.3039 | 1198035.9982 | 2600458.2301 | 1198021.5802
30 | 2600443.9273 | 1198047.1596 | 2600462.3705 | 1198056.7214 | 2600470.6858 | 1198061.3355 | 2600472.5362 | 1198061.9804 | 2600474.5237 | 1198062.3141 | 2600476.5189 | 1198062.3698 | 2600478.1561 | 1198062.0475 | 2600479.7249 | 1198061.1916 | 2600485.9961 | 1198056.7561
31 | 2600485.9961 | 1198056.7561 | 2600508.5527 | 1198040.8026
32 | 2600461.3144 | 1198018.6788 | 2600458.2301 | 1198021.5802
33 | 2600458.2301 | 1198021.5802 | 2600452.6711 | 1198020.7794 | 2600430.4014 | 1198021.5178
34 | 2600461.3144 | 1198018.6788 | 2600467.2393 | 1198013.9878 | 2600480.1086 | 1198004.7334
35 | 2600461.3144 | 1198018.6788 | 2600456.54 | 1198015.3323
36 | 2600397.4802 | 1198056.5548 | 2600414.1954 | 1198066.6694
37 | 2600494.8985 | 1197998.7927 | 2600482.9275 | 1198007.3248
38 | 2600494.8985 | 1197998.7927 | 2600492.6523 | 1197995.7131
39 | 2600494.8985 | 1197998.7927 | 2600506.1374 | 1198014.4463 | 2600510.8411 | 1198018.6009
40 | 2600494.8985 | 1197998.7927 | 2600503.5955 | 1197992.59 | 2600504.7636 | 1197991.5638
41 | 2600492.6523 | 1197995.7131 | 2600480.1086 | 1198004.7334
42 | 2600456.54 | 1198015.3323 | 2600451.1869 | 1198010.1924
43 | 2600456.54 | 1198015.3323 | 2600423.87 | 1198016.9658
44 | 2600397.4802 | 1198056.5548 | 2600392.2708 | 1198053.4025
45 | 2600534.66 | 1197957.9534 | 2600531.6292 | 1197962.6095 | 2600528.956 | 1197966.1333 | 2600520.1292 | 1197976.6494 | 2600510.9598 | 1197986.1204 | 2600504.7636 | 1197991.5638
46 | 2600492.6523 | 1197995.7131 | 2600494.9446 | 1197994.0013 | 2600499.9244 | 1197990.2598
47 | 2600513.5388 | 1198020.9837 | 2600510.8411 | 1198018.6009
48 | 2600538.4303 | 1197855.4973 | 2600550.5393 | 1197848.3055 | 2600552.7316 | 1197859.4895 | 2600553.2112 | 1197861.9464 | 2600553.6907 | 1197864.4033 | 2600554.5502 | 1197878.1106 | 2600554.5724 | 1197885.1033 | 2600554.5341 | 1197888.6607 | 2600554.1071 | 1197895.1864 | 2600553.2841 | 1197901.9232
49 | 2600553.2841 | 1197901.9232 | 2600551.7147 | 1197909.8273 | 2600550.8615 | 1197913.3625 | 2600548.0736 | 1197922.6672 | 2600544.2499 | 1197933.0725 | 2600540.9672 | 1197940.2538 | 2600539.8095 | 1197942.5806
50 | 2600538.4303 | 1197855.4973 | 2600539.74 | 1197857.6208 | 2600540.1664 | 1197858.31 | 2600537.2953 | 1197859.9663 | 2600535.3304 | 1197861.4558 | 2600533.5711 | 1197863.3456 | 2600531.8803 | 1197866.247 | 2600520.9204 | 1197885.4008 | 2600510.8365 | 1197902.398 | 2600509.4458 | 1197904.3747
51 | 2600514.2118 | 1197879.6306 | 2600518.5524 | 1197880.8204 | 2600526.1232 | 1197865.3683 | 2600531.8351 | 1197859.599 | 2600538.4303 | 1197855.4973
52 | 2600539.8095 | 1197942.5806 | 2600536.7858 | 1197948.658 | 2600531.6372 | 1197957.0398 | 2600528.1271 | 1197961.78
53 | 2600514.2118 | 1197879.6306 | 2600507.2505 | 1197891.2918 | 2600500.6854 | 1197901.8081 | 2600493.2217 | 1197911.6239 | 2600485.9638 | 1197920.1501 | 2600478.1043 | 1197928.1761 | 2600466.9625 | 1197938.592 | 2600450.1473 | 1197951.898 | 2600449.0778 | 1197952.5608
54 | 2600514.2118 | 1197879.6306 | 2600512.3384 | 1197879.7194 | 2600510.6325 | 1197880.1306 | 2600497.3086 | 1197887.97
55 | 2600497.3086 | 1197887.97 | 2600490.5502 | 1197891.9465 | 2600488.7681 | 1197892.5578 | 2600486.7577 | 1197892.7912 | 2600469.7604 | 1197892.3898 | 2600467.7499 | 1197892.6676 | 2600465.5872 | 1197893.4234 | 2600463.7137 | 1197894.2237 | 2600454.8492 | 1197899.5479
56 | 2600509.4458 | 1197904.3747 | 2600503.8678 | 1197912.3028 | 2600500.1096 | 1197916.9954
57 | 2600499.9244 | 1197990.2598 | 2600505.5378 | 1197986.0422 | 2600511.7598 | 1197980.562 | 2600514.5037 | 1197977.8968
58 | 2600528.1271 | 1197961.78 | 2600526.3441 | 1197964.1877 | 2600525.0647 | 1197965.844 | 2600521.5766 | 1197970.1572 | 2600515.9485 | 1197976.4934 | 2600514.5037 | 1197977.8968
59 | 2600452.9971 | 1197900.6603 | 2600454.8492 | 1197899.5479
60 | 2600452.0985 | 1197960.9397 | 2600452.1038 | 1197960.9363 | 2600458.5999 | 1197956.4121 | 2600464.3496 | 1197952.2325 | 2600469.4902 | 1197948.1862 | 2600476.527 | 1197941.9167 | 2600482.7567 | 1197936.114 | 2600489.3824 | 1197929.6443 | 2600495.5436 | 1197922.6966 | 2600500.1096 | 1197916.9954
61 | 2600327.9833 | 1198054.6047 | 2600340.2769 | 1198050.172
62 | 2600360.6273 | 1198042.8343 | 2600340.2769 | 1198050.172
63 | 2600325.5517 | 1198056.1067 | 2600327.0354 | 1198054.9465 | 2600327.9833 | 1198054.6047
64 | 2600371.6274 | 1198038.4009 | 2600361.5628 | 1198042.497 | 2600360.6273 | 1198042.8343
65 | 2600311.1732 | 1198067.3504 | 2600325.5517 | 1198056.1067
66 | 2600371.6274 | 1198038.4009 | 2600386.4723 | 1198032.3595 | 2600411.2677 | 1198021.3105 | 2600420.1852 | 1198017.5757 | 2600422.1195 | 1198017.0533 | 2600423.87 | 1198016.9658
67 | 2600390.2712 | 1198052.1925 | 2600392.2708 | 1198053.4025
68 | 2600378.4806 | 1198070.0569 | 2600366.9741 | 1198077.9219
69 | 2600366.9741 | 1198077.9219 | 2600365.3526 | 1198079.0302
70 | 2600358.4537 | 1198086.7871 | 2600358.7812 | 1198085.064 | 2600359.5733 | 1198083.4298 | 2600361.1116 | 1198081.9291 | 2600365.3526 | 1198079.0302
71 | 2600361.9106 | 1198092.2902 | 2600358.4537 | 1198086.7871
72 | 2600361.9106 | 1198092.2902 | 2600360.9588 | 1198092.0789 | 2600360.045 | 1198092.0678 | 2600358.3468 | 1198092.3234 | 2600357.0522 | 1198092.9237 | 2600355.5825 | 1198093.8129 | 2600354.1508 | 1198094.869 | 2600353.2217 | 1198095.9251 | 2600349.249 | 1198102.2634
73 | 2600436.5895 | 1197996.1764 | 2600451.1869 | 1198010.1924
74 | 2600452.9971 | 1197900.6603 | 2600400.6878 | 1197932.0782
75 | 2600397.6394 | 1197933.9092 | 2600400.6878 | 1197932.0782
76 | 2600352.2143 | 1197961.0631 | 2600370.3247 | 1197950.3149 | 2600397.6394 | 1197933.9092
77 | 2600352.2143 | 1197961.0631 | 2600348.9541 | 1197962.998
78 | 2600452.0985 | 1197960.9397 | 2600446.415 | 1197964.5712 | 2600412.3161 | 1197984.9133
79 | 2600388.9477 | 1197998.854 | 2600412.3161 | 1197984.9133
80 | 2600388.9477 | 1197998.854 | 2600379.0247 | 1198004.7737

## bus_geodata
| x | y | coords
0 | 2600455.4217 | 1198158.9997
1 | 2600488.5686 | 1198133.3752
2 | 2600547.8322 | 1198085.1539
3 | 2600516.1471 | 1198071.0105
4 | 2600585.3256 | 1198060.9492
5 | 2600433.5163 | 1198066.9361
6 | 2600549.0091 | 1198027.2359
7 | 2600400.7243 | 1198095.1493
8 | 2600406.7087 | 1198090.8912
9 | 2600393.884 | 1198100.1126
10 | 2600296.593 | 1198185.4149
11 | 2600261.8849 | 1198164.4803
12 | 2600334.5891 | 1198125.4302
13 | 2600210.7515 | 1198124.6132
14 | 2600438.2422 | 1198057.9589
15 | 2600441.6014 | 1198071.3492
16 | 2600287.797 | 1198059.1965
17 | 2600385.3337 | 1198107.3772
18 | 2600381.5872 | 1198105.0536
19 | 2600374.0022 | 1198114.8473
20 | 2600424.85 | 1198073.1167
21 | 2600336.9244 | 1198121.9271
22 | 2600319.1292 | 1198096.2904
23 | 2600321.5441 | 1198098.2755
24 | 2600443.9273 | 1198047.1596
25 | 2600451.1195 | 1198076.5417
26 | 2600485.9961 | 1198056.7561
27 | 2600508.5527 | 1198040.8026
28 | 2600452.4126 | 1198034.4648
29 | 2600458.2301 | 1198021.5802
30 | 2600461.3144 | 1198018.6788
31 | 2600430.4014 | 1198021.5178
32 | 2600414.1954 | 1198066.6694
33 | 2600482.9275 | 1198007.3249
34 | 2600494.8985 | 1197998.7927
35 | 2600480.1086 | 1198004.7334
36 | 2600456.54 | 1198015.3323
37 | 2600397.4802 | 1198056.5548
38 | 2600534.66 | 1197957.9534
39 | 2600504.7636 | 1197991.5638
40 | 2600492.6523 | 1197995.7131
41 | 2600510.8411 | 1198018.6009
42 | 2600553.2841 | 1197901.9232
43 | 2600538.4303 | 1197855.4973
44 | 2600539.8095 | 1197942.5806
45 | 2600514.2118 | 1197879.6306
46 | 2600449.0778 | 1197952.5608
47 | 2600497.3086 | 1197887.97
48 | 2600509.4458 | 1197904.3747
49 | 2600499.9244 | 1197990.2598
50 | 2600513.5388 | 1198020.9837
51 | 2600528.1271 | 1197961.78
52 | 2600454.8492 | 1197899.5479
53 | 2600500.1096 | 1197916.9954
54 | 2600514.5037 | 1197977.8968
55 | 2600340.2769 | 1198050.172
56 | 2600327.9833 | 1198054.6047
57 | 2600360.6273 | 1198042.8343
58 | 2600325.5517 | 1198056.1067
59 | 2600371.6274 | 1198038.4009
60 | 2600311.1732 | 1198067.3504
61 | 2600423.87 | 1198016.9658
62 | 2600392.2708 | 1198053.4025
63 | 2600390.2712 | 1198052.1925
64 | 2600378.4806 | 1198070.0569
65 | 2600366.9741 | 1198077.9219
66 | 2600365.3526 | 1198079.0302
67 | 2600358.4537 | 1198086.7871
68 | 2600361.9106 | 1198092.2902
69 | 2600451.1869 | 1198010.1924
70 | 2600436.5895 | 1197996.1764
71 | 2600452.9971 | 1197900.6603
72 | 2600400.6878 | 1197932.0782
73 | 2600397.6394 | 1197933.9092
74 | 2600352.2143 | 1197961.0631
75 | 2600348.9541 | 1197962.998
76 | 2600452.0985 | 1197960.9397
77 | 2600412.3161 | 1197984.9133
78 | 2600388.9477 | 1197998.854
79 | 2600379.0247 | 1198004.7737
80 | 2600327.7278 | 1198116.0399
81 | 2600349.249 | 1198102.2634
82 | 2600407.8708 | 1198030.9488

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1