## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_351-232_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_351-232_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_351-232_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_351-232_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_351-232_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_351-232_0_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_351-232_0_2_node_46 | 0.4 | n |  | TRUE
7 | bus_LV_351-232_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_351-232_0_2_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_351-232_0_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_351-232_0_2_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_351-232_0_2_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_351-232_0_2_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_351-232_0_2_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_351-232_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_351-232_0_2_node_49 | 0.4 | n |  | TRUE
16 | bus_LV_351-232_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_351-232_0_2_node_32 | 0.4 | n |  | TRUE
18 | bus_LV_351-232_0_2_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_351-232_0_2_node_37 | 0.4 | n |  | TRUE
20 | bus_LV_351-232_0_2_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_351-232_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_351-232_0_2_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_351-232_0_2_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_351-232_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_351-232_0_2_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_351-232_0_2_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_351-232_0_2_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_351-232_0_2_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_351-232_0_2_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_351-232_0_2_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_351-232_0_2_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_351-232_0_2_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_351-232_0_2_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_351-232_0_2_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_351-232_0_2_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_351-232_0_2_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_351-232_0_2_node_50 | 0.4 | n |  | TRUE
38 | bus_LV_351-232_0_2_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_351-232_0_2_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_351-232_0_2_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_351-232_0_2_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_351-232_0_2_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_351-232_0_2_node_48 | 0.4 | n |  | TRUE
44 | bus_LV_351-232_0_2_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_351-232_0_2_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_351-232_0_2_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_351-232_0_2_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_351-232_0_2_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_351-232_0_2_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_351-232_0_2_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_351-232_0_2_node_51 | 0.4 | n |  | TRUE
52 | bus_LV_351-232_0_2_node_53 | 0.4 | n |  | TRUE
53 | bus_MV_598_0_node_19 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_351-232_0_2_load_0 | 0 | 0.0034548 | 0.00086585 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_351-232_0_2_load_1 | 1 | 0.0032031 | 0.00080278 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_351-232_0_2_load_3 | 3 | 0.0033246 | 0.00083321 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_351-232_0_2_load_4 | 4 | 0.0028608 | 0.00071698 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_351-232_0_2_load_20 | 5 | 0.0030559 | 0.00076589 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_351-232_0_2_load_46 | 6 | 0.0031576 | 0.00079137 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_351-232_0_2_load_25 | 10 | 0.0032433 | 0.00081284 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_351-232_0_2_load_27 | 11 | 0.0030517 | 0.00076482 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_351-232_0_2_load_49 | 15 | 0.014927 | 0.0037411 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_351-232_0_2_load_32 | 17 | 0.012334 | 0.0030912 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_351-232_0_2_load_31 | 18 | 0.013919 | 0.0034885 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_351-232_0_2_load_37 | 19 | 0.0072198 | 0.0018095 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_351-232_0_2_load_36 | 22 | 0.015186 | 0.003806 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_351-232_0_2_load_55 | 25 | 0.03743 | 0.0093807 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_351-232_0_2_load_41 | 29 | 0.011022 | 0.0027623 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_351-232_0_2_load_54 | 30 | 0.007991 | 0.0020027 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_351-232_0_2_load_21 | 31 | 0.0032657 | 0.00081846 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_351-232_0_2_load_44 | 32 | 0.0037042 | 0.00092836 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_351-232_0_2_load_38 | 33 | 0.0052916 | 0.0013262 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_351-232_0_2_load_39 | 34 | 0.0053131 | 0.0013316 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_351-232_0_2_load_26 | 35 | 0.0046493 | 0.0011652 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_351-232_0_2_load_24 | 36 | 0.0035041 | 0.00087821 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_351-232_0_2_load_50 | 37 | 0.0074445 | 0.0018658 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_351-232_0_2_load_33 | 38 | 0.0159 | 0.003985 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_351-232_0_2_load_43 | 39 | 0.0048892 | 0.0012253 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_351-232_0_2_load_42 | 40 | 0.0074861 | 0.0018762 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_351-232_0_2_load_28 | 41 | 0.0060584 | 0.0015184 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_351-232_0_2_load_45 | 42 | 0.0036746 | 0.00092094 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_351-232_0_2_load_48 | 43 | 0.0079113 | 0.0019828 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_351-232_0_2_load_34 | 44 | 0.0079853 | 0.0020013 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_351-232_0_2_load_52 | 45 | 0.0074562 | 0.0018687 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_351-232_0_2_load_22 | 46 | 0.0030938 | 0.00077539 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_351-232_0_2_load_23 | 47 | 0.003314 | 0.00083056 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_351-232_0_2_load_30 | 48 | 0.010759 | 0.0026965 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_351-232_0_2_load_47 | 49 | 0.0079269 | 0.0019867 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_351-232_0_2_load_40 | 50 | 0.0079418 | 0.0019904 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_351-232_0_2_load_51 | 51 | 0.014101 | 0.003534 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_351-232_0_2_load_53 | 52 | 0.0074611 | 0.0018699 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_351-232_0_2_line_0 |  | 0 | 1 | 0.019434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_351-232_0_2_line_1 |  | 0 | 2 | 0.010144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_351-232_0_2_line_2 |  | 1 | 3 | 0.002258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_351-232_0_2_line_3 |  | 2 | 4 | 0.0024637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_351-232_0_2_line_4 |  | 3 | 5 | 0.0059847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_351-232_0_2_line_5 |  | 4 | 6 | 0.015671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_351-232_0_2_line_6 |  | 5 | 31 | 0.0053833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_351-232_0_2_line_7 |  | 6 | 32 | 0.011881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_351-232_0_2_line_8 |  | 7 | 8 | 0.026377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_351-232_0_2_line_9 |  | 7 | 9 | 0.051849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_351-232_0_2_line_10 |  | 7 | 10 | 0.028659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_351-232_0_2_line_11 |  | 8 | 23 | 0.018676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_351-232_0_2_line_12 |  | 9 | 11 | 0.043804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_351-232_0_2_line_13 |  | 10 | 36 | 0.010593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_351-232_0_2_line_14 |  | 11 | 35 | 0.0070813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_351-232_0_2_line_15 |  | 12 | 13 | 0.009239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_351-232_0_2_line_16 |  | 12 | 14 | 0.01421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_351-232_0_2_line_17 |  | 12 | 15 | 0.002006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_351-232_0_2_line_18 |  | 13 | 19 | 0.017603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_351-232_0_2_line_19 |  | 14 | 16 | 0.013229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_351-232_0_2_line_20 |  | 14 | 17 | 0.0045979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_351-232_0_2_line_21 |  | 15 | 37 | 0.011232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_351-232_0_2_line_22 |  | 16 | 18 | 0.03284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_351-232_0_2_line_23 |  | 17 | 38 | 0.022274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_351-232_0_2_line_24 |  | 18 | 24 | 0.015896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_351-232_0_2_line_25 |  | 19 | 22 | 0.016506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_351-232_0_2_line_26 |  | 20 | 21 | 0.014895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_351-232_0_2_line_27 |  | 20 | 22 | 0.017386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_351-232_0_2_line_28 |  | 21 | 25 | 0.020987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_351-232_0_2_line_29 |  | 23 | 41 | 0.028519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_351-232_0_2_line_30 |  | 23 | 24 | 0.028253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_351-232_0_2_line_31 |  | 26 | 27 | 0.006886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_351-232_0_2_line_32 |  | 26 | 28 | 0.01767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_351-232_0_2_line_33 |  | 26 | 29 | 0.031882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_351-232_0_2_line_34 |  | 27 | 43 | 0.014755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_351-232_0_2_line_35 |  | 27 | 44 | 0.016623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_351-232_0_2_line_36 |  | 28 | 30 | 0.010368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_351-232_0_2_line_37 |  | 29 | 40 | 0.016966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_351-232_0_2_line_38 |  | 30 | 45 | 0.0095408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_351-232_0_2_line_39 |  | 31 | 46 | 0.0054193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_351-232_0_2_line_40 |  | 32 | 42 | 0.0083727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_351-232_0_2_line_41 |  | 33 | 34 | 0.0018483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_351-232_0_2_line_42 |  | 34 | 50 | 0.019547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_351-232_0_2_line_43 |  | 36 | 47 | 0.0058082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_351-232_0_2_line_44 |  | 37 | 51 | 0.013314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_351-232_0_2_line_45 |  | 39 | 40 | 0.013329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_351-232_0_2_line_46 |  | 41 | 48 | 0.028695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_351-232_0_2_line_47 |  | 43 | 49 | 0.019153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_351-232_0_2_line_48 |  | 45 | 52 | 0.0092017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_351-232_0_2_line_49 |  | 46 | 47 | 0.0054592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_351-232_0_2_line_50 |  | 49 | 50 | 0.009032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_351-232_0_2_line_51 |  | 51 | 52 | 0.013308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_351-232_0_2_trafo_33 | 0.63 MVA 20/0.4 kV | 53 | 38 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2599314.0365 | 1200572.2312 | 2599317.9986 | 1200578.4176 | 2599318.8131 | 1200579.1846 | 2599320.0006 | 1200579.7625 | 2599321.4317 | 1200580.1181 | 2599322.8095 | 1200580.029 | 2599324.3165 | 1200579.5063 | 2599328.8966 | 1200577.0487
1 | 2599308.5656 | 1200563.6887 | 2599314.0365 | 1200572.2312
2 | 2599330.8863 | 1200575.9811 | 2599328.8966 | 1200577.0487
3 | 2599308.5656 | 1200563.6887 | 2599308.8621 | 1200561.2429
4 | 2599330.8863 | 1200575.9811 | 2599334.5538 | 1200574.0132 | 2599336.1192 | 1200573.0797
5 | 2599321.5807 | 1200552.3586 | 2599310.057 | 1200559.4974 | 2599308.8621 | 1200561.2429
6 | 2599336.1192 | 1200573.0797 | 2599340.7429 | 1200570.3226
7 | 2599331.6806 | 1200546.1018 | 2599321.5807 | 1200552.3586
8 | 2599374.2433 | 1200519.7348 | 2599384.6584 | 1200536.954 | 2599386.2496 | 1200539.0327 | 2599388.7846 | 1200541.6671
9 | 2599388.7846 | 1200541.6671 | 2599390.3909 | 1200543.101 | 2599411.4016 | 1200559.3852 | 2599412.0486 | 1200559.8854 | 2599414.439 | 1200561.5749 | 2599401.2644 | 1200575.7729
10 | 2599388.7846 | 1200541.6671 | 2599377.1621 | 1200548.5944 | 2599364.1703 | 1200556.346
11 | 2599374.2433 | 1200519.7348 | 2599364.5819 | 1200503.7385
12 | 2599401.2644 | 1200575.7729 | 2599395.9427 | 1200566.9466 | 2599392.3501 | 1200568.9147 | 2599366.8642 | 1200583.5746
13 | 2599355.0734 | 1200561.7737 | 2599364.1703 | 1200556.346
14 | 2599360.7259 | 1200587.1054 | 2599366.8642 | 1200583.5746
15 | 2599314.431 | 1200417.5094 | 2599314.2712 | 1200418.321 | 2599313.8679 | 1200419.1214 | 2599313.3352 | 1200419.8886 | 2599312.6197 | 1200420.5557 | 2599311.6074 | 1200421.2673 | 2599307.8016 | 1200423.4357
16 | 2599307.8016 | 1200423.4357 | 2599308.9971 | 1200426.2926 | 2599310.4134 | 1200429.7165 | 2599310.8169 | 1200430.6725 | 2599311.19 | 1200431.584 | 2599312.7205 | 1200435.3081 | 2599313.2383 | 1200436.5642
17 | 2599307.8016 | 1200423.4357 | 2599305.9957 | 1200424.3088
18 | 2599314.431 | 1200417.5094 | 2599314.3852 | 1200416.3643 | 2599314.0653 | 1200415.2304 | 2599306.6294 | 1200401.8836
19 | 2599313.2383 | 1200436.5642 | 2599317.6683 | 1200434.7182 | 2599319.2516 | 1200434.4623 | 2599320.8882 | 1200434.5622 | 2599322.2356 | 1200435.0401 | 2599323.2937 | 1200435.8515 | 2599324.6642 | 1200437.8857
20 | 2599313.2383 | 1200436.5642 | 2599308.9927 | 1200438.3294
21 | 2599305.9957 | 1200424.3088 | 2599300.3956 | 1200427.0163 | 2599295.7709 | 1200428.9468
22 | 2599324.6642 | 1200437.8857 | 2599341.7017 | 1200465.96
23 | 2599308.9927 | 1200438.3294 | 2599288.4252 | 1200446.8804
24 | 2599349.9488 | 1200479.5494 | 2599341.7017 | 1200465.96
25 | 2599298.5962 | 1200387.4648 | 2599306.6294 | 1200401.8836
26 | 2599290.135 | 1200372.2771 | 2599277.1497 | 1200379.6384
27 | 2599290.135 | 1200372.2771 | 2599292.4572 | 1200376.4457 | 2599298.5962 | 1200387.4648
28 | 2599277.1497 | 1200379.6384 | 2599277.6372 | 1200382.4064 | 2599277.5384 | 1200383.3181 | 2599277.1427 | 1200384.3298 | 2599275.9934 | 1200385.4972 | 2599269.6912 | 1200389.9115 | 2599268.7017 | 1200390.8789 | 2599268.2527 | 1200391.5459 | 2599267.9864 | 1200392.4242 | 2599268.055 | 1200393.2135 | 2599268.2759 | 1200394.0917 | 2599268.5576 | 1200394.8032 | 2599269.1744 | 1200395.9371
29 | 2599364.5819 | 1200503.7385 | 2599362.1082 | 1200505.1951 | 2599339.9915 | 1200518.1836
30 | 2599349.9488 | 1200479.5494 | 2599364.5819 | 1200503.7385
31 | 2599252.3912 | 1200461.9415 | 2599246.0203 | 1200464.5993
32 | 2599246.0203 | 1200464.5993 | 2599243.774 | 1200459.319 | 2599247.3134 | 1200457.8177 | 2599245.326 | 1200452.882 | 2599244.298 | 1200450.3141
33 | 2599246.0203 | 1200464.5993 | 2599258.5049 | 1200493.9352
34 | 2599252.3912 | 1200461.9415 | 2599251.5616 | 1200462.7976 | 2599251.0745 | 1200463.687 | 2599250.694 | 1200464.632 | 2599250.5876 | 1200465.6437 | 2599250.8009 | 1200466.5886 | 2599254.5387 | 1200475.3699
35 | 2599252.3912 | 1200461.9415 | 2599267.7212 | 1200455.5145
36 | 2599244.298 | 1200450.3141 | 2599248.1799 | 1200448.8128 | 2599253.9068 | 1200446.4222
37 | 2599258.5049 | 1200493.9352 | 2599262.4979 | 1200503.3179 | 2599265.0912 | 1200509.5704
38 | 2599262.7113 | 1200442.7469 | 2599253.9068 | 1200446.4222
39 | 2599340.7429 | 1200570.3226 | 2599344.791 | 1200567.9087 | 2599345.3974 | 1200567.5469
40 | 2599331.6806 | 1200546.1018 | 2599338.7983 | 1200541.6925
41 | 2599273.781 | 1200521.0643 | 2599273.0731 | 1200519.3569
42 | 2599273.0731 | 1200519.3569 | 2599265.9993 | 1200502.2946 | 2599265.5775 | 1200501.3037
43 | 2599350.0855 | 1200564.7497 | 2599355.0734 | 1200561.7737
44 | 2599295.7709 | 1200428.9468 | 2599283.4843 | 1200434.0756
45 | 2599270.1979 | 1200521.8824 | 2599265.0912 | 1200509.5704
46 | 2599318.1801 | 1200509.5584 | 2599327.4215 | 1200512.9035 | 2599333.1392 | 1200522.2077 | 2599339.9915 | 1200518.1836
47 | 2599262.0401 | 1200492.9932 | 2599254.5387 | 1200475.3699
48 | 2599262.7113 | 1200442.7469 | 2599271.2029 | 1200439.2022
49 | 2599345.3974 | 1200567.5469 | 2599350.0855 | 1200564.7497
50 | 2599262.0401 | 1200492.9932 | 2599265.5775 | 1200501.3037
51 | 2599271.2029 | 1200439.2022 | 2599283.4843 | 1200434.0756

## bus_geodata
| x | y | coords
0 | 2599314.0365 | 1200572.2312
1 | 2599328.8966 | 1200577.0487
2 | 2599308.5656 | 1200563.6887
3 | 2599330.8863 | 1200575.9811
4 | 2599308.8621 | 1200561.2429
5 | 2599336.1192 | 1200573.0797
6 | 2599321.5807 | 1200552.3586
7 | 2599388.7846 | 1200541.6671
8 | 2599374.2433 | 1200519.7348
9 | 2599401.2644 | 1200575.7729
10 | 2599364.1703 | 1200556.346
11 | 2599366.8642 | 1200583.5746
12 | 2599307.8016 | 1200423.4356
13 | 2599314.431 | 1200417.5094
14 | 2599313.2383 | 1200436.5642
15 | 2599305.9957 | 1200424.3088
16 | 2599324.6642 | 1200437.8857
17 | 2599308.9927 | 1200438.3294
18 | 2599341.7017 | 1200465.96
19 | 2599306.6294 | 1200401.8836
20 | 2599290.135 | 1200372.2771
21 | 2599277.1497 | 1200379.6384
22 | 2599298.5962 | 1200387.4648
23 | 2599364.5819 | 1200503.7385
24 | 2599349.9488 | 1200479.5494
25 | 2599269.1744 | 1200395.9371
26 | 2599246.0203 | 1200464.5993
27 | 2599252.3912 | 1200461.9415
28 | 2599244.298 | 1200450.3141
29 | 2599258.5049 | 1200493.9352
30 | 2599253.9068 | 1200446.4222
31 | 2599340.7429 | 1200570.3226
32 | 2599331.6806 | 1200546.1018
33 | 2599273.781 | 1200521.0643
34 | 2599273.0731 | 1200519.3569
35 | 2599360.7259 | 1200587.1054
36 | 2599355.0734 | 1200561.7737
37 | 2599295.7709 | 1200428.9468
38 | 2599288.4252 | 1200446.8804
39 | 2599270.1979 | 1200521.8824
40 | 2599265.0912 | 1200509.5704
41 | 2599339.9915 | 1200518.1836
42 | 2599338.7983 | 1200541.6925
43 | 2599254.5387 | 1200475.3699
44 | 2599267.7212 | 1200455.5145
45 | 2599262.7113 | 1200442.7469
46 | 2599345.3974 | 1200567.5469
47 | 2599350.0855 | 1200564.7497
48 | 2599318.1801 | 1200509.5584
49 | 2599262.0401 | 1200492.9932
50 | 2599265.5775 | 1200501.3037
51 | 2599283.4843 | 1200434.0756
52 | 2599271.2029 | 1200439.2022
53 | 2599313.2383 | 1200436.5642

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1