## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_351-411_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_351-411_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_351-411_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_351-411_0_8_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_351-411_0_8_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_351-411_0_8_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_351-411_0_8_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_351-411_0_8_node_76 | 0.4 | n |  | TRUE
8 | bus_LV_351-411_0_8_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_351-411_0_8_node_10 | 0.4 | n |  | TRUE
10 | bus_LV_351-411_0_8_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_351-411_0_8_node_58 | 0.4 | n |  | TRUE
12 | bus_LV_351-411_0_8_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_351-411_0_8_node_64 | 0.4 | n |  | TRUE
14 | bus_LV_351-411_0_8_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_351-411_0_8_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_351-411_0_8_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_351-411_0_8_node_62 | 0.4 | n |  | TRUE
18 | bus_LV_351-411_0_8_node_65 | 0.4 | n |  | TRUE
19 | bus_LV_351-411_0_8_node_5 | 0.4 | n |  | TRUE
20 | bus_LV_351-411_0_8_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_351-411_0_8_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_351-411_0_8_node_61 | 0.4 | n |  | TRUE
23 | bus_LV_351-411_0_8_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_351-411_0_8_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_351-411_0_8_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_351-411_0_8_node_90 | 0.4 | n |  | TRUE
27 | bus_LV_351-411_0_8_node_91 | 0.4 | n |  | TRUE
28 | bus_LV_351-411_0_8_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_351-411_0_8_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_351-411_0_8_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_351-411_0_8_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_351-411_0_8_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_351-411_0_8_node_17 | 0.4 | n |  | TRUE
34 | bus_LV_351-411_0_8_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_351-411_0_8_node_89 | 0.4 | n |  | TRUE
36 | bus_LV_351-411_0_8_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_351-411_0_8_node_98 | 0.4 | n |  | TRUE
38 | bus_LV_351-411_0_8_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_351-411_0_8_node_50 | 0.4 | n |  | TRUE
40 | bus_LV_351-411_0_8_node_68 | 0.4 | n |  | TRUE
41 | bus_LV_351-411_0_8_node_56 | 0.4 | n |  | TRUE
42 | bus_LV_351-411_0_8_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_351-411_0_8_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_351-411_0_8_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_351-411_0_8_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_351-411_0_8_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_351-411_0_8_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_351-411_0_8_node_96 | 0.4 | n |  | TRUE
49 | bus_LV_351-411_0_8_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_351-411_0_8_node_3 | 0.4 | n |  | TRUE
51 | bus_LV_351-411_0_8_node_77 | 0.4 | n |  | TRUE
52 | bus_LV_351-411_0_8_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_351-411_0_8_node_59 | 0.4 | n |  | TRUE
54 | bus_LV_351-411_0_8_node_88 | 0.4 | n |  | TRUE
55 | bus_LV_351-411_0_8_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_351-411_0_8_node_63 | 0.4 | n |  | TRUE
57 | bus_LV_351-411_0_8_node_81 | 0.4 | n |  | TRUE
58 | bus_LV_351-411_0_8_node_54 | 0.4 | n |  | TRUE
59 | bus_LV_351-411_0_8_node_92 | 0.4 | n |  | TRUE
60 | bus_LV_351-411_0_8_node_93 | 0.4 | n |  | TRUE
61 | bus_LV_351-411_0_8_node_99 | 0.4 | n |  | TRUE
62 | bus_LV_351-411_0_8_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_351-411_0_8_node_31 | 0.4 | n |  | TRUE
64 | bus_LV_351-411_0_8_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_351-411_0_8_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_351-411_0_8_node_75 | 0.4 | n |  | TRUE
67 | bus_LV_351-411_0_8_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_351-411_0_8_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_351-411_0_8_node_27 | 0.4 | n |  | TRUE
70 | bus_LV_351-411_0_8_node_34 | 0.4 | n |  | TRUE
71 | bus_LV_351-411_0_8_node_33 | 0.4 | n |  | TRUE
72 | bus_LV_351-411_0_8_node_35 | 0.4 | n |  | TRUE
73 | bus_LV_351-411_0_8_node_36 | 0.4 | n |  | TRUE
74 | bus_LV_351-411_0_8_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_351-411_0_8_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_351-411_0_8_node_53 | 0.4 | n |  | TRUE
77 | bus_LV_351-411_0_8_node_49 | 0.4 | n |  | TRUE
78 | bus_LV_351-411_0_8_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_351-411_0_8_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_351-411_0_8_node_80 | 0.4 | n |  | TRUE
81 | bus_LV_351-411_0_8_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_351-411_0_8_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_351-411_0_8_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_351-411_0_8_node_70 | 0.4 | n |  | TRUE
85 | bus_LV_351-411_0_8_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_351-411_0_8_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_351-411_0_8_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_351-411_0_8_node_82 | 0.4 | n |  | TRUE
89 | bus_LV_351-411_0_8_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_351-411_0_8_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_351-411_0_8_node_85 | 0.4 | n |  | TRUE
92 | bus_LV_351-411_0_8_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_351-411_0_8_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_351-411_0_8_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_351-411_0_8_node_100 | 0.4 | n |  | TRUE
96 | bus_LV_351-411_0_8_node_97 | 0.4 | n |  | TRUE
97 | bus_MV_604_0_node_120 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_351-411_0_8_load_0 | 0 | 0.0097497 | 0.0024435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_351-411_0_8_load_1 | 1 | 0.025131 | 0.0062983 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_351-411_0_8_load_76 | 7 | 0.0028812 | 0.0007221 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_351-411_0_8_load_30 | 10 | 0.0013018 | 0.00032627 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_351-411_0_8_load_58 | 11 | 0.0055573 | 0.0013928 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_351-411_0_8_load_64 | 13 | 0.0030204 | 0.00075698 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_351-411_0_8_load_42 | 14 | 0.0030448 | 0.0007631 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_351-411_0_8_load_32 | 16 | 0.014243 | 0.0035697 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_351-411_0_8_load_62 | 17 | 0.0076252 | 0.001911 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_351-411_0_8_load_65 | 18 | 0.0039057 | 0.00097886 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_351-411_0_8_load_61 | 22 | 0.0056866 | 0.0014252 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_351-411_0_8_load_78 | 24 | 0.003438 | 0.00086165 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_351-411_0_8_load_55 | 25 | 0.0043183 | 0.0010823 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_351-411_0_8_load_90 | 26 | 0.0099154 | 0.002485 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_351-411_0_8_load_45 | 30 | 0.034347 | 0.0086082 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_351-411_0_8_load_44 | 32 | 0.02094 | 0.005248 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_351-411_0_8_load_89 | 35 | 0.046302 | 0.011604 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_351-411_0_8_load_98 | 37 | 0.0087484 | 0.0021925 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_351-411_0_8_load_68 | 40 | 0.014817 | 0.0037135 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_351-411_0_8_load_60 | 42 | 0.0056845 | 0.0014247 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_351-411_0_8_load_41 | 43 | 0.0025198 | 0.00063152 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_351-411_0_8_load_40 | 44 | 0.0025215 | 0.00063194 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_351-411_0_8_load_43 | 47 | 0.0025886 | 0.00064877 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_351-411_0_8_load_96 | 48 | 0.0066122 | 0.0016572 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_351-411_0_8_load_46 | 49 | 0.019306 | 0.0048386 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_351-411_0_8_load_3 | 50 | 0.071001 | 0.017795 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_351-411_0_8_load_77 | 51 | 0.0028674 | 0.00071865 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_351-411_0_8_load_28 | 52 | 0.0013013 | 0.00032613 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_351-411_0_8_load_59 | 53 | 0.0032277 | 0.00080893 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_351-411_0_8_load_88 | 54 | 0.003081 | 0.00077217 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_351-411_0_8_load_63 | 56 | 0.0075651 | 0.001896 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_351-411_0_8_load_81 | 57 | 0.0030143 | 0.00075545 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_351-411_0_8_load_54 | 58 | 0.0040977 | 0.001027 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_351-411_0_8_load_92 | 59 | 0.009808 | 0.0024581 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_351-411_0_8_load_99 | 61 | 0.008288 | 0.0020772 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_351-411_0_8_load_48 | 64 | 0.010106 | 0.0025327 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_351-411_0_8_load_75 | 66 | 0.0025196 | 0.00063147 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_351-411_0_8_load_52 | 67 | 0.0025898 | 0.00064907 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_351-411_0_8_load_47 | 68 | 0.0066151 | 0.0016579 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_351-411_0_8_load_27 | 69 | 0.0091962 | 0.0023048 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_351-411_0_8_load_34 | 70 | 0.0090449 | 0.0022669 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_351-411_0_8_load_33 | 71 | 0.0093015 | 0.0023312 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_351-411_0_8_load_35 | 72 | 0.0052437 | 0.0013142 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_351-411_0_8_load_36 | 73 | 0.013674 | 0.003427 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_351-411_0_8_load_39 | 74 | 0.0097987 | 0.0024558 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_351-411_0_8_load_74 | 75 | 0.003102 | 0.00077743 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_351-411_0_8_load_53 | 76 | 0.0025872 | 0.00064842 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_351-411_0_8_load_49 | 77 | 0.0088699 | 0.002223 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_351-411_0_8_load_51 | 78 | 0.00069574 | 0.00017437 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_351-411_0_8_load_66 | 79 | 0.0044008 | 0.0011029 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_351-411_0_8_load_80 | 80 | 0.0025893 | 0.00064893 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_351-411_0_8_load_79 | 81 | 0.0025904 | 0.00064921 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_351-411_0_8_load_69 | 82 | 0.0016463 | 0.00041261 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_351-411_0_8_load_72 | 83 | 0.0019238 | 0.00048215 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_351-411_0_8_load_70 | 84 | 0.0016464 | 0.00041262 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_351-411_0_8_load_87 | 85 | 0.0030228 | 0.0007576 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_351-411_0_8_load_71 | 86 | 0.0016472 | 0.00041283 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_351-411_0_8_load_73 | 87 | 0.0016474 | 0.00041289 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_351-411_0_8_load_83 | 89 | 0.0030423 | 0.00076247 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_351-411_0_8_load_85 | 91 | 0.0031945 | 0.00080062 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_351-411_0_8_load_94 | 92 | 0.012886 | 0.0032295 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_351-411_0_8_load_86 | 94 | 0.0031216 | 0.00078234 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_351-411_0_8_load_100 | 95 | 0.014719 | 0.0036889 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_351-411_0_8_load_97 | 96 | 0.0099842 | 0.0025023 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_351-411_0_8_line_0 |  | 0 | 1 | 0.021437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_351-411_0_8_line_1 |  | 1 | 2 | 0.030277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_351-411_0_8_line_2 |  | 2 | 3 | 0.26233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_351-411_0_8_line_3 |  | 2 | 4 | 0.278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_351-411_0_8_line_4 |  | 3 | 18 | 0.028889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_351-411_0_8_line_5 |  | 3 | 19 | 0.017055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_351-411_0_8_line_6 |  | 4 | 26 | 0.004698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_351-411_0_8_line_7 |  | 4 | 27 | 0.015059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_351-411_0_8_line_8 |  | 4 | 28 | 0.07661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_351-411_0_8_line_9 |  | 5 | 6 | 0.015618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_351-411_0_8_line_10 |  | 5 | 7 | 0.009079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_351-411_0_8_line_11 |  | 6 | 43 | 0.013145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_351-411_0_8_line_12 |  | 6 | 44 | 0.0071965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_351-411_0_8_line_13 |  | 7 | 51 | 0.0073436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_351-411_0_8_line_14 |  | 8 | 9 | 0.033108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_351-411_0_8_line_15 |  | 8 | 10 | 0.0099771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_351-411_0_8_line_16 |  | 9 | 11 | 0.050554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_351-411_0_8_line_17 |  | 10 | 52 | 0.014283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_351-411_0_8_line_18 |  | 11 | 53 | 0.035517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_351-411_0_8_line_19 |  | 12 | 13 | 0.013545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_351-411_0_8_line_20 |  | 12 | 14 | 0.010221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_351-411_0_8_line_21 |  | 12 | 15 | 0.011788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_351-411_0_8_line_22 |  | 12 | 16 | 0.015925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_351-411_0_8_line_23 |  | 13 | 54 | 0.006344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_351-411_0_8_line_24 |  | 15 | 17 | 0.015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_351-411_0_8_line_25 |  | 16 | 55 | 0.0324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_351-411_0_8_line_26 |  | 17 | 56 | 0.01656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_351-411_0_8_line_27 |  | 19 | 50 | 0.0079174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_351-411_0_8_line_28 |  | 20 | 21 | 0.028529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_351-411_0_8_line_29 |  | 20 | 22 | 0.028487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_351-411_0_8_line_30 |  | 21 | 35 | 0.01032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_351-411_0_8_line_31 |  | 21 | 28 | 0.080636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_351-411_0_8_line_32 |  | 22 | 42 | 0.017678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_351-411_0_8_line_33 |  | 23 | 24 | 0.019742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_351-411_0_8_line_34 |  | 23 | 25 | 0.014311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_351-411_0_8_line_35 |  | 24 | 57 | 0.0066991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_351-411_0_8_line_36 |  | 25 | 58 | 0.0148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_351-411_0_8_line_37 |  | 27 | 59 | 0.004344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_351-411_0_8_line_38 |  | 27 | 60 | 0.014722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_351-411_0_8_line_39 |  | 28 | 36 | 0.015801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_351-411_0_8_line_40 |  | 28 | 37 | 0.002038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_351-411_0_8_line_41 |  | 29 | 30 | 0.005419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_351-411_0_8_line_42 |  | 29 | 31 | 0.035759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_351-411_0_8_line_43 |  | 29 | 32 | 0.034881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_351-411_0_8_line_44 |  | 31 | 41 | 0.027416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_351-411_0_8_line_45 |  | 31 | 42 | 0.012132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_351-411_0_8_line_46 |  | 32 | 33 | 0.039841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_351-411_0_8_line_47 |  | 33 | 34 | 0.002559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_351-411_0_8_line_48 |  | 34 | 49 | 0.025621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_351-411_0_8_line_49 |  | 36 | 61 | 0.002312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_351-411_0_8_line_50 |  | 36 | 62 | 0.014923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_351-411_0_8_line_51 |  | 38 | 39 | 0.04301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_351-411_0_8_line_52 |  | 38 | 40 | 0.0099612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_351-411_0_8_line_53 |  | 39 | 63 | 0.016006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_351-411_0_8_line_54 |  | 39 | 64 | 0.011009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_351-411_0_8_line_55 |  | 41 | 65 | 0.0037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_351-411_0_8_line_56 |  | 41 | 58 | 0.011929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_351-411_0_8_line_57 |  | 43 | 66 | 0.0063423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_351-411_0_8_line_58 |  | 44 | 45 | 0.025825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_351-411_0_8_line_59 |  | 45 | 46 | 0.036505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_351-411_0_8_line_60 |  | 45 | 47 | 0.0075734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_351-411_0_8_line_61 |  | 46 | 48 | 0.011913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_351-411_0_8_line_62 |  | 47 | 67 | 0.0085345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_351-411_0_8_line_63 |  | 49 | 68 | 0.015876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_351-411_0_8_line_64 |  | 52 | 69 | 0.014286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_351-411_0_8_line_65 |  | 54 | 85 | 0.0068224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_351-411_0_8_line_66 |  | 55 | 63 | 0.018049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_351-411_0_8_line_67 |  | 55 | 69 | 0.012062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_351-411_0_8_line_68 |  | 57 | 88 | 0.0030592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_351-411_0_8_line_69 |  | 60 | 96 | 0.004128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_351-411_0_8_line_70 |  | 62 | 74 | 0.001979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_351-411_0_8_line_71 |  | 62 | 73 | 0.0059145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_351-411_0_8_line_72 |  | 63 | 70 | 0.01219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_351-411_0_8_line_73 |  | 64 | 77 | 0.014871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_351-411_0_8_line_74 |  | 65 | 82 | 0.016954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_351-411_0_8_line_75 |  | 66 | 75 | 0.0063449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_351-411_0_8_line_76 |  | 67 | 76 | 0.0085347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_351-411_0_8_line_77 |  | 70 | 71 | 0.014799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_351-411_0_8_line_78 |  | 71 | 72 | 0.00021191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_351-411_0_8_line_79 |  | 75 | 87 | 0.0063442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_351-411_0_8_line_80 |  | 76 | 80 | 0.0085358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_351-411_0_8_line_81 |  | 77 | 78 | 0.013068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_351-411_0_8_line_82 |  | 78 | 79 | 0.00087142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_351-411_0_8_line_83 |  | 80 | 81 | 0.0085351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_351-411_0_8_line_84 |  | 81 | 83 | 0.008533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_351-411_0_8_line_85 |  | 82 | 84 | 0.0063426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_351-411_0_8_line_86 |  | 84 | 86 | 0.0063441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_351-411_0_8_line_87 |  | 85 | 94 | 0.0063311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_351-411_0_8_line_88 |  | 86 | 87 | 0.0063465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_351-411_0_8_line_89 |  | 88 | 89 | 0.0033986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_351-411_0_8_line_90 |  | 88 | 90 | 0.016052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_351-411_0_8_line_91 |  | 89 | 91 | 0.0057729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_351-411_0_8_line_92 |  | 90 | 92 | 0.009576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_351-411_0_8_line_93 |  | 90 | 93 | 0.01532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_351-411_0_8_line_94 |  | 91 | 94 | 0.0064947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_351-411_0_8_line_95 |  | 93 | 95 | 0.010638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_351-411_0_8_trafo_14 | 0.63 MVA 20/0.4 kV | 97 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2597203.9553 | 1198867.8587 | 2597186.9459 | 1198854.8117
1 | 2597167.0085 | 1198873.7517 | 2597172.5027 | 1198867.2122 | 2597184.4955 | 1198852.9321 | 2597186.9459 | 1198854.8117
2 | 2597047.6695 | 1198700.1848 | 2597031.6047 | 1198717.4688 | 2597009.4972 | 1198740.7259 | 2597019.5906 | 1198749.67 | 2597024.2595 | 1198752.4246 | 2597043.3034 | 1198768.9126 | 2597054.2643 | 1198777.1559 | 2597091.0644 | 1198809.3324 | 2597116.7805 | 1198831.2647 | 2597141.6802 | 1198849.918 | 2597159.1307 | 1198863.7057 | 2597162.5367 | 1198868.8512 | 2597167.0085 | 1198873.7517
3 | 2597088.7695 | 1198879.4377 | 2597107.7487 | 1198874.2477 | 2597131.1588 | 1198898.9383 | 2597136.3846 | 1198904.1385 | 2597139.8505 | 1198907.3051 | 2597160.4488 | 1198927.8838 | 2597165.1718 | 1198932.7174 | 2597168.4093 | 1198936.0288 | 2597177.0021 | 1198944.707 | 2597191.8413 | 1198959.6967 | 2597193.0589 | 1198958.4733 | 2597202.0998 | 1198949.2418 | 2597229.4788 | 1198915.5662 | 2597230.468 | 1198914.3429 | 2597214.2066 | 1198902.6999 | 2597209.1566 | 1198898.8559 | 2597206.2174 | 1198898.3459 | 2597203.6066 | 1198900.0703 | 2597195.3906 | 1198899.0292 | 2597172.783 | 1198880.0634 | 2597167.0085 | 1198873.7517
4 | 2597047.6695 | 1198700.1848 | 2597063.0881 | 1198684.4352 | 2597064.9597 | 1198681.4994 | 2597066.0015 | 1198678.7752 | 2597066.0597 | 1198678.3291
5 | 2597060.1856 | 1198711.8069 | 2597047.6695 | 1198700.1848
6 | 2597088.7695 | 1198879.4377 | 2597086.9019 | 1198875.1252
7 | 2597088.7695 | 1198879.4377 | 2597074.6329 | 1198884.7365
8 | 2597088.7695 | 1198879.4377 | 2597107.7487 | 1198874.2477 | 2597078.0315 | 1198844.5356 | 2597071.074 | 1198848.0409 | 2597064.7102 | 1198851.2347
9 | 2596886.0369 | 1198833.8403 | 2596889.0588 | 1198832.1822 | 2596883.8625 | 1198825.726 | 2596887.1203 | 1198823.612
10 | 2596886.0369 | 1198833.8403 | 2596878.088 | 1198838.2269
11 | 2596887.1203 | 1198823.612 | 2596898.1966 | 1198816.5336
12 | 2596887.1203 | 1198823.612 | 2596883.6994 | 1198819.645 | 2596882.4787 | 1198818.1138
13 | 2596878.088 | 1198838.2269 | 2596871.6584 | 1198841.775
14 | 2596975.5989 | 1198931.79 | 2596976.3152 | 1198932.9347 | 2596984.8876 | 1198945.8149 | 2596991.6015 | 1198957.5733 | 2596992.0434 | 1198958.0733 | 2596992.5538 | 1198958.4955 | 2596993.1326 | 1198958.8732 | 2596993.7876 | 1198959.1842
15 | 2596975.5989 | 1198931.79 | 2596969.3384 | 1198924.0216
16 | 2596993.7876 | 1198959.1842 | 2596994.3816 | 1198959.3728 | 2596995.0136 | 1198959.4948 | 2596995.775 | 1198959.5389 | 2596996.6277 | 1198959.494 | 2596997.3738 | 1198959.3379 | 2596998.0894 | 1198959.0152 | 2597038.7969 | 1198937.3292
17 | 2596969.3384 | 1198924.0216 | 2596960.3762 | 1198912.9006
18 | 2597038.7969 | 1198937.3292 | 2597046.4247 | 1198933.2656 | 2597059.183 | 1198927.7451 | 2597071.2182 | 1198922.9031
19 | 2596912.9488 | 1198855.2263 | 2596923.4834 | 1198849.0841 | 2596924.6057 | 1198848.3335
20 | 2596912.9488 | 1198855.2263 | 2596906.5149 | 1198847.2843
21 | 2596903.7358 | 1198855.3646 | 2596906.8415 | 1198853.6398 | 2596909.0662 | 1198856.3512 | 2596909.691 | 1198857.0957 | 2596912.9488 | 1198855.2263
22 | 2596912.9488 | 1198855.2263 | 2596923.1295 | 1198867.4715
23 | 2596929.8791 | 1198844.8066 | 2596924.6057 | 1198848.3335
24 | 2596903.7358 | 1198855.3646 | 2596890.532 | 1198862.697
25 | 2596943.8433 | 1198892.3855 | 2596923.1295 | 1198867.4715
26 | 2596890.532 | 1198862.697 | 2596876.0547 | 1198870.7365
27 | 2597060.1856 | 1198711.8069 | 2597065.9496 | 1198717.2347
28 | 2597008.7867 | 1198780.592 | 2597015.437 | 1198786.6252 | 2597029.8268 | 1198799.8582
29 | 2597008.7867 | 1198780.592 | 2597007.8735 | 1198781.5263 | 2596997.1128 | 1198792.6823 | 2596988.479 | 1198784.8157
30 | 2597021.1039 | 1198805.4101 | 2597022.5958 | 1198804.4644 | 2597025.1533 | 1198802.84 | 2597029.8268 | 1198799.8582
31 | 2597029.8268 | 1198799.8582 | 2597042.3884 | 1198811.4136 | 2597047.2942 | 1198815.9246 | 2597053.1902 | 1198821.3468 | 2597054.8204 | 1198822.8467 | 2597078.0315 | 1198844.5356 | 2597071.074 | 1198848.0409 | 2597064.7102 | 1198851.2347
32 | 2596975.4115 | 1198772.9095 | 2596988.479 | 1198784.8157
33 | 2596977.9046 | 1198811.7357 | 2596961.5436 | 1198822.7848
34 | 2596977.9046 | 1198811.7357 | 2596976.0916 | 1198810.1247 | 2596967.2261 | 1198802.2079
35 | 2596961.5436 | 1198822.7848 | 2596955.9919 | 1198826.534
36 | 2596956.1867 | 1198792.3497 | 2596967.2261 | 1198802.2079
37 | 2597073.1081 | 1198880.6685 | 2597074.6329 | 1198884.7365
38 | 2597074.6329 | 1198884.7365 | 2597060.8619 | 1198890.0463
39 | 2597064.7102 | 1198851.2347 | 2597050.5593 | 1198858.3457
40 | 2597063.8184 | 1198849.4009 | 2597064.7102 | 1198851.2347
41 | 2596964.1466 | 1198739.9934 | 2596960.9053 | 1198744.3418
42 | 2596964.1466 | 1198739.9934 | 2596974.4002 | 1198749.4042 | 2596978.1939 | 1198752.8374 | 2596966.4438 | 1198764.7388
43 | 2596964.1466 | 1198739.9934 | 2596938.4617 | 1198716.3933
44 | 2596947.2892 | 1198784.4037 | 2596966.4438 | 1198764.7388
45 | 2596966.4438 | 1198764.7388 | 2596975.4115 | 1198772.9095
46 | 2596909.2061 | 1198689.3507 | 2596913.3352 | 1198693.3062 | 2596938.4617 | 1198716.3933
47 | 2596907.0597 | 1198690.7526 | 2596909.2061 | 1198689.3507
48 | 2596907.0597 | 1198690.7526 | 2596909.14 | 1198693.842 | 2596912.4472 | 1198698.8207 | 2596899.0021 | 1198707.3439
49 | 2597049.5912 | 1198856.245 | 2597050.5593 | 1198858.3457
50 | 2597050.5593 | 1198858.3457 | 2597037.1924 | 1198865.056
51 | 2597004.8652 | 1198854.2001 | 2597006.0232 | 1198855.5224 | 2597006.9298 | 1198856.6114 | 2596972.9667 | 1198877.429
52 | 2597004.8652 | 1198854.2001 | 2597000.5799 | 1198856.9037 | 2596999.8255 | 1198855.7479 | 2596996.8777 | 1198857.6609
53 | 2596957.4585 | 1198880.4942 | 2596964.4394 | 1198878.2783 | 2596969.7762 | 1198876.9526 | 2596972.9667 | 1198877.429
54 | 2596972.9667 | 1198877.429 | 2596977.5379 | 1198882.6961 | 2596980.091 | 1198885.8201
55 | 2596944.557 | 1198786.9065 | 2596947.2892 | 1198784.4037
56 | 2596947.2892 | 1198784.4037 | 2596949.864 | 1198786.7036 | 2596956.1867 | 1198792.3497
57 | 2596903.5408 | 1198813.1183 | 2596898.1966 | 1198816.5336
58 | 2596866.3809 | 1198797.9205 | 2596882.4787 | 1198818.1138
59 | 2596866.3809 | 1198797.9205 | 2596843.0207 | 1198769.818
60 | 2596866.3809 | 1198797.9205 | 2596872.7447 | 1198793.8146
61 | 2596849.0852 | 1198762.4219 | 2596850.541 | 1198765.1115 | 2596843.2567 | 1198769.6289 | 2596843.0207 | 1198769.818
62 | 2596872.7447 | 1198793.8146 | 2596879.9161 | 1198789.1878
63 | 2596885.5932 | 1198715.8441 | 2596899.0021 | 1198707.3439
64 | 2596951.4121 | 1198901.7774 | 2596960.3762 | 1198912.9006
65 | 2596935.538 | 1198840.9965 | 2596935.1593 | 1198841.2738 | 2596932.0006 | 1198843.3877 | 2596929.8791 | 1198844.8066
66 | 2596943.8433 | 1198892.3855 | 2596957.4585 | 1198880.4942
67 | 2596943.8433 | 1198892.3855 | 2596951.4121 | 1198901.7774
68 | 2596953.4567 | 1198828.2461 | 2596955.9919 | 1198826.534
69 | 2597059.3599 | 1198886.2006 | 2597060.8619 | 1198890.0463
70 | 2597036.3007 | 1198863.2889 | 2597037.1924 | 1198865.056
71 | 2597037.1924 | 1198865.056 | 2597031.9096 | 1198867.7157
72 | 2596957.4585 | 1198880.4942 | 2596957.38 | 1198875.9807 | 2596952.446 | 1198870.1002
73 | 2596980.091 | 1198885.8201 | 2596989.5014 | 1198897.3346
74 | 2596944.557 | 1198786.9065 | 2596930.271 | 1198796.0361
75 | 2596908.8872 | 1198809.7016 | 2596903.5408 | 1198813.1183
76 | 2596887.0878 | 1198784.5608 | 2596879.9161 | 1198789.1878
77 | 2596952.446 | 1198870.1002 | 2596942.9339 | 1198858.7636
78 | 2596942.9339 | 1198858.7636 | 2596942.7977 | 1198858.6013
79 | 2596914.233 | 1198806.2853 | 2596908.8872 | 1198809.7016
80 | 2596894.2603 | 1198779.9332 | 2596887.0878 | 1198784.5608
81 | 2596989.5014 | 1198897.3346 | 2596997.7709 | 1198907.4532
82 | 2596998.3224 | 1198908.128 | 2596997.7709 | 1198907.4532
83 | 2596901.4322 | 1198775.306 | 2596894.2603 | 1198779.9332
84 | 2596908.6023 | 1198770.68 | 2596901.4322 | 1198775.306
85 | 2596930.271 | 1198796.0361 | 2596924.9265 | 1198799.4516
86 | 2596924.9265 | 1198799.4516 | 2596919.5808 | 1198802.8678
87 | 2596940.6463 | 1198837.2565 | 2596935.538 | 1198840.9965
88 | 2596919.5808 | 1198802.8678 | 2596914.233 | 1198806.2853
89 | 2596953.4567 | 1198828.2461 | 2596950.6057 | 1198830.0961
90 | 2596953.4567 | 1198828.2461 | 2596958.3869 | 1198835.5586 | 2596962.4407 | 1198841.5486
91 | 2596950.6057 | 1198830.0961 | 2596950.4045 | 1198830.2266 | 2596947.9232 | 1198831.9288 | 2596945.8867 | 1198833.4198
92 | 2596970.5851 | 1198836.475 | 2596968.9638 | 1198837.4763 | 2596967.1979 | 1198838.589 | 2596962.4407 | 1198841.5486
93 | 2596962.4407 | 1198841.5486 | 2596966.2659 | 1198847.2274 | 2596971.0055 | 1198854.2509
94 | 2596945.8867 | 1198833.4198 | 2596940.6463 | 1198837.2565
95 | 2596980.3072 | 1198849.0433 | 2596978.7239 | 1198849.9113 | 2596977.0645 | 1198850.8571 | 2596971.0055 | 1198854.2509

## bus_geodata
| x | y | coords
0 | 2597203.9553 | 1198867.8587
1 | 2597186.9459 | 1198854.8116
2 | 2597167.0085 | 1198873.7517
3 | 2597047.6695 | 1198700.1848
4 | 2597088.7695 | 1198879.4377
5 | 2596886.0369 | 1198833.8403
6 | 2596887.1203 | 1198823.612
7 | 2596878.088 | 1198838.2269
8 | 2596975.5989 | 1198931.79
9 | 2596993.7876 | 1198959.1842
10 | 2596969.3384 | 1198924.0216
11 | 2597038.7969 | 1198937.3292
12 | 2596912.9488 | 1198855.2263
13 | 2596924.6057 | 1198848.3335
14 | 2596906.5149 | 1198847.2843
15 | 2596903.7358 | 1198855.3646
16 | 2596923.1295 | 1198867.4715
17 | 2596890.532 | 1198862.697
18 | 2597066.0597 | 1198678.3291
19 | 2597060.1856 | 1198711.8069
20 | 2597008.7867 | 1198780.592
21 | 2597029.8268 | 1198799.8582
22 | 2596988.479 | 1198784.8157
23 | 2596977.9046 | 1198811.7357
24 | 2596961.5436 | 1198822.7848
25 | 2596967.2261 | 1198802.2079
26 | 2597086.9019 | 1198875.1252
27 | 2597074.6329 | 1198884.7365
28 | 2597064.7102 | 1198851.2347
29 | 2596964.1466 | 1198739.9934
30 | 2596960.9053 | 1198744.3418
31 | 2596966.4438 | 1198764.7388
32 | 2596938.4617 | 1198716.3933
33 | 2596909.2061 | 1198689.3507
34 | 2596907.0597 | 1198690.7526
35 | 2597021.1039 | 1198805.4101
36 | 2597050.5593 | 1198858.3457
37 | 2597063.8184 | 1198849.4009
38 | 2597004.8652 | 1198854.2001
39 | 2596972.9667 | 1198877.429
40 | 2596996.8777 | 1198857.6609
41 | 2596947.2892 | 1198784.4037
42 | 2596975.4115 | 1198772.9095
43 | 2596898.1966 | 1198816.5335
44 | 2596882.4787 | 1198818.1138
45 | 2596866.3809 | 1198797.9205
46 | 2596843.0207 | 1198769.818
47 | 2596872.7447 | 1198793.8146
48 | 2596849.0852 | 1198762.4219
49 | 2596899.0021 | 1198707.3439
50 | 2597065.9496 | 1198717.2347
51 | 2596871.6584 | 1198841.775
52 | 2596960.3762 | 1198912.9006
53 | 2597071.2182 | 1198922.9031
54 | 2596929.8791 | 1198844.8066
55 | 2596943.8433 | 1198892.3855
56 | 2596876.0547 | 1198870.7365
57 | 2596955.9919 | 1198826.534
58 | 2596956.1867 | 1198792.3497
59 | 2597073.1081 | 1198880.6685
60 | 2597060.8619 | 1198890.0463
61 | 2597049.5912 | 1198856.245
62 | 2597037.1924 | 1198865.056
63 | 2596957.4585 | 1198880.4942
64 | 2596980.091 | 1198885.8201
65 | 2596944.557 | 1198786.9065
66 | 2596903.5408 | 1198813.1183
67 | 2596879.9161 | 1198789.1878
68 | 2596885.5932 | 1198715.8441
69 | 2596951.4121 | 1198901.7774
70 | 2596952.446 | 1198870.1002
71 | 2596942.9339 | 1198858.7636
72 | 2596942.7977 | 1198858.6013
73 | 2597031.9096 | 1198867.7157
74 | 2597036.3007 | 1198863.2889
75 | 2596908.8872 | 1198809.7016
76 | 2596887.0878 | 1198784.5608
77 | 2596989.5014 | 1198897.3346
78 | 2596997.7709 | 1198907.4532
79 | 2596998.3224 | 1198908.128
80 | 2596894.2603 | 1198779.9332
81 | 2596901.4322 | 1198775.306
82 | 2596930.271 | 1198796.0361
83 | 2596908.6023 | 1198770.68
84 | 2596924.9265 | 1198799.4516
85 | 2596935.538 | 1198840.9965
86 | 2596919.5808 | 1198802.8678
87 | 2596914.233 | 1198806.2853
88 | 2596953.4567 | 1198828.2461
89 | 2596950.6057 | 1198830.0961
90 | 2596962.4407 | 1198841.5486
91 | 2596945.8867 | 1198833.4198
92 | 2596970.5851 | 1198836.475
93 | 2596971.0055 | 1198854.2509
94 | 2596940.6463 | 1198837.2565
95 | 2596980.3072 | 1198849.0433
96 | 2597059.3599 | 1198886.2006
97 | 2596953.4567 | 1198828.2461

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1