## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_351-435_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_351-435_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_351-435_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_351-435_0_3_node_16 | 0.4 | n |  | TRUE
4 | bus_LV_351-435_0_3_node_61 | 0.4 | n |  | TRUE
5 | bus_LV_351-435_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_351-435_0_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_351-435_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_351-435_0_3_node_48 | 0.4 | n |  | TRUE
9 | bus_LV_351-435_0_3_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_351-435_0_3_node_60 | 0.4 | n |  | TRUE
11 | bus_LV_351-435_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_351-435_0_3_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_351-435_0_3_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_351-435_0_3_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_351-435_0_3_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_351-435_0_3_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_351-435_0_3_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_351-435_0_3_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_351-435_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_351-435_0_3_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_351-435_0_3_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_351-435_0_3_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_351-435_0_3_node_75 | 0.4 | n |  | TRUE
24 | bus_LV_351-435_0_3_node_73 | 0.4 | n |  | TRUE
25 | bus_LV_351-435_0_3_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_351-435_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_351-435_0_3_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_351-435_0_3_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_351-435_0_3_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_351-435_0_3_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_351-435_0_3_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_351-435_0_3_node_59 | 0.4 | n |  | TRUE
33 | bus_LV_351-435_0_3_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_351-435_0_3_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_351-435_0_3_node_76 | 0.4 | n |  | TRUE
36 | bus_LV_351-435_0_3_node_71 | 0.4 | n |  | TRUE
37 | bus_LV_351-435_0_3_node_69 | 0.4 | n |  | TRUE
38 | bus_LV_351-435_0_3_node_13 | 0.4 | n |  | TRUE
39 | bus_LV_351-435_0_3_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_351-435_0_3_node_17 | 0.4 | n |  | TRUE
41 | bus_LV_351-435_0_3_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_351-435_0_3_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_351-435_0_3_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_351-435_0_3_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_351-435_0_3_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_351-435_0_3_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_351-435_0_3_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_351-435_0_3_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_351-435_0_3_node_68 | 0.4 | n |  | TRUE
50 | bus_LV_351-435_0_3_node_66 | 0.4 | n |  | TRUE
51 | bus_LV_351-435_0_3_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_351-435_0_3_node_31 | 0.4 | n |  | TRUE
53 | bus_LV_351-435_0_3_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_351-435_0_3_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_351-435_0_3_node_37 | 0.4 | n |  | TRUE
56 | bus_LV_351-435_0_3_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_351-435_0_3_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_351-435_0_3_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_351-435_0_3_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_351-435_0_3_node_51 | 0.4 | n |  | TRUE
61 | bus_LV_351-435_0_3_node_52 | 0.4 | n |  | TRUE
62 | bus_LV_351-435_0_3_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_351-435_0_3_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_351-435_0_3_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_351-435_0_3_node_63 | 0.4 | n |  | TRUE
66 | bus_LV_351-435_0_3_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_351-435_0_3_node_56 | 0.4 | n |  | TRUE
68 | bus_LV_351-435_0_3_node_78 | 0.4 | n |  | TRUE
69 | bus_LV_351-435_0_3_node_67 | 0.4 | n |  | TRUE
70 | bus_LV_351-435_0_3_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_351-435_0_3_node_77 | 0.4 | n |  | TRUE
72 | bus_MV_605_0_node_15 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_351-435_0_3_load_0 | 0 | 0.04214 | 0.010561 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_351-435_0_3_load_61 | 4 | 0.0021198 | 0.00053128 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_351-435_0_3_load_23 | 6 | 0.0046652 | 0.0011692 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_351-435_0_3_load_48 | 8 | 0.0018505 | 0.00046378 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_351-435_0_3_load_60 | 10 | 0.0017114 | 0.00042891 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_351-435_0_3_load_38 | 12 | 0.0023177 | 0.00058088 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_351-435_0_3_load_39 | 13 | 0.0037247 | 0.00093349 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_351-435_0_3_load_29 | 14 | 0.0018989 | 0.00047592 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_351-435_0_3_load_34 | 17 | 0.0026141 | 0.00065515 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_351-435_0_3_load_22 | 19 | 0.0030056 | 0.00075328 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_351-435_0_3_load_19 | 20 | 0.0071225 | 0.0017851 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_351-435_0_3_load_75 | 23 | 0.001021 | 0.00025589 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_351-435_0_3_load_21 | 25 | 0.0044821 | 0.0011233 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_351-435_0_3_load_14 | 26 | 0.0046386 | 0.0011625 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_351-435_0_3_load_25 | 27 | 0.0022057 | 0.00055281 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_351-435_0_3_load_24 | 28 | 0.0033539 | 0.00084057 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_351-435_0_3_load_32 | 29 | 0.0047175 | 0.0011823 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_351-435_0_3_load_33 | 30 | 0.0026232 | 0.00065743 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_351-435_0_3_load_28 | 31 | 0.0013108 | 0.00032853 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_351-435_0_3_load_59 | 32 | 0.0017091 | 0.00042833 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_351-435_0_3_load_35 | 33 | 0.0023269 | 0.00058317 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_351-435_0_3_load_20 | 34 | 0.0035418 | 0.00088765 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_351-435_0_3_load_76 | 35 | 0.013379 | 0.0033531 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_351-435_0_3_load_69 | 37 | 0.022355 | 0.0056026 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_351-435_0_3_load_13 | 38 | 0.0037758 | 0.00094629 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_351-435_0_3_load_17 | 40 | 0.0043477 | 0.0010896 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_351-435_0_3_load_18 | 41 | 0.0024309 | 0.00060923 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_351-435_0_3_load_40 | 42 | 0.002756 | 0.00069072 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_351-435_0_3_load_54 | 43 | 0.00377 | 0.00094486 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_351-435_0_3_load_41 | 44 | 0.007524 | 0.0018857 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_351-435_0_3_load_36 | 46 | 0.0027975 | 0.00070112 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_351-435_0_3_load_26 | 47 | 0.0046391 | 0.0011627 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_351-435_0_3_load_27 | 48 | 0.0033939 | 0.00085058 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_351-435_0_3_load_68 | 49 | 0.0031331 | 0.00078523 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_351-435_0_3_load_66 | 50 | 0.00052555 | 0.00013171 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_351-435_0_3_load_30 | 51 | 0.0023892 | 0.0005988 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_351-435_0_3_load_31 | 52 | 0.001955 | 0.00048996 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_351-435_0_3_load_46 | 53 | 0.0031898 | 0.00079945 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_351-435_0_3_load_44 | 54 | 0.0022843 | 0.00057249 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_351-435_0_3_load_37 | 55 | 0.0035635 | 0.00089311 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_351-435_0_3_load_50 | 56 | 0.0033328 | 0.00083527 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_351-435_0_3_load_53 | 57 | 0.0035665 | 0.00089385 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_351-435_0_3_load_42 | 58 | 0.0029376 | 0.00073622 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_351-435_0_3_load_43 | 59 | 0.0025294 | 0.00063392 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_351-435_0_3_load_51 | 60 | 0.0069015 | 0.0017297 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_351-435_0_3_load_52 | 61 | 0.0028288 | 0.00070896 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_351-435_0_3_load_45 | 62 | 0.0029815 | 0.00074723 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_351-435_0_3_load_47 | 63 | 0.003862 | 0.0009679 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_351-435_0_3_load_63 | 65 | 0.0081689 | 0.0020473 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_351-435_0_3_load_58 | 66 | 0.0017054 | 0.0004274 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_351-435_0_3_load_78 | 68 | 0.00051727 | 0.00012964 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_351-435_0_3_load_67 | 69 | 0.00030608 | 7.6711e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_351-435_0_3_load_70 | 70 | 0.030992 | 0.0077672 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_351-435_0_3_load_77 | 71 | 0.021114 | 0.0052918 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_351-435_0_3_line_0 |  | 0 | 1 | 0.013508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_351-435_0_3_line_1 |  | 1 | 2 | 0.049631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_351-435_0_3_line_2 |  | 2 | 3 | 0.003588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_351-435_0_3_line_3 |  | 2 | 4 | 0.01276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_351-435_0_3_line_4 |  | 3 | 25 | 0.016768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_351-435_0_3_line_5 |  | 3 | 26 | 0.034773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_351-435_0_3_line_6 |  | 5 | 6 | 0.032445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_351-435_0_3_line_7 |  | 5 | 7 | 0.24637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_351-435_0_3_line_8 |  | 5 | 8 | 0.010978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_351-435_0_3_line_9 |  | 6 | 18 | 0.033004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_351-435_0_3_line_10 |  | 7 | 9 | 0.081889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_351-435_0_3_line_11 |  | 8 | 12 | 0.028442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_351-435_0_3_line_12 |  | 9 | 10 | 0.05508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_351-435_0_3_line_13 |  | 10 | 16 | 0.014593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_351-435_0_3_line_14 |  | 11 | 12 | 0.014614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_351-435_0_3_line_15 |  | 11 | 13 | 0.057035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_351-435_0_3_line_16 |  | 11 | 14 | 0.013895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_351-435_0_3_line_17 |  | 13 | 22 | 0.0082269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_351-435_0_3_line_18 |  | 14 | 31 | 0.0082423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_351-435_0_3_line_19 |  | 15 | 16 | 0.00464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_351-435_0_3_line_20 |  | 15 | 17 | 0.014612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_351-435_0_3_line_21 |  | 16 | 32 | 0.0074049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_351-435_0_3_line_22 |  | 17 | 30 | 0.001656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_351-435_0_3_line_23 |  | 18 | 19 | 0.017078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_351-435_0_3_line_24 |  | 18 | 20 | 0.015498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_351-435_0_3_line_25 |  | 19 | 33 | 0.0070807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_351-435_0_3_line_26 |  | 20 | 34 | 0.026202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_351-435_0_3_line_27 |  | 21 | 22 | 0.013846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_351-435_0_3_line_28 |  | 21 | 23 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_351-435_0_3_line_29 |  | 22 | 24 | 0.004556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_351-435_0_3_line_30 |  | 24 | 35 | 0.025009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_351-435_0_3_line_31 |  | 24 | 36 | 0.011833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_351-435_0_3_line_32 |  | 25 | 34 | 0.010944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_351-435_0_3_line_33 |  | 26 | 38 | 0.01074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_351-435_0_3_line_34 |  | 27 | 28 | 0.017251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_351-435_0_3_line_35 |  | 28 | 47 | 0.025669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_351-435_0_3_line_36 |  | 29 | 30 | 0.022632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_351-435_0_3_line_37 |  | 31 | 51 | 0.024119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_351-435_0_3_line_38 |  | 32 | 66 | 0.01026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_351-435_0_3_line_39 |  | 33 | 46 | 0.018259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_351-435_0_3_line_40 |  | 35 | 71 | 0.1037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_351-435_0_3_line_41 |  | 36 | 37 | 0.057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_351-435_0_3_line_42 |  | 37 | 70 | 0.066925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_351-435_0_3_line_43 |  | 39 | 40 | 0.028476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_351-435_0_3_line_44 |  | 39 | 41 | 0.0075674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_351-435_0_3_line_45 |  | 40 | 42 | 0.0066392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_351-435_0_3_line_46 |  | 41 | 43 | 0.0062084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_351-435_0_3_line_47 |  | 42 | 44 | 0.0038338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_351-435_0_3_line_48 |  | 43 | 45 | 0.034429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_351-435_0_3_line_49 |  | 44 | 58 | 0.01955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_351-435_0_3_line_50 |  | 45 | 67 | 0.003414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_351-435_0_3_line_51 |  | 45 | 64 | 0.01899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_351-435_0_3_line_52 |  | 46 | 55 | 0.010478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_351-435_0_3_line_53 |  | 47 | 48 | 0.014804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_351-435_0_3_line_54 |  | 48 | 49 | 0.024789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_351-435_0_3_line_55 |  | 49 | 50 | 0.015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_351-435_0_3_line_56 |  | 50 | 69 | 0.013624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_351-435_0_3_line_57 |  | 51 | 52 | 0.013806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_351-435_0_3_line_58 |  | 52 | 53 | 0.017981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_351-435_0_3_line_59 |  | 53 | 54 | 0.0069914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_351-435_0_3_line_60 |  | 54 | 62 | 0.023147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_351-435_0_3_line_61 |  | 55 | 56 | 0.0072835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_351-435_0_3_line_62 |  | 56 | 57 | 0.002239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_351-435_0_3_line_63 |  | 57 | 61 | 0.0059523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_351-435_0_3_line_64 |  | 58 | 59 | 0.0066108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_351-435_0_3_line_65 |  | 59 | 60 | 0.0039907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_351-435_0_3_line_66 |  | 60 | 61 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_351-435_0_3_line_67 |  | 63 | 64 | 0.020958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_351-435_0_3_line_68 |  | 64 | 65 | 0.051282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_351-435_0_3_line_69 |  | 67 | 68 | 0.009448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_351-435_0_3_line_70 |  | 67 | 69 | 0.021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_351-435_0_3_trafo_42 | 0.63 MVA 20/0.4 kV | 72 | 58 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18
0 | 2595757.0315 | 1199165.927 | 2595753.9757 | 1199162.1494 | 2595748.5416 | 1199155.4207
1 | 2595718.6112 | 1199194.7481 | 2595721.602 | 1199192.945 | 2595722.4328 | 1199194.1672 | 2595743.3122 | 1199177.1318 | 2595757.0315 | 1199165.927
2 | 2595720.3418 | 1199197.893 | 2595718.6112 | 1199194.7481
3 | 2595718.6112 | 1199194.7481 | 2595712.4915 | 1199183.551
4 | 2595720.3418 | 1199197.893 | 2595723.512 | 1199202.004 | 2595730.9463 | 1199210.8785
5 | 2595720.3418 | 1199197.893 | 2595693.6144 | 1199213.821 | 2595690.4196 | 1199215.6066
6 | 2595805.8564 | 1199302.1649 | 2595785.48 | 1199276.9169
7 | 2595805.8564 | 1199302.1649 | 2595813.0696 | 1199296.0231 | 2595829.5588 | 1199282.9599 | 2595832.1342 | 1199285.893 | 2595848.2656 | 1199272.7523 | 2595855.3573 | 1199266.9331 | 2595894.7271 | 1199234.6548 | 2595943.1068 | 1199195.0221 | 2595940.8742 | 1199192.3667 | 2595942.4111 | 1199190.9316 | 2595942.662 | 1199190.3422 | 2595942.7834 | 1199189.7084 | 2595942.821 | 1199189.0858 | 2595942.7215 | 1199188.3633 | 2595942.485 | 1199187.5853 | 2595938.644 | 1199182.2184 | 2595919.6169 | 1199159.4416 | 2595908.2701 | 1199145.0418 | 2595905.1458 | 1199141.2753
8 | 2595805.8564 | 1199302.1649 | 2595800.1117 | 1199307.0605 | 2595797.4267 | 1199309.1952
9 | 2595764.7525 | 1199251.2338 | 2595785.48 | 1199276.9169
10 | 2595852.9094 | 1199078.2227 | 2595855.6449 | 1199081.289 | 2595858.8909 | 1199084.8553 | 2595902.5702 | 1199138.0976 | 2595905.1458 | 1199141.2753
11 | 2595797.4267 | 1199309.1952 | 2595775.1637 | 1199326.8954
12 | 2595852.9094 | 1199078.2227 | 2595812.2265 | 1199115.3532
13 | 2595802.4337 | 1199125.9063 | 2595802.8667 | 1199124.5719 | 2595803.4066 | 1199123.6377 | 2595804.2586 | 1199122.6254 | 2595812.2265 | 1199115.3532
14 | 2595763.5877 | 1199335.8133 | 2595770.0633 | 1199330.9504 | 2595775.1637 | 1199326.8954
15 | 2595763.5877 | 1199335.8133 | 2595758.1014 | 1199339.9305 | 2595754.7532 | 1199342.2898 | 2595750.1571 | 1199345.6282 | 2595716.4134 | 1199367.8422
16 | 2595763.5877 | 1199335.8133 | 2595749.7577 | 1199334.4672
17 | 2595709.4904 | 1199372.2832 | 2595711.1722 | 1199371.2925 | 2595716.4134 | 1199367.8422
18 | 2595741.5712 | 1199333.5257 | 2595744.8802 | 1199333.9925 | 2595749.7577 | 1199334.4672
19 | 2595802.4337 | 1199125.9063 | 2595807.0855 | 1199125.7695
20 | 2595807.0855 | 1199125.7695 | 2595806.7892 | 1199126.6147 | 2595806.6909 | 1199127.5486 | 2595806.7067 | 1199128.3045 | 2595806.8748 | 1199129.2271 | 2595807.1724 | 1199130.0829 | 2595807.6145 | 1199130.8608 | 2595813.496 | 1199138.0419
21 | 2595802.4337 | 1199125.9063 | 2595796.642 | 1199130.5204
22 | 2595813.496 | 1199138.0419 | 2595814.5452 | 1199139.323
23 | 2595764.7525 | 1199251.2338 | 2595751.4395 | 1199261.9315
24 | 2595764.7525 | 1199251.2338 | 2595754.8003 | 1199239.3536
25 | 2595751.4395 | 1199261.9315 | 2595745.92 | 1199266.3667
26 | 2595754.8003 | 1199239.3536 | 2595737.9743 | 1199219.268
27 | 2595711.1046 | 1199382.9655 | 2595711.2026 | 1199381.687 | 2595711.5823 | 1199380.2637 | 2595712.1523 | 1199378.9515 | 2595714.3129 | 1199376.7043 | 2595709.4904 | 1199372.2832
28 | 2595711.1046 | 1199382.9655 | 2595711.1895 | 1199384.4996 | 2595711.3962 | 1199386.1003 | 2595711.8695 | 1199387.8453 | 2595712.7235 | 1199389.6234 | 2595713.4935 | 1199390.9903 | 2595714.5605 | 1199392.6015 | 2595716.2293 | 1199394.5791 | 2595718.279 | 1199396.9233 | 2595718.6896 | 1199397.2689
29 | 2595709.4904 | 1199372.2832 | 2595708.3107 | 1199372.8621 | 2595707.3821 | 1199373.1963 | 2595706.324 | 1199373.4083 | 2595705.1441 | 1199373.5537
30 | 2595705.1441 | 1199373.5537 | 2595703.9564 | 1199373.6324 | 2595702.8219 | 1199373.5332 | 2595701.5808 | 1199373.3229 | 2595700.4462 | 1199373.0235 | 2595699.3572 | 1199372.613 | 2595697.8493 | 1199371.9915 | 2595690.0419 | 1199367.0724 | 2595688.6253 | 1199366.3953 | 2595686.95 | 1199365.9074 | 2595682.12 | 1199365.0249
31 | 2595697.065 | 1199382.1976 | 2595700.5719 | 1199378.304 | 2595705.1441 | 1199373.5537
32 | 2595737.9743 | 1199219.268 | 2595730.9463 | 1199210.8785
33 | 2595681.0448 | 1199220.846 | 2595690.4196 | 1199215.6066
34 | 2595674.0553 | 1199221.0138 | 2595689.1331 | 1199212.6317
35 | 2595674.0553 | 1199221.0138 | 2595651.6201 | 1199233.4861
36 | 2595814.5452 | 1199139.323 | 2595828.8857 | 1199156.8324
37 | 2595717.7946 | 1199329.4973 | 2595734.2964 | 1199332.4994 | 2595741.5712 | 1199333.5257
38 | 2595788.6178 | 1199136.9133 | 2595796.642 | 1199130.5204
39 | 2595731.0734 | 1199276.783 | 2595733.8136 | 1199275.7471 | 2595735.7009 | 1199274.5784 | 2595745.92 | 1199266.3667
40 | 2595682.12 | 1199365.0249 | 2595580.1063 | 1199346.3872
41 | 2595697.065 | 1199382.1976 | 2595693.3322 | 1199379.2209 | 2595690.3238 | 1199377.7557 | 2595687.2169 | 1199376.8575 | 2595678.6434 | 1199375.741 | 2595642.2338 | 1199369.1631
42 | 2595642.2338 | 1199369.1631 | 2595576.3751 | 1199357.2649
43 | 2595618.644 | 1199255.7211 | 2595646.5756 | 1199261.2642
44 | 2595618.644 | 1199255.7211 | 2595612.0424 | 1199259.4203
45 | 2595653.0878 | 1199262.5566 | 2595646.5756 | 1199261.2642
46 | 2595606.6263 | 1199262.4552 | 2595612.0424 | 1199259.4203
47 | 2595656.8482 | 1199263.3028 | 2595653.0878 | 1199262.5566
48 | 2595578.2124 | 1199281.2206 | 2595580.2659 | 1199278.2619 | 2595583.2027 | 1199275.5805 | 2595606.6263 | 1199262.4552
49 | 2595656.8482 | 1199263.3028 | 2595676.0242 | 1199267.1083
50 | 2595578.2124 | 1199281.2206 | 2595575.3027 | 1199279.4219
51 | 2595578.2124 | 1199281.2206 | 2595576.822 | 1199285.046 | 2595576.5738 | 1199289.0594 | 2595577.2315 | 1199292.9499 | 2595578.544 | 1199296.8621 | 2595579.9848 | 1199299.2956
52 | 2595731.0734 | 1199276.783 | 2595731.0734 | 1199276.783 | 2595728.0968 | 1199277.0964 | 2595725.3558 | 1199276.8983 | 2595720.7096 | 1199275.9763
53 | 2595638.681 | 1199240.6793 | 2595651.6201 | 1199233.4861
54 | 2595638.681 | 1199240.6793 | 2595617.0145 | 1199252.7242
55 | 2595603.5657 | 1199260.2008 | 2595617.0145 | 1199252.7242
56 | 2595603.5657 | 1199260.2008 | 2595591.6581 | 1199266.8204
57 | 2595717.7946 | 1199329.4973 | 2595704.2114 | 1199327.0262
58 | 2595686.5212 | 1199323.808 | 2595704.2114 | 1199327.0262
59 | 2595679.6427 | 1199322.5567 | 2595686.5212 | 1199323.808
60 | 2595679.6427 | 1199322.5567 | 2595656.8698 | 1199318.4138
61 | 2595720.7096 | 1199275.9763 | 2595713.5654 | 1199274.5585
62 | 2595711.3693 | 1199274.1226 | 2595713.5654 | 1199274.5585
63 | 2595705.5308 | 1199272.964 | 2595711.3693 | 1199274.1226
64 | 2595676.0242 | 1199267.1083 | 2595682.5086 | 1199268.3952
65 | 2595686.423 | 1199269.172 | 2595682.5086 | 1199268.3952
66 | 2595686.423 | 1199269.172 | 2595705.5308 | 1199272.964
67 | 2595579.9848 | 1199299.2956 | 2595581.6691 | 1199301.6957 | 2595583.9243 | 1199303.8173 | 2595586.0191 | 1199305.2276 | 2595588.4712 | 1199305.9706 | 2595598.1545 | 1199307.7322
68 | 2595579.9848 | 1199299.2956 | 2595568.3071 | 1199301.2499 | 2595529.4599 | 1199294.4275
69 | 2595575.3027 | 1199279.4219 | 2595572.8425 | 1199277.9785 | 2595569.8307 | 1199272.0998
70 | 2595575.3027 | 1199279.4219 | 2595576.3673 | 1199277.7424 | 2595578.17 | 1199275.3842 | 2595580.2242 | 1199273.4816 | 2595582.4386 | 1199271.9458 | 2595591.6581 | 1199266.8204

## bus_geodata
| x | y | coords
0 | 2595748.5416 | 1199155.4207
1 | 2595757.0315 | 1199165.927
2 | 2595718.6112 | 1199194.7481
3 | 2595720.3418 | 1199197.893
4 | 2595712.4915 | 1199183.551
5 | 2595805.8564 | 1199302.1649
6 | 2595785.48 | 1199276.9169
7 | 2595905.1458 | 1199141.2753
8 | 2595797.4267 | 1199309.1952
9 | 2595852.9094 | 1199078.2227
10 | 2595812.2265 | 1199115.3532
11 | 2595763.5877 | 1199335.8133
12 | 2595775.1637 | 1199326.8954
13 | 2595716.4134 | 1199367.8422
14 | 2595749.7577 | 1199334.4672
15 | 2595807.0855 | 1199125.7695
16 | 2595802.4337 | 1199125.9063
17 | 2595813.496 | 1199138.0419
18 | 2595764.7525 | 1199251.2338
19 | 2595751.4395 | 1199261.9315
20 | 2595754.8003 | 1199239.3536
21 | 2595711.1046 | 1199382.9655
22 | 2595709.4904 | 1199372.2832
23 | 2595718.6896 | 1199397.2689
24 | 2595705.1441 | 1199373.5537
25 | 2595730.9463 | 1199210.8785
26 | 2595690.4196 | 1199215.6066
27 | 2595689.1331 | 1199212.6317
28 | 2595674.0553 | 1199221.0138
29 | 2595828.8857 | 1199156.8324
30 | 2595814.5452 | 1199139.323
31 | 2595741.5712 | 1199333.5257
32 | 2595796.642 | 1199130.5204
33 | 2595745.92 | 1199266.3667
34 | 2595737.9743 | 1199219.268
35 | 2595682.12 | 1199365.0249
36 | 2595697.065 | 1199382.1976
37 | 2595642.2338 | 1199369.1631
38 | 2595681.0448 | 1199220.846
39 | 2595618.644 | 1199255.7211
40 | 2595646.5756 | 1199261.2642
41 | 2595612.0424 | 1199259.4203
42 | 2595653.0878 | 1199262.5566
43 | 2595606.6263 | 1199262.4552
44 | 2595656.8482 | 1199263.3028
45 | 2595578.2124 | 1199281.2206
46 | 2595731.0734 | 1199276.783
47 | 2595651.6201 | 1199233.4861
48 | 2595638.681 | 1199240.6793
49 | 2595617.0145 | 1199252.7242
50 | 2595603.5657 | 1199260.2008
51 | 2595717.7946 | 1199329.4973
52 | 2595704.2114 | 1199327.0262
53 | 2595686.5212 | 1199323.808
54 | 2595679.6427 | 1199322.5567
55 | 2595720.7096 | 1199275.9763
56 | 2595713.5654 | 1199274.5585
57 | 2595711.3693 | 1199274.1226
58 | 2595676.0242 | 1199267.1083
59 | 2595682.5086 | 1199268.3952
60 | 2595686.423 | 1199269.172
61 | 2595705.5308 | 1199272.964
62 | 2595656.8698 | 1199318.4138
63 | 2595598.1545 | 1199307.7322
64 | 2595579.9848 | 1199299.2956
65 | 2595529.4599 | 1199294.4275
66 | 2595788.6178 | 1199136.9133
67 | 2595575.3027 | 1199279.4219
68 | 2595569.8307 | 1199272.0998
69 | 2595591.6581 | 1199266.8204
70 | 2595576.3751 | 1199357.2649
71 | 2595580.1063 | 1199346.3872
72 | 2595618.644 | 1199255.7211

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1