## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_351-443_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_351-443_0_2_node_39 | 0.4 | n |  | TRUE
2 | bus_LV_351-443_0_2_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_351-443_0_2_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_351-443_0_2_node_62 | 0.4 | n |  | TRUE
5 | bus_LV_351-443_0_2_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_351-443_0_2_node_81 | 0.4 | n |  | TRUE
7 | bus_LV_351-443_0_2_node_13 | 0.4 | n |  | TRUE
8 | bus_LV_351-443_0_2_node_2 | 0.4 | n |  | TRUE
9 | bus_LV_351-443_0_2_node_78 | 0.4 | n |  | TRUE
10 | bus_LV_351-443_0_2_node_86 | 0.4 | n |  | TRUE
11 | bus_LV_351-443_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_351-443_0_2_node_3 | 0.4 | n |  | TRUE
13 | bus_LV_351-443_0_2_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_351-443_0_2_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_351-443_0_2_node_4 | 0.4 | n |  | TRUE
16 | bus_LV_351-443_0_2_node_64 | 0.4 | n |  | TRUE
17 | bus_LV_351-443_0_2_node_52 | 0.4 | n |  | TRUE
18 | bus_LV_351-443_0_2_node_83 | 0.4 | n |  | TRUE
19 | bus_LV_351-443_0_2_node_55 | 0.4 | n |  | TRUE
20 | bus_LV_351-443_0_2_node_5 | 0.4 | n |  | TRUE
21 | bus_LV_351-443_0_2_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_351-443_0_2_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_351-443_0_2_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_351-443_0_2_node_49 | 0.4 | n |  | TRUE
25 | bus_LV_351-443_0_2_node_7 | 0.4 | n |  | TRUE
26 | bus_LV_351-443_0_2_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_351-443_0_2_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_351-443_0_2_node_98 | 0.4 | n |  | TRUE
29 | bus_LV_351-443_0_2_node_63 | 0.4 | n |  | TRUE
30 | bus_LV_351-443_0_2_node_8 | 0.4 | n |  | TRUE
31 | bus_LV_351-443_0_2_node_90 | 0.4 | n |  | TRUE
32 | bus_LV_351-443_0_2_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_351-443_0_2_node_15 | 0.4 | n |  | TRUE
34 | bus_LV_351-443_0_2_node_9 | 0.4 | n |  | TRUE
35 | bus_LV_351-443_0_2_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_351-443_0_2_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_351-443_0_2_node_14 | 0.4 | n |  | TRUE
38 | bus_LV_351-443_0_2_node_94 | 0.4 | n |  | TRUE
39 | bus_LV_351-443_0_2_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_351-443_0_2_node_76 | 0.4 | n |  | TRUE
41 | bus_LV_351-443_0_2_node_17 | 0.4 | n |  | TRUE
42 | bus_LV_351-443_0_2_node_77 | 0.4 | n |  | TRUE
43 | bus_LV_351-443_0_2_node_75 | 0.4 | n |  | TRUE
44 | bus_LV_351-443_0_2_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_351-443_0_2_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_351-443_0_2_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_351-443_0_2_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_351-443_0_2_node_79 | 0.4 | n |  | TRUE
49 | bus_LV_351-443_0_2_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_351-443_0_2_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_351-443_0_2_node_95 | 0.4 | n |  | TRUE
52 | bus_LV_351-443_0_2_node_18 | 0.4 | n |  | TRUE
53 | bus_LV_351-443_0_2_node_87 | 0.4 | n |  | TRUE
54 | bus_LV_351-443_0_2_node_97 | 0.4 | n |  | TRUE
55 | bus_LV_351-443_0_2_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_351-443_0_2_node_19 | 0.4 | n |  | TRUE
57 | bus_LV_351-443_0_2_node_96 | 0.4 | n |  | TRUE
58 | bus_LV_351-443_0_2_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_351-443_0_2_node_21 | 0.4 | n |  | TRUE
60 | bus_LV_351-443_0_2_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_351-443_0_2_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_351-443_0_2_node_22 | 0.4 | n |  | TRUE
63 | bus_LV_351-443_0_2_node_100 | 0.4 | n |  | TRUE
64 | bus_LV_351-443_0_2_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_351-443_0_2_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_351-443_0_2_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_351-443_0_2_node_45 | 0.4 | n |  | TRUE
68 | bus_LV_351-443_0_2_node_92 | 0.4 | n |  | TRUE
69 | bus_LV_351-443_0_2_node_24 | 0.4 | n |  | TRUE
70 | bus_LV_351-443_0_2_node_27 | 0.4 | n |  | TRUE
71 | bus_LV_351-443_0_2_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_351-443_0_2_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_351-443_0_2_node_28 | 0.4 | n |  | TRUE
74 | bus_LV_351-443_0_2_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_351-443_0_2_node_31 | 0.4 | n |  | TRUE
76 | bus_LV_351-443_0_2_node_85 | 0.4 | n |  | TRUE
77 | bus_LV_351-443_0_2_node_89 | 0.4 | n |  | TRUE
78 | bus_LV_351-443_0_2_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_351-443_0_2_node_33 | 0.4 | n |  | TRUE
80 | bus_LV_351-443_0_2_node_35 | 0.4 | n |  | TRUE
81 | bus_LV_351-443_0_2_node_47 | 0.4 | n |  | TRUE
82 | bus_LV_351-443_0_2_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_351-443_0_2_node_99 | 0.4 | n |  | TRUE
84 | bus_LV_351-443_0_2_node_41 | 0.4 | n |  | TRUE
85 | bus_LV_351-443_0_2_node_40 | 0.4 | n |  | TRUE
86 | bus_LV_351-443_0_2_node_65 | 0.4 | n |  | TRUE
87 | bus_LV_351-443_0_2_node_51 | 0.4 | n |  | TRUE
88 | bus_LV_351-443_0_2_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_351-443_0_2_node_42 | 0.4 | n |  | TRUE
90 | bus_LV_351-443_0_2_node_46 | 0.4 | n |  | TRUE
91 | bus_LV_351-443_0_2_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_351-443_0_2_node_69 | 0.4 | n |  | TRUE
93 | bus_LV_351-443_0_2_node_67 | 0.4 | n |  | TRUE
94 | bus_LV_351-443_0_2_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_351-443_0_2_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_351-443_0_2_node_73 | 0.4 | n |  | TRUE
97 | bus_LV_351-443_0_2_node_56 | 0.4 | n |  | TRUE
98 | bus_LV_351-443_0_2_node_80 | 0.4 | n |  | TRUE
99 | bus_LV_351-443_0_2_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_351-443_0_2_node_93 | 0.4 | n |  | TRUE
101 | bus_MV_605_0_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_351-443_0_2_load_0 | 0 | 0.0056873 | 0.0014254 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_351-443_0_2_load_39 | 1 | 0.0012354 | 0.00030963 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_351-443_0_2_load_23 | 2 | 0.0030361 | 0.00076091 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_351-443_0_2_load_1 | 3 | 0.0030603 | 0.00076698 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_351-443_0_2_load_62 | 4 | 0.0020979 | 0.00052577 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_351-443_0_2_load_10 | 5 | 0.0022675 | 0.00056829 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_351-443_0_2_load_13 | 7 | 0.011622 | 0.0029127 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_351-443_0_2_load_2 | 8 | 0.002857 | 0.00071603 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_351-443_0_2_load_78 | 9 | 0.0028938 | 0.00072525 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_351-443_0_2_load_86 | 10 | 0.0041952 | 0.0010514 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_351-443_0_2_load_6 | 11 | 0.0026999 | 0.00067667 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_351-443_0_2_load_3 | 12 | 0.0062895 | 0.0015763 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_351-443_0_2_load_26 | 13 | 0.003017 | 0.00075613 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_351-443_0_2_load_54 | 14 | 0.0024285 | 0.00060864 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_351-443_0_2_load_4 | 15 | 0.0018971 | 0.00047545 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_351-443_0_2_load_64 | 16 | 0.0018248 | 0.00045734 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_351-443_0_2_load_52 | 17 | 0.0016087 | 0.00040318 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_351-443_0_2_load_55 | 19 | 0.0019766 | 0.00049539 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_351-443_0_2_load_5 | 20 | 0.00090747 | 0.00022743 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_351-443_0_2_load_25 | 21 | 0.004306 | 0.0010792 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_351-443_0_2_load_11 | 22 | 0.0012232 | 0.00030656 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_351-443_0_2_load_12 | 23 | 0.002194 | 0.00054987 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_351-443_0_2_load_7 | 25 | 0.0016691 | 0.00041831 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_351-443_0_2_load_58 | 27 | 0.0018474 | 0.00046299 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_351-443_0_2_load_63 | 29 | 0.0027492 | 0.00068901 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_351-443_0_2_load_8 | 30 | 0.00095561 | 0.0002395 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_351-443_0_2_load_90 | 31 | 0.0013074 | 0.00032766 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_351-443_0_2_load_20 | 32 | 0.0019914 | 0.0004991 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_351-443_0_2_load_16 | 36 | 0.01052 | 0.0026367 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_351-443_0_2_load_94 | 38 | 0.0023465 | 0.00058808 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_351-443_0_2_load_76 | 40 | 0.0031487 | 0.00078913 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_351-443_0_2_load_75 | 43 | 0.0010555 | 0.00026454 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_351-443_0_2_load_50 | 44 | 0.0013278 | 0.00033278 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_351-443_0_2_load_88 | 45 | 0.0019898 | 0.00049868 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_351-443_0_2_load_36 | 46 | 0.0023511 | 0.00058924 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_351-443_0_2_load_79 | 48 | 0.0016752 | 0.00041985 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_351-443_0_2_load_44 | 50 | 0.0021337 | 0.00053476 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_351-443_0_2_load_95 | 51 | 0.0028019 | 0.00070223 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_351-443_0_2_load_18 | 52 | 0.002292 | 0.00057444 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_351-443_0_2_load_87 | 53 | 0.0022896 | 0.00057382 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_351-443_0_2_load_97 | 54 | 0.01464 | 0.0036691 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_351-443_0_2_load_59 | 55 | 0.0034075 | 0.00085401 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_351-443_0_2_load_19 | 56 | 0.0024292 | 0.0006088 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_351-443_0_2_load_96 | 57 | 0.0024339 | 0.00060998 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_351-443_0_2_load_48 | 58 | 0.002297 | 0.00057568 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_351-443_0_2_load_21 | 59 | 0.0059396 | 0.0014886 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_351-443_0_2_load_71 | 60 | 0.0022078 | 0.00055333 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_351-443_0_2_load_53 | 61 | 0.0030892 | 0.00077423 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_351-443_0_2_load_22 | 62 | 0.0019535 | 0.0004896 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_351-443_0_2_load_100 | 63 | 0.0033645 | 0.00084321 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_351-443_0_2_load_34 | 64 | 0.0036173 | 0.00090657 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_351-443_0_2_load_37 | 65 | 0.0030153 | 0.00075571 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_351-443_0_2_load_43 | 66 | 0.0023893 | 0.00059882 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_351-443_0_2_load_92 | 68 | 0.0016762 | 0.00042009 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_351-443_0_2_load_24 | 69 | 0.0028027 | 0.00070243 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_351-443_0_2_load_27 | 70 | 0.0017734 | 0.00044445 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_351-443_0_2_load_60 | 71 | 0.0015203 | 0.00038102 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_351-443_0_2_load_61 | 72 | 0.0052654 | 0.0013196 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_351-443_0_2_load_28 | 73 | 0.0024189 | 0.00060624 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_351-443_0_2_load_82 | 74 | 0.0043366 | 0.0010869 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_351-443_0_2_load_31 | 75 | 0.00063518 | 0.00015919 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_351-443_0_2_load_85 | 76 | 0.002103 | 0.00052707 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_351-443_0_2_load_89 | 77 | 0.00065654 | 0.00016454 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_351-443_0_2_load_33 | 79 | 0.0018156 | 0.00045503 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_351-443_0_2_load_35 | 80 | 0.014496 | 0.003633 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_351-443_0_2_load_47 | 81 | 0.0053186 | 0.001333 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_351-443_0_2_load_68 | 82 | 0.0027198 | 0.00068166 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_351-443_0_2_load_99 | 83 | 0.0023795 | 0.00059635 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_351-443_0_2_load_41 | 84 | 0.0089844 | 0.0022517 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_351-443_0_2_load_40 | 85 | 0.0020582 | 0.00051584 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_351-443_0_2_load_65 | 86 | 0.0025848 | 0.00064782 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_351-443_0_2_load_51 | 87 | 0.0015852 | 0.00039728 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_351-443_0_2_load_70 | 88 | 0.0015719 | 0.00039395 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_351-443_0_2_load_42 | 89 | 0.0021936 | 0.00054976 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_351-443_0_2_load_46 | 90 | 0.0029504 | 0.00073943 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_351-443_0_2_load_91 | 91 | 0.0014389 | 0.00036061 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_351-443_0_2_load_69 | 92 | 0.0016165 | 0.00040514 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_351-443_0_2_load_67 | 93 | 0.012222 | 0.0030632 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_351-443_0_2_load_74 | 94 | 0.0030608 | 0.00076712 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_351-443_0_2_load_84 | 95 | 0.0039406 | 0.0009876 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_351-443_0_2_load_56 | 97 | 0.0043618 | 0.0010932 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_351-443_0_2_load_80 | 98 | 0.0054212 | 0.0013587 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_351-443_0_2_load_66 | 99 | 0.00041806 | 0.00010478 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 80 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_351-443_0_2_line_0 |  | 0 | 1 | 0.0013403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_351-443_0_2_line_1 |  | 1 | 2 | 0.0014077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_351-443_0_2_line_2 |  | 2 | 67 | 0.033621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_351-443_0_2_line_3 |  | 3 | 4 | 0.0073286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_351-443_0_2_line_4 |  | 3 | 5 | 0.0072404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_351-443_0_2_line_5 |  | 4 | 6 | 0.012398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_351-443_0_2_line_6 |  | 5 | 7 | 0.001213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_351-443_0_2_line_7 |  | 6 | 47 | 0.017207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_351-443_0_2_line_8 |  | 6 | 37 | 0.016862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_351-443_0_2_line_9 |  | 8 | 9 | 0.0047542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_351-443_0_2_line_10 |  | 8 | 10 | 0.0029678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_351-443_0_2_line_11 |  | 9 | 11 | 0.010694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_351-443_0_2_line_12 |  | 11 | 23 | 0.0018174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_351-443_0_2_line_13 |  | 12 | 13 | 0.0015585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_351-443_0_2_line_14 |  | 13 | 14 | 0.0073735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_351-443_0_2_line_15 |  | 14 | 50 | 0.0087983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_351-443_0_2_line_16 |  | 15 | 16 | 0.0060487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_351-443_0_2_line_17 |  | 15 | 17 | 0.0055576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_351-443_0_2_line_18 |  | 16 | 18 | 0.040848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_351-443_0_2_line_19 |  | 17 | 19 | 0.0041086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_351-443_0_2_line_20 |  | 18 | 20 | 0.094541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_351-443_0_2_line_21 |  | 19 | 79 | 0.010866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_351-443_0_2_line_22 |  | 20 | 21 | 9.0917e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_351-443_0_2_line_23 |  | 21 | 22 | 0.033819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_351-443_0_2_line_24 |  | 22 | 44 | 0.01272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_351-443_0_2_line_25 |  | 23 | 24 | 0.016646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_351-443_0_2_line_26 |  | 24 | 42 | 0.016856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_351-443_0_2_line_27 |  | 24 | 26 | 0.016963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_351-443_0_2_line_28 |  | 25 | 26 | 0.018388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_351-443_0_2_line_29 |  | 25 | 27 | 0.0087823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_351-443_0_2_line_30 |  | 26 | 28 | 0.017063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_351-443_0_2_line_31 |  | 27 | 29 | 0.0014531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_351-443_0_2_line_32 |  | 28 | 49 | 0.01683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_351-443_0_2_line_33 |  | 28 | 69 | 0.015072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_351-443_0_2_line_34 |  | 29 | 97 | 0.0057816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_351-443_0_2_line_35 |  | 30 | 31 | 0.0053708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_351-443_0_2_line_36 |  | 30 | 32 | 0.0047995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_351-443_0_2_line_37 |  | 32 | 33 | 0.05356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_351-443_0_2_line_38 |  | 33 | 42 | 0.020491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_351-443_0_2_line_39 |  | 33 | 34 | 0.13524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_351-443_0_2_line_40 |  | 34 | 35 | 0.086711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_351-443_0_2_line_41 |  | 34 | 36 | 0.007064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_351-443_0_2_line_42 |  | 35 | 43 | 0.087606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_351-443_0_2_line_43 |  | 37 | 38 | 0.012377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_351-443_0_2_line_44 |  | 37 | 39 | 0.051047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_351-443_0_2_line_45 |  | 38 | 46 | 0.0027821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_351-443_0_2_line_46 |  | 39 | 40 | 0.015696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_351-443_0_2_line_47 |  | 39 | 41 | 0.017076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_351-443_0_2_line_48 |  | 40 | 85 | 0.0073287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_351-443_0_2_line_49 |  | 41 | 49 | 0.017182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_351-443_0_2_line_50 |  | 41 | 50 | 0.015077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_351-443_0_2_line_51 |  | 42 | 48 | 0.014545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_351-443_0_2_line_52 |  | 43 | 70 | 0.22789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_351-443_0_2_line_53 |  | 44 | 45 | 0.0092848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_351-443_0_2_line_54 |  | 45 | 96 | 0.014678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_351-443_0_2_line_55 |  | 46 | 55 | 0.0045387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_351-443_0_2_line_56 |  | 47 | 95 | 0.02088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_351-443_0_2_line_57 |  | 47 | 67 | 0.016547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_351-443_0_2_line_58 |  | 48 | 57 | 0.0073504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_351-443_0_2_line_59 |  | 49 | 51 | 0.014406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_351-443_0_2_line_60 |  | 51 | 73 | 0.010185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_351-443_0_2_line_61 |  | 52 | 53 | 0.0059049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_351-443_0_2_line_62 |  | 52 | 54 | 0.0011931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_351-443_0_2_line_63 |  | 53 | 55 | 0.0013446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_351-443_0_2_line_64 |  | 56 | 57 | 0.0086987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_351-443_0_2_line_65 |  | 56 | 58 | 0.0059498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_351-443_0_2_line_66 |  | 59 | 60 | 0.0009071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_351-443_0_2_line_67 |  | 60 | 61 | 0.0075477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_351-443_0_2_line_68 |  | 61 | 69 | 0.0087469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_351-443_0_2_line_69 |  | 62 | 63 | 0.0010661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_351-443_0_2_line_70 |  | 62 | 64 | 0.0030936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_351-443_0_2_line_71 |  | 63 | 65 | 0.0033285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_351-443_0_2_line_72 |  | 64 | 66 | 0.00031385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_351-443_0_2_line_73 |  | 65 | 83 | 0.0050926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
74 | LV_351-443_0_2_line_74 |  | 66 | 76 | 0.0026977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_351-443_0_2_line_75 |  | 67 | 68 | 0.022136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_351-443_0_2_line_76 |  | 68 | 94 | 0.0082806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_351-443_0_2_line_77 |  | 70 | 71 | 0.004465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
78 | LV_351-443_0_2_line_78 |  | 71 | 72 | 0.00014617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_351-443_0_2_line_79 |  | 72 | 88 | 0.0013341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_351-443_0_2_line_80 |  | 73 | 74 | 0.010077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_351-443_0_2_line_81 |  | 75 | 76 | 0.0041155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_351-443_0_2_line_82 |  | 75 | 77 | 0.00055678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_351-443_0_2_line_83 |  | 77 | 78 | 0.038833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_351-443_0_2_line_84 |  | 78 | 96 | 0.036217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_351-443_0_2_line_85 |  | 78 | 100 | 0.23163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_351-443_0_2_line_86 |  | 80 | 81 | 0.0061328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_351-443_0_2_line_87 |  | 81 | 82 | 0.0070225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_351-443_0_2_line_88 |  | 82 | 86 | 0.0028736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_351-443_0_2_line_89 |  | 83 | 84 | 0.0011344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_351-443_0_2_line_90 |  | 84 | 87 | 0.0056133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_351-443_0_2_line_91 |  | 85 | 86 | 0.0058976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
92 | LV_351-443_0_2_line_92 |  | 87 | 88 | 0.00094753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_351-443_0_2_line_93 |  | 89 | 90 | 3.9901e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_351-443_0_2_line_94 |  | 89 | 91 | 0.0033836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_351-443_0_2_line_95 |  | 90 | 92 | 0.0049035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_351-443_0_2_line_96 |  | 91 | 93 | 0.016977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_351-443_0_2_line_97 |  | 92 | 94 | 0.0098368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_351-443_0_2_line_98 |  | 95 | 98 | 0.006878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_351-443_0_2_line_99 |  | 99 | 100 | 0.091098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_351-443_0_2_trafo_35 | 0.63 MVA 20/0.4 kV | 101 | 80 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2594837.6985 | 1199662.9729 | 2594838.7293 | 1199662.1162
1 | 2594839.812 | 1199661.2166 | 2594838.7293 | 1199662.1162
2 | 2594863.5606 | 1199663.7284 | 2594852.5103 | 1199650.6644 | 2594839.812 | 1199661.2166
3 | 2594870.4307 | 1199701.9656 | 2594876.0633 | 1199697.277
4 | 2594870.4307 | 1199701.9656 | 2594864.8659 | 1199706.5977
5 | 2594885.5921 | 1199689.3452 | 2594876.0633 | 1199697.277
6 | 2594863.9337 | 1199707.3737 | 2594864.8659 | 1199706.5977
7 | 2594885.5921 | 1199689.3452 | 2594874.1842 | 1199676.4371
8 | 2594896.4823 | 1199702.2427 | 2594885.5921 | 1199689.3452
9 | 2594950.3115 | 1199833.7803 | 2594946.6682 | 1199836.8346
10 | 2594944.3939 | 1199838.7412 | 2594946.6682 | 1199836.8346
11 | 2594958.5063 | 1199826.9103 | 2594950.3115 | 1199833.7803
12 | 2594958.5063 | 1199826.9103 | 2594959.899 | 1199825.7428
13 | 2594908.3123 | 1199780.7523 | 2594909.5013 | 1199779.7447
14 | 2594915.1264 | 1199774.9775 | 2594909.5013 | 1199779.7447
15 | 2594921.8385 | 1199769.2892 | 2594915.1264 | 1199774.9775
16 | 2594795.6883 | 1199659.872 | 2594798.6291 | 1199663.8188 | 2594799.3559 | 1199664.6799
17 | 2594802.9403 | 1199668.9272 | 2594799.3559 | 1199664.6799
18 | 2594773.8222 | 1199633.9692 | 2594778.8533 | 1199632.6529 | 2594780.7336 | 1199632.5178 | 2594782.3096 | 1199632.6276 | 2594783.7869 | 1199632.982 | 2594785.2568 | 1199633.6478 | 2594786.7422 | 1199634.6136 | 2594787.7786 | 1199635.7578 | 2594788.4497 | 1199637.1468 | 2594788.9003 | 1199638.7695 | 2594790.5693 | 1199649.2848 | 2594792.0886 | 1199654.1305 | 2594794.8791 | 1199658.7861 | 2594795.6883 | 1199659.872
19 | 2594802.9403 | 1199668.9272 | 2594805.5902 | 1199672.067
20 | 2594773.8222 | 1199633.9692 | 2594787.0664 | 1199682.6725 | 2594787.9225 | 1199686.5627 | 2594788.2073 | 1199690.031 | 2594788.4766 | 1199693.3214 | 2594788.3962 | 1199697.1124 | 2594787.9506 | 1199701.126 | 2594786.9039 | 1199705.5182 | 2594785.1185 | 1199709.6109 | 2594776.9183 | 1199723.9215
21 | 2594812.5985 | 1199680.3712 | 2594805.5902 | 1199672.067
22 | 2594776.9183 | 1199723.9215 | 2594776.9178 | 1199723.9223
23 | 2594762.4871 | 1199754.2958 | 2594762.9719 | 1199751.8865 | 2594764.2548 | 1199747.7609 | 2594765.9561 | 1199743.2681 | 2594768.4263 | 1199738.7413 | 2594776.9178 | 1199723.9223
24 | 2594761.2948 | 1199766.9221 | 2594761.2487 | 1199766.0179 | 2594761.359 | 1199761.6599 | 2594761.8956 | 1199757.2348 | 2594762.4871 | 1199754.2958
25 | 2594972.6552 | 1199815.0488 | 2594959.899 | 1199825.7428
26 | 2594972.6552 | 1199815.0488 | 2594983.1113 | 1199828.2914
27 | 2594972.6552 | 1199815.0488 | 2594961.9859 | 1199801.8397
28 | 2594961.9859 | 1199801.8397 | 2594947.9386 | 1199813.7053
29 | 2594947.9386 | 1199813.7053 | 2594941.2295 | 1199819.3724
30 | 2594961.9859 | 1199801.8397 | 2594951.7578 | 1199788.1633
31 | 2594941.2295 | 1199819.3724 | 2594940.1194 | 1199820.31
32 | 2594951.7578 | 1199788.1633 | 2594942.633 | 1199774.008
33 | 2594951.7578 | 1199788.1633 | 2594940.2686 | 1199797.918
34 | 2594935.7026 | 1199824.0408 | 2594940.1194 | 1199820.31
35 | 2594953.1297 | 1199864.9621 | 2594950.9193 | 1199866.8063 | 2594949.029 | 1199868.4303
36 | 2594953.1297 | 1199864.9621 | 2594956.815 | 1199861.8875
37 | 2594995.9906 | 1199844.2557 | 2594983.1876 | 1199855.1836 | 2594979.7263 | 1199858.1325 | 2594976.516 | 1199860.8701 | 2594968.6806 | 1199867.5581 | 2594964.3901 | 1199871.2193 | 2594956.815 | 1199861.8875 | 2594956.815 | 1199861.8875
38 | 2594995.9906 | 1199844.2557 | 2594983.1113 | 1199828.2914
39 | 2594995.9906 | 1199844.2557 | 2595014.8264 | 1199828.3979 | 2595026.8794 | 1199839.627 | 2595063.6628 | 1199873.9033 | 2595062.4435 | 1199917.7501
40 | 2595062.4435 | 1199917.7501 | 2595067.6071 | 1199920.3361 | 2595085.2902 | 1199928.0254 | 2595095.1057 | 1199931.2634 | 2595111.72 | 1199935.3962 | 2595117.1114 | 1199937.2928 | 2595120.744 | 1199938.924 | 2595125.6264 | 1199942.2106 | 2595113.1517 | 1199945.1558 | 2595110.4647 | 1199945.536 | 2595107.3816 | 1199945.5053
41 | 2595062.4435 | 1199917.7501 | 2595055.8032 | 1199915.2877
42 | 2595107.3816 | 1199945.5053 | 2595077.8116 | 1199942.6395 | 2595062.7519 | 1199940.5287 | 2595050.6002 | 1199938.2822 | 2595031.2753 | 1199933.596 | 2595021.2403 | 1199930.6876
43 | 2594896.4823 | 1199702.2427 | 2594886.9631 | 1199710.1525
44 | 2594896.4823 | 1199702.2427 | 2594908.6716 | 1199720.8755 | 2594917.9492 | 1199735.4753 | 2594923.9338 | 1199745.2754
45 | 2594884.8233 | 1199711.9305 | 2594886.9631 | 1199710.1525
46 | 2594923.9338 | 1199745.2754 | 2594911.9281 | 1199755.3864
47 | 2594923.9338 | 1199745.2754 | 2594933.3404 | 1199759.5416
48 | 2594911.9281 | 1199755.3864 | 2594906.3225 | 1199760.1073
49 | 2594942.633 | 1199774.008 | 2594933.3404 | 1199759.5416
50 | 2594933.3404 | 1199759.5416 | 2594921.8385 | 1199769.2892
51 | 2594983.1113 | 1199828.2914 | 2594971.9963 | 1199837.6724
52 | 2595021.2403 | 1199930.6876 | 2595006.1472 | 1199926.3133 | 2594980.097 | 1199917.8976 | 2594972.4437 | 1199914.947 | 2594937.3872 | 1199897.3454 | 2594922.177 | 1199888.4871 | 2594912.8229 | 1199882.0361 | 2594905.3198 | 1199876.762 | 2594879.8224 | 1199856.7067 | 2594831.8109 | 1199815.9601 | 2594828.7782 | 1199813.629
53 | 2594761.8402 | 1199776.1895 | 2594761.6904 | 1199774.6777 | 2594761.2948 | 1199766.9221
54 | 2594763.2882 | 1199790.796 | 2594761.8402 | 1199776.1895
55 | 2594884.8233 | 1199711.9305 | 2594881.3324 | 1199714.8311
56 | 2594874.1842 | 1199676.4371 | 2594858.2645 | 1199689.948
57 | 2594863.5606 | 1199663.7284 | 2594874.1842 | 1199676.4371
58 | 2594971.9963 | 1199837.6724 | 2594966.3792 | 1199842.4133
59 | 2594942.633 | 1199774.008 | 2594931.5685 | 1199783.2339
60 | 2594931.5685 | 1199783.2339 | 2594923.7462 | 1199789.7564
61 | 2594880.2983 | 1199715.6905 | 2594875.7566 | 1199719.4642
62 | 2594874.839 | 1199720.2267 | 2594875.7566 | 1199719.4642
63 | 2594880.2983 | 1199715.6905 | 2594881.3324 | 1199714.8311
64 | 2594959.7317 | 1199848.0238 | 2594966.3792 | 1199842.4133
65 | 2594955.1849 | 1199851.8613 | 2594959.7317 | 1199848.0238
66 | 2594927.1557 | 1199809.0513 | 2594927.8472 | 1199808.4642
67 | 2594933.6008 | 1199803.5792 | 2594927.8472 | 1199808.4642
68 | 2594940.2686 | 1199797.918 | 2594933.6008 | 1199803.5792
69 | 2594808.7957 | 1199805.0435 | 2594807.7399 | 1199804.8957
70 | 2594804.6762 | 1199804.4667 | 2594804.6762 | 1199804.4667 | 2594807.7399 | 1199804.8957
71 | 2594812.092 | 1199805.5052 | 2594808.7957 | 1199805.0435
72 | 2594804.3624 | 1199804.4733 | 2594804.6762 | 1199804.4667
73 | 2594816.9683 | 1199806.9737 | 2594812.092 | 1199805.5052 | 2594812.092 | 1199805.5052
74 | 2594801.6653 | 1199804.5304 | 2594804.3624 | 1199804.4733
75 | 2594863.5606 | 1199663.7284 | 2594846.4055 | 1199677.7176 | 2594846.4055 | 1199677.7176
76 | 2594841.0043 | 1199671.441 | 2594846.4055 | 1199677.7176
77 | 2594828.7782 | 1199813.629 | 2594825.2382 | 1199810.9078
78 | 2594825.1223 | 1199810.8188 | 2594825.2382 | 1199810.9078
79 | 2594823.928 | 1199810.2243 | 2594825.1223 | 1199810.8188 | 2594825.1223 | 1199810.8188
80 | 2594916.007 | 1199796.2095 | 2594923.7462 | 1199789.7564
81 | 2594801.6653 | 1199804.5304 | 2594797.5507 | 1199804.6175 | 2594797.5507 | 1199804.6175
82 | 2594797.0091 | 1199804.7465 | 2594797.5507 | 1199804.6175
83 | 2594766.0305 | 1199826.9018 | 2594784.6362 | 1199809.7317 | 2594789.9166 | 1199806.4363 | 2594797.0091 | 1199804.7465
84 | 2594763.2882 | 1199790.796 | 2594766.0305 | 1199826.9018
85 | 2594655.3755 | 1199983.4852 | 2594667.2272 | 1199982.1515 | 2594685.191 | 1199979.9897 | 2594694.4009 | 1199978.4472 | 2594704.5313 | 1199976.148 | 2594715.6201 | 1199973.0475 | 2594722.0584 | 1199970.8183 | 2594728.245 | 1199968.1002 | 2594732.6504 | 1199965.5282 | 2594742.3121 | 1199958.3824 | 2594745.872 | 1199955.1553 | 2594750.3893 | 1199950.004 | 2594753.9933 | 1199945.0093 | 2594758.7978 | 1199937.5343 | 2594762.2564 | 1199931.7503 | 2594765.2654 | 1199925.3887 | 2594767.9541 | 1199918.3825 | 2594769.6916 | 1199911.8442 | 2594770.5917 | 1199905.3843 | 2594770.9215 | 1199899.5698 | 2594770.8152 | 1199891.2099 | 2594766.0305 | 1199826.9018
86 | 2594890.249 | 1199765.6265 | 2594894.2422 | 1199770.2811 | 2594894.2422 | 1199770.2811
87 | 2594899.6136 | 1199765.7574 | 2594894.2422 | 1199770.2811
88 | 2594899.6136 | 1199765.7574 | 2594901.8115 | 1199763.9064
89 | 2594818.0545 | 1199807.3009 | 2594816.9683 | 1199806.9737
90 | 2594823.0797 | 1199809.8021 | 2594818.0545 | 1199807.3009 | 2594818.0545 | 1199807.3009
91 | 2594906.3225 | 1199760.1073 | 2594901.8115 | 1199763.9064
92 | 2594823.0797 | 1199809.8021 | 2594823.928 | 1199810.2243
93 | 2594829.7854 | 1199680.9514 | 2594829.8157 | 1199680.9254
94 | 2594829.7854 | 1199680.9514 | 2594827.2153 | 1199683.1521
95 | 2594829.8157 | 1199680.9254 | 2594833.5403 | 1199677.7361
96 | 2594817.103 | 1199695.0748 | 2594821.5613 | 1199691.7691 | 2594822.1393 | 1199691.046 | 2594822.5269 | 1199690.2897 | 2594822.6632 | 1199689.4558 | 2594822.571 | 1199688.5443 | 2594822.0601 | 1199687.5664 | 2594827.2153 | 1199683.1521
97 | 2594841.0043 | 1199671.441 | 2594840.9566 | 1199671.3856 | 2594833.5403 | 1199677.7361
98 | 2594853.0205 | 1199694.3985 | 2594858.2645 | 1199689.948
99 | 2594655.3755 | 1199983.4852 | 2594666.2803 | 1199987.2996 | 2594691.8331 | 1199992.7461 | 2594710.5708 | 1199996.1311 | 2594719.8074 | 1199998.9465 | 2594728.2755 | 1200002.0962 | 2594742.4862 | 1200008.7397

## bus_geodata
| x | y | coords
0 | 2594837.6985 | 1199662.9729
1 | 2594838.7293 | 1199662.1162
2 | 2594839.812 | 1199661.2166
3 | 2594870.4307 | 1199701.9656
4 | 2594876.0633 | 1199697.277
5 | 2594864.8659 | 1199706.5977
6 | 2594885.5921 | 1199689.3452
7 | 2594863.9337 | 1199707.3737
8 | 2594946.6682 | 1199836.8346
9 | 2594950.3115 | 1199833.7803
10 | 2594944.3939 | 1199838.7412
11 | 2594958.5063 | 1199826.9103
12 | 2594908.3123 | 1199780.7523
13 | 2594909.5013 | 1199779.7447
14 | 2594915.1264 | 1199774.9775
15 | 2594799.3559 | 1199664.6799
16 | 2594795.6883 | 1199659.872
17 | 2594802.9403 | 1199668.9272
18 | 2594773.8222 | 1199633.9692
19 | 2594805.5902 | 1199672.067
20 | 2594776.9183 | 1199723.9215
21 | 2594776.9178 | 1199723.9223
22 | 2594762.4871 | 1199754.2958
23 | 2594959.899 | 1199825.7428
24 | 2594972.6552 | 1199815.0488
25 | 2594947.9386 | 1199813.7053
26 | 2594961.9859 | 1199801.8397
27 | 2594941.2295 | 1199819.3724
28 | 2594951.7578 | 1199788.1633
29 | 2594940.1194 | 1199820.31
30 | 2594953.1297 | 1199864.9621
31 | 2594949.029 | 1199868.4303
32 | 2594956.815 | 1199861.8875
33 | 2594995.9906 | 1199844.2557
34 | 2595062.4435 | 1199917.7501
35 | 2595107.3816 | 1199945.5053
36 | 2595055.8032 | 1199915.2877
37 | 2594896.4823 | 1199702.2427
38 | 2594886.9631 | 1199710.1525
39 | 2594923.9338 | 1199745.2754
40 | 2594911.9281 | 1199755.3864
41 | 2594933.3404 | 1199759.5416
42 | 2594983.1113 | 1199828.2914
43 | 2595021.2403 | 1199930.6876
44 | 2594761.2948 | 1199766.9221
45 | 2594761.8402 | 1199776.1895
46 | 2594884.8233 | 1199711.9305
47 | 2594874.1842 | 1199676.4371
48 | 2594971.9963 | 1199837.6724
49 | 2594942.633 | 1199774.008
50 | 2594921.8385 | 1199769.2892
51 | 2594931.5685 | 1199783.2339
52 | 2594875.7566 | 1199719.4642
53 | 2594880.2983 | 1199715.6905
54 | 2594874.839 | 1199720.2267
55 | 2594881.3324 | 1199714.8311
56 | 2594959.7317 | 1199848.0238
57 | 2594966.3792 | 1199842.4133
58 | 2594955.1849 | 1199851.8613
59 | 2594927.1557 | 1199809.0513
60 | 2594927.8472 | 1199808.4642
61 | 2594933.6008 | 1199803.5792
62 | 2594807.7399 | 1199804.8957
63 | 2594808.7957 | 1199805.0435
64 | 2594804.6762 | 1199804.4667
65 | 2594812.092 | 1199805.5052
66 | 2594804.3624 | 1199804.4733
67 | 2594863.5606 | 1199663.7284
68 | 2594846.4055 | 1199677.7176
69 | 2594940.2686 | 1199797.918
70 | 2594828.7782 | 1199813.629
71 | 2594825.2382 | 1199810.9078
72 | 2594825.1223 | 1199810.8188
73 | 2594923.7462 | 1199789.7564
74 | 2594916.007 | 1199796.2095
75 | 2594797.5507 | 1199804.6175
76 | 2594801.6653 | 1199804.5304
77 | 2594797.0091 | 1199804.7465
78 | 2594766.0305 | 1199826.9018
79 | 2594812.5985 | 1199680.3712
80 | 2594890.249 | 1199765.6265
81 | 2594894.2422 | 1199770.2811
82 | 2594899.6136 | 1199765.7574
83 | 2594816.9683 | 1199806.9737
84 | 2594818.0545 | 1199807.3009
85 | 2594906.3225 | 1199760.1073
86 | 2594901.8115 | 1199763.9064
87 | 2594823.0797 | 1199809.8021
88 | 2594823.928 | 1199810.2243
89 | 2594829.7854 | 1199680.9514
90 | 2594829.8157 | 1199680.9254
91 | 2594827.2153 | 1199683.1521
92 | 2594833.5403 | 1199677.7361
93 | 2594817.103 | 1199695.0748
94 | 2594841.0043 | 1199671.441
95 | 2594858.2645 | 1199689.948
96 | 2594763.2882 | 1199790.796
97 | 2594935.7026 | 1199824.0408
98 | 2594853.0205 | 1199694.3985
99 | 2594742.4862 | 1200008.7397
100 | 2594655.3755 | 1199983.4852
101 | 2594923.9338 | 1199745.2754

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1