## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_352-12_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_352-12_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_352-12_0_5_node_47 | 0.4 | n |  | TRUE
3 | bus_LV_352-12_0_5_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_352-12_0_5_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_352-12_0_5_node_21 | 0.4 | n |  | TRUE
6 | bus_LV_352-12_0_5_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_352-12_0_5_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_352-12_0_5_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_352-12_0_5_node_24 | 0.4 | n |  | TRUE
10 | bus_LV_352-12_0_5_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_352-12_0_5_node_23 | 0.4 | n |  | TRUE
12 | bus_LV_352-12_0_5_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_352-12_0_5_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_352-12_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_352-12_0_5_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_352-12_0_5_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_352-12_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_352-12_0_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_352-12_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_352-12_0_5_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_352-12_0_5_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_352-12_0_5_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_352-12_0_5_node_44 | 0.4 | n |  | TRUE
24 | bus_LV_352-12_0_5_node_43 | 0.4 | n |  | TRUE
25 | bus_LV_352-12_0_5_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_352-12_0_5_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_352-12_0_5_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_352-12_0_5_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_352-12_0_5_node_48 | 0.4 | n |  | TRUE
30 | bus_LV_352-12_0_5_node_64 | 0.4 | n |  | TRUE
31 | bus_LV_352-12_0_5_node_61 | 0.4 | n |  | TRUE
32 | bus_LV_352-12_0_5_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_352-12_0_5_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_352-12_0_5_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_352-12_0_5_node_46 | 0.4 | n |  | TRUE
36 | bus_LV_352-12_0_5_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_352-12_0_5_node_16 | 0.4 | n |  | TRUE
38 | bus_LV_352-12_0_5_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_352-12_0_5_node_18 | 0.4 | n |  | TRUE
40 | bus_LV_352-12_0_5_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_352-12_0_5_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_352-12_0_5_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_352-12_0_5_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_352-12_0_5_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_352-12_0_5_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_352-12_0_5_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_352-12_0_5_node_37 | 0.4 | n |  | TRUE
48 | bus_LV_352-12_0_5_node_34 | 0.4 | n |  | TRUE
49 | bus_LV_352-12_0_5_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_352-12_0_5_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_352-12_0_5_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_352-12_0_5_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_352-12_0_5_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_352-12_0_5_node_65 | 0.4 | n |  | TRUE
55 | bus_LV_352-12_0_5_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_352-12_0_5_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_352-12_0_5_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_352-12_0_5_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_352-12_0_5_node_69 | 0.4 | n |  | TRUE
60 | bus_LV_352-12_0_5_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_352-12_0_5_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_352-12_0_5_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_352-12_0_5_node_56 | 0.4 | n |  | TRUE
64 | bus_LV_352-12_0_5_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_352-12_0_5_node_57 | 0.4 | n |  | TRUE
66 | bus_LV_352-12_0_5_node_66 | 0.4 | n |  | TRUE
67 | bus_LV_352-12_0_5_node_67 | 0.4 | n |  | TRUE
68 | bus_LV_352-12_0_5_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_352-12_0_5_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_352-12_0_5_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_352-12_0_5_node_62 | 0.4 | n |  | TRUE
72 | bus_MV_602_0_node_2 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_352-12_0_5_load_0 | 0 | 0.040909 | 0.010253 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_352-12_0_5_load_47 | 2 | 0.0015652 | 0.00039228 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_352-12_0_5_load_2 | 3 | 0.0011999 | 0.00030073 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_352-12_0_5_load_29 | 4 | 0.00066161 | 0.00016582 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_352-12_0_5_load_21 | 5 | 0.0041824 | 0.0010482 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_352-12_0_5_load_19 | 6 | 0.0040677 | 0.0010195 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_352-12_0_5_load_4 | 7 | 0.017544 | 0.0043969 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_352-12_0_5_load_3 | 8 | 0.087288 | 0.021876 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_352-12_0_5_load_24 | 9 | 0.004404 | 0.0011037 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_352-12_0_5_load_26 | 10 | 0.0029966 | 0.00075102 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_352-12_0_5_load_23 | 11 | 0.0078643 | 0.001971 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_352-12_0_5_load_25 | 12 | 0.0018887 | 0.00047335 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_352-12_0_5_load_5 | 13 | 0.0025413 | 0.00063691 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_352-12_0_5_load_9 | 17 | 0.0023611 | 0.00059175 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_352-12_0_5_load_11 | 19 | 0.0028295 | 0.00070913 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_352-12_0_5_load_15 | 20 | 0.0037584 | 0.00094195 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_352-12_0_5_load_12 | 21 | 0.0038139 | 0.00095587 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_352-12_0_5_load_44 | 23 | 0.002913 | 0.00073005 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_352-12_0_5_load_43 | 24 | 0.0039484 | 0.00098957 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_352-12_0_5_load_63 | 25 | 0.0032461 | 0.00081354 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_352-12_0_5_load_36 | 26 | 0.0090235 | 0.0022615 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_352-12_0_5_load_13 | 27 | 0.0032668 | 0.00081874 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_352-12_0_5_load_51 | 28 | 0.0022868 | 0.00057312 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_352-12_0_5_load_48 | 29 | 0.0019552 | 0.00049002 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_352-12_0_5_load_64 | 30 | 0.0031192 | 0.00078173 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_352-12_0_5_load_45 | 33 | 0.0029835 | 0.00074774 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_352-12_0_5_load_35 | 34 | 0.0020019 | 0.00050171 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_352-12_0_5_load_46 | 35 | 0.0049011 | 0.0012283 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_352-12_0_5_load_16 | 37 | 0.0042428 | 0.0010633 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_352-12_0_5_load_17 | 38 | 0.0012773 | 0.00032012 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_352-12_0_5_load_18 | 39 | 0.00082585 | 0.00020698 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_352-12_0_5_load_22 | 40 | 0.0066087 | 0.0016563 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_352-12_0_5_load_42 | 41 | 0.0033597 | 0.00084201 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_352-12_0_5_load_20 | 42 | 0.0059586 | 0.0014934 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_352-12_0_5_load_28 | 43 | 0.0028822 | 0.00072235 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_352-12_0_5_load_27 | 45 | 0.0058691 | 0.0014709 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_352-12_0_5_load_39 | 46 | 0.0058189 | 0.0014584 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_352-12_0_5_load_37 | 47 | 0.0069781 | 0.0017489 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_352-12_0_5_load_34 | 48 | 0.002103 | 0.00052707 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_352-12_0_5_load_38 | 49 | 0.0036185 | 0.00090687 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_352-12_0_5_load_30 | 50 | 0.0070004 | 0.0017545 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_352-12_0_5_load_31 | 51 | 0.0078112 | 0.0019577 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_352-12_0_5_load_40 | 53 | 0.0036277 | 0.00090918 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_352-12_0_5_load_65 | 54 | 0.0028881 | 0.00072382 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_352-12_0_5_load_52 | 56 | 0.0018027 | 0.00045179 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_352-12_0_5_load_68 | 57 | 0.0021387 | 0.000536 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_352-12_0_5_load_70 | 58 | 0.0018125 | 0.00045426 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_352-12_0_5_load_69 | 59 | 0.002303 | 0.00057718 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_352-12_0_5_load_53 | 61 | 0.0018326 | 0.00045929 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_352-12_0_5_load_54 | 62 | 0.0017849 | 0.00044734 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_352-12_0_5_load_56 | 63 | 0.0017191 | 0.00043084 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_352-12_0_5_load_55 | 64 | 0.0029132 | 0.00073012 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_352-12_0_5_load_57 | 65 | 0.003922 | 0.00098294 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_352-12_0_5_load_66 | 66 | 0.0018275 | 0.000458 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_352-12_0_5_load_67 | 67 | 0.0017717 | 0.00044404 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_352-12_0_5_load_59 | 68 | 0.0033371 | 0.00083635 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_352-12_0_5_load_58 | 69 | 0.0030693 | 0.00076925 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_352-12_0_5_load_60 | 70 | 0.0017943 | 0.0004497 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_352-12_0_5_load_62 | 71 | 0.0022643 | 0.0005675 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_352-12_0_5_line_0 |  | 0 | 1 | 0.066404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_352-12_0_5_line_1 |  | 0 | 2 | 0.18415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_352-12_0_5_line_2 |  | 1 | 3 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_352-12_0_5_line_3 |  | 2 | 4 | 0.0048646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_352-12_0_5_line_4 |  | 3 | 7 | 0.053899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_352-12_0_5_line_5 |  | 4 | 43 | 0.0082791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_352-12_0_5_line_6 |  | 5 | 6 | 0.010176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_352-12_0_5_line_7 |  | 6 | 42 | 0.023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_352-12_0_5_line_8 |  | 6 | 39 | 0.045043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_352-12_0_5_line_9 |  | 7 | 8 | 0.07724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_352-12_0_5_line_10 |  | 9 | 10 | 0.056173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_352-12_0_5_line_11 |  | 9 | 11 | 0.034126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_352-12_0_5_line_12 |  | 10 | 46 | 0.013411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_352-12_0_5_line_13 |  | 11 | 12 | 0.0065618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_352-12_0_5_line_14 |  | 12 | 45 | 0.020278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_352-12_0_5_line_15 |  | 13 | 14 | 0.023175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_352-12_0_5_line_16 |  | 14 | 18 | 0.055329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_352-12_0_5_line_17 |  | 14 | 19 | 0.020535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_352-12_0_5_line_18 |  | 15 | 16 | 0.017042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_352-12_0_5_line_19 |  | 15 | 17 | 0.02548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_352-12_0_5_line_20 |  | 16 | 20 | 0.013588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_352-12_0_5_line_21 |  | 16 | 21 | 0.037202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_352-12_0_5_line_22 |  | 17 | 22 | 0.010479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_352-12_0_5_line_23 |  | 18 | 23 | 0.018538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_352-12_0_5_line_24 |  | 18 | 24 | 0.02901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_352-12_0_5_line_25 |  | 19 | 25 | 0.0096053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_352-12_0_5_line_26 |  | 20 | 26 | 0.017788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_352-12_0_5_line_27 |  | 21 | 27 | 0.031063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_352-12_0_5_line_28 |  | 22 | 28 | 0.012449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_352-12_0_5_line_29 |  | 22 | 29 | 0.017891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_352-12_0_5_line_30 |  | 23 | 30 | 0.00014925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_352-12_0_5_line_31 |  | 25 | 31 | 0.00054764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_352-12_0_5_line_32 |  | 27 | 32 | 0.011267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_352-12_0_5_line_33 |  | 28 | 57 | 0.0072046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_352-12_0_5_line_34 |  | 29 | 55 | 0.011144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_352-12_0_5_line_35 |  | 30 | 54 | 0.00010929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_352-12_0_5_line_36 |  | 31 | 68 | 0.011677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_352-12_0_5_line_37 |  | 31 | 65 | 9.9698e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_352-12_0_5_line_38 |  | 32 | 33 | 0.030625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_352-12_0_5_line_39 |  | 32 | 34 | 0.041275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_352-12_0_5_line_40 |  | 33 | 35 | 0.014486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_352-12_0_5_line_41 |  | 34 | 36 | 0.030506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_352-12_0_5_line_42 |  | 36 | 48 | 0.022764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_352-12_0_5_line_43 |  | 36 | 50 | 0.012503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_352-12_0_5_line_44 |  | 37 | 38 | 0.028385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_352-12_0_5_line_45 |  | 38 | 39 | 0.0020362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_352-12_0_5_line_46 |  | 39 | 43 | 0.022378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_352-12_0_5_line_47 |  | 40 | 41 | 0.026632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_352-12_0_5_line_48 |  | 40 | 42 | 0.023117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_352-12_0_5_line_49 |  | 41 | 44 | 0.012689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_352-12_0_5_line_50 |  | 44 | 52 | 0.045013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_352-12_0_5_line_51 |  | 44 | 51 | 0.017355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_352-12_0_5_line_52 |  | 45 | 47 | 0.024134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_352-12_0_5_line_53 |  | 46 | 48 | 0.024551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_352-12_0_5_line_54 |  | 47 | 49 | 0.024609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_352-12_0_5_line_55 |  | 50 | 51 | 0.03018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_352-12_0_5_line_56 |  | 52 | 53 | 0.021257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_352-12_0_5_line_57 |  | 55 | 56 | 0.010705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_352-12_0_5_line_58 |  | 56 | 58 | 0.0072655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_352-12_0_5_line_59 |  | 57 | 59 | 0.0072285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_352-12_0_5_line_60 |  | 58 | 60 | 0.0065286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_352-12_0_5_line_61 |  | 59 | 71 | 0.0074377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_352-12_0_5_line_62 |  | 60 | 67 | 0.00065458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_352-12_0_5_line_63 |  | 61 | 62 | 0.007276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_352-12_0_5_line_64 |  | 62 | 63 | 0.0070476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_352-12_0_5_line_65 |  | 63 | 66 | 0.0071277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_352-12_0_5_line_66 |  | 64 | 65 | 0.017689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_352-12_0_5_line_67 |  | 66 | 67 | 0.0072299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_352-12_0_5_line_68 |  | 68 | 69 | 0.007278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_352-12_0_5_line_69 |  | 69 | 70 | 0.0070715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_352-12_0_5_line_70 |  | 70 | 71 | 0.0072698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_352-12_0_5_trafo_26 | 0.63 MVA 20/0.4 kV | 72 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2604657.1838 | 1201770.5723 | 2604601.6135 | 1201806.9238
1 | 2604652.2877 | 1201983.9652 | 2604601.6135 | 1201806.9238
2 | 2604657.1838 | 1201770.5723 | 2604667.2396 | 1201763.9936
3 | 2604648.55 | 1201987.0787 | 2604652.2877 | 1201983.9652
4 | 2604716.1102 | 1201741.7738 | 2604678.7395 | 1201756.4701 | 2604667.2396 | 1201763.9936
5 | 2604648.55 | 1201987.0787 | 2604642.1889 | 1201992.3777
6 | 2604664.6535 | 1202032.3971 | 2604656.6785 | 1202038.7171
7 | 2604638.6525 | 1202053.0021 | 2604656.6785 | 1202038.7171
8 | 2604656.6785 | 1202038.7171 | 2604624.9954 | 1202006.7002
9 | 2604716.1102 | 1201741.7738 | 2604731.948 | 1201817.3723
10 | 2604741.148 | 1202027.3678 | 2604747.8071 | 1202023.9571 | 2604792.9512 | 1202005.7143
11 | 2604792.9512 | 1202005.7143 | 2604811.0133 | 1201998.4154 | 2604824.9517 | 1201993.9232
12 | 2604729.2116 | 1202033.4816 | 2604741.148 | 1202027.3678
13 | 2604831.1972 | 1201991.9103 | 2604824.9517 | 1201993.9232
14 | 2604850.4977 | 1201985.6899 | 2604831.1972 | 1201991.9103
15 | 2604769.0292 | 1202094.4896 | 2604790.022 | 1202084.6733
16 | 2604769.0292 | 1202094.4896 | 2604741.0141 | 1202107.9638 | 2604735.22 | 1202111.6724 | 2604731.4503 | 1202115.2381 | 2604729.5602 | 1202118.9608 | 2604729.298 | 1202123.363 | 2604730.1627 | 1202126.9434
17 | 2604769.0292 | 1202094.4896 | 2604774.1113 | 1202105.822 | 2604777.8683 | 1202113.0157
18 | 2604824.8764 | 1202068.3753 | 2604829.3682 | 1202065.9331 | 2604831.9112 | 1202064.3232 | 2604833.9294 | 1202062.3793 | 2604835.4693 | 1202059.0454 | 2604835.692 | 1202056.5887
19 | 2604824.8764 | 1202068.3753 | 2604826.9218 | 1202070.5114 | 2604832.2125 | 1202068.2255 | 2604839.2331 | 1202083.4435
20 | 2604835.692 | 1202056.5887 | 2604848.509 | 1202052.0782
21 | 2604835.692 | 1202056.5887 | 2604834.7967 | 1202053.1972 | 2604832.4553 | 1202050.1048 | 2604829.4584 | 1202048.3348 | 2604826.3235 | 1202047.7653 | 2604806.7576 | 1202048.4946 | 2604803.197 | 1202048.7486
22 | 2604843.6229 | 1202092.9591 | 2604839.2331 | 1202083.4435
23 | 2604730.1627 | 1202126.9434 | 2604738.607 | 1202143.446
24 | 2604730.1627 | 1202126.9434 | 2604730.2487 | 1202133.825 | 2604740.4429 | 1202153.4653
25 | 2604777.8683 | 1202113.0157 | 2604782.3148 | 1202121.5298
26 | 2604865.2879 | 1202046.1734 | 2604848.509 | 1202052.0782
27 | 2604772.2123 | 1202050.9586 | 2604803.197 | 1202048.7486
28 | 2604843.6229 | 1202092.9591 | 2604832.3824 | 1202098.3085
29 | 2604843.6229 | 1202092.9591 | 2604850.879 | 1202109.3122
30 | 2604738.607 | 1202143.446 | 2604738.675 | 1202143.5789
31 | 2604782.3148 | 1202121.5298 | 2604782.5683 | 1202122.0152
32 | 2604760.9734 | 1202051.7602 | 2604772.2123 | 1202050.9586
33 | 2604832.3824 | 1202098.3085 | 2604825.8769 | 1202101.4045
34 | 2604854.1418 | 1202119.0705 | 2604855.002 | 1202118.6043 | 2604850.879 | 1202109.3122
35 | 2604738.675 | 1202143.5789 | 2604738.7248 | 1202143.6762
36 | 2604782.5683 | 1202122.0152 | 2604793.1124 | 1202116.9972
37 | 2604782.5683 | 1202122.0152 | 2604782.6124 | 1202122.1046
38 | 2604760.9734 | 1202051.7602 | 2604761.184 | 1202054.851 | 2604741.5732 | 1202074.1682
39 | 2604760.9734 | 1202051.7602 | 2604757.2214 | 1202052.0241 | 2604719.8545 | 1202055.3395
40 | 2604754.319 | 1202075.2566 | 2604753.2556 | 1202072.7544 | 2604741.5732 | 1202074.1682
41 | 2604689.586 | 1202059.0974 | 2604713.7502 | 1202055.8811 | 2604719.8545 | 1202055.3395
42 | 2604689.586 | 1202059.0974 | 2604695.1441 | 1202055.5554 | 2604708.135 | 1202045.9208
43 | 2604689.586 | 1202059.0974 | 2604680.174 | 1202067.3275
44 | 2604623.4309 | 1202008.0035 | 2604601.6214 | 1202026.1713
45 | 2604623.4309 | 1202008.0035 | 2604624.9954 | 1202006.7002
46 | 2604642.1889 | 1201992.3777 | 2604624.9954 | 1202006.7002
47 | 2604620.5344 | 1202067.36 | 2604620.5344 | 1202067.36 | 2604636.6919 | 1202088.5303
48 | 2604620.5344 | 1202067.36 | 2604638.6525 | 1202053.0021
49 | 2604644.3905 | 1202098.6173 | 2604636.6919 | 1202088.5303
50 | 2604644.3905 | 1202098.6173 | 2604638.1366 | 1202106.6836 | 2604633.9757 | 1202114.4624 | 2604631.8321 | 1202121.2755 | 2604630.091 | 1202129.1118 | 2604629.649 | 1202139.9284
51 | 2604644.3905 | 1202098.6173 | 2604657.455 | 1202087.1935
52 | 2604850.4977 | 1201985.6899 | 2604866.9617 | 1201980.3837 | 2604873.5842 | 1201978.6893
53 | 2604729.2116 | 1202033.4816 | 2604715.2993 | 1202040.6074 | 2604708.135 | 1202045.9208
54 | 2604897.4251 | 1201972.5898 | 2604873.5842 | 1201978.6893
55 | 2604680.174 | 1202067.3275 | 2604657.455 | 1202087.1935
56 | 2604629.649 | 1202139.9284 | 2604610.96 | 1202129.8008
57 | 2604854.1418 | 1202119.0705 | 2604844.4717 | 1202123.663
58 | 2604844.4717 | 1202123.663 | 2604837.9087 | 1202126.78
59 | 2604819.3498 | 1202104.5107 | 2604825.8769 | 1202101.4045
60 | 2604832.0114 | 1202129.5807 | 2604837.9087 | 1202126.78
61 | 2604812.6339 | 1202107.7069 | 2604819.3498 | 1202104.5107
62 | 2604831.4207 | 1202129.8627 | 2604832.0114 | 1202129.5807
63 | 2604805.5375 | 1202142.2186 | 2604812.1037 | 1202139.0841
64 | 2604812.1037 | 1202139.0841 | 2604818.4638 | 1202136.0479
65 | 2604818.4638 | 1202136.0479 | 2604824.8961 | 1202132.9773
66 | 2604782.6124 | 1202122.1046 | 2604790.4287 | 1202137.9731
67 | 2604831.4207 | 1202129.8627 | 2604824.8961 | 1202132.9773
68 | 2604799.6842 | 1202113.8697 | 2604793.1124 | 1202116.9972
69 | 2604799.6842 | 1202113.8697 | 2604806.0695 | 1202110.8309
70 | 2604812.6339 | 1202107.7069 | 2604806.0695 | 1202110.8309

## bus_geodata
| x | y | coords
0 | 2604601.6135 | 1201806.9238
1 | 2604657.1838 | 1201770.5723
2 | 2604652.2877 | 1201983.9652
3 | 2604667.2396 | 1201763.9936
4 | 2604648.55 | 1201987.0787
5 | 2604664.6535 | 1202032.3971
6 | 2604656.6785 | 1202038.7171
7 | 2604716.1102 | 1201741.7738
8 | 2604731.948 | 1201817.3723
9 | 2604792.9512 | 1202005.7143
10 | 2604741.148 | 1202027.3678
11 | 2604824.9517 | 1201993.9232
12 | 2604831.1972 | 1201991.9103
13 | 2604790.022 | 1202084.6733
14 | 2604769.0292 | 1202094.4896
15 | 2604824.8764 | 1202068.3753
16 | 2604835.692 | 1202056.5887
17 | 2604839.2331 | 1202083.4435
18 | 2604730.1627 | 1202126.9434
19 | 2604777.8683 | 1202113.0157
20 | 2604848.509 | 1202052.0782
21 | 2604803.197 | 1202048.7486
22 | 2604843.6229 | 1202092.9591
23 | 2604738.607 | 1202143.446
24 | 2604740.4429 | 1202153.4653
25 | 2604782.3148 | 1202121.5298
26 | 2604865.2879 | 1202046.1734
27 | 2604772.2123 | 1202050.9586
28 | 2604832.3824 | 1202098.3085
29 | 2604850.879 | 1202109.3122
30 | 2604738.675 | 1202143.5789
31 | 2604782.5683 | 1202122.0152
32 | 2604760.9734 | 1202051.7602
33 | 2604741.5732 | 1202074.1682
34 | 2604719.8545 | 1202055.3395
35 | 2604754.319 | 1202075.2566
36 | 2604689.586 | 1202059.0974
37 | 2604601.6214 | 1202026.1713
38 | 2604623.4309 | 1202008.0035
39 | 2604624.9954 | 1202006.7002
40 | 2604620.5344 | 1202067.36
41 | 2604636.6919 | 1202088.5303
42 | 2604638.6525 | 1202053.0021
43 | 2604642.1889 | 1201992.3777
44 | 2604644.3905 | 1202098.6173
45 | 2604850.4977 | 1201985.6899
46 | 2604729.2116 | 1202033.4816
47 | 2604873.5842 | 1201978.6893
48 | 2604708.135 | 1202045.9208
49 | 2604897.4251 | 1201972.5898
50 | 2604680.174 | 1202067.3275
51 | 2604657.455 | 1202087.1935
52 | 2604629.649 | 1202139.9284
53 | 2604610.96 | 1202129.8008
54 | 2604738.7248 | 1202143.6762
55 | 2604854.1418 | 1202119.0705
56 | 2604844.4717 | 1202123.663
57 | 2604825.8769 | 1202101.4045
58 | 2604837.9087 | 1202126.78
59 | 2604819.3498 | 1202104.5107
60 | 2604832.0114 | 1202129.5807
61 | 2604805.5375 | 1202142.2186
62 | 2604812.1037 | 1202139.0841
63 | 2604818.4638 | 1202136.0479
64 | 2604790.4287 | 1202137.9731
65 | 2604782.6124 | 1202122.1046
66 | 2604824.8961 | 1202132.9773
67 | 2604831.4207 | 1202129.8627
68 | 2604793.1124 | 1202116.9972
69 | 2604799.6842 | 1202113.8697
70 | 2604806.0695 | 1202110.8309
71 | 2604812.6339 | 1202107.7069
72 | 2604689.586 | 1202059.0974

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1