## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_352-13_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_352-13_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_352-13_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_352-13_0_6_node_52 | 0.4 | n |  | TRUE
4 | bus_LV_352-13_0_6_node_53 | 0.4 | n |  | TRUE
5 | bus_LV_352-13_0_6_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_352-13_0_6_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_352-13_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_352-13_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_352-13_0_6_node_83 | 0.4 | n |  | TRUE
10 | bus_LV_352-13_0_6_node_79 | 0.4 | n |  | TRUE
11 | bus_LV_352-13_0_6_node_86 | 0.4 | n |  | TRUE
12 | bus_LV_352-13_0_6_node_80 | 0.4 | n |  | TRUE
13 | bus_LV_352-13_0_6_node_81 | 0.4 | n |  | TRUE
14 | bus_LV_352-13_0_6_node_44 | 0.4 | n |  | TRUE
15 | bus_LV_352-13_0_6_node_76 | 0.4 | n |  | TRUE
16 | bus_LV_352-13_0_6_node_77 | 0.4 | n |  | TRUE
17 | bus_LV_352-13_0_6_node_33 | 0.4 | n |  | TRUE
18 | bus_LV_352-13_0_6_node_78 | 0.4 | n |  | TRUE
19 | bus_LV_352-13_0_6_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_352-13_0_6_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_352-13_0_6_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_352-13_0_6_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_352-13_0_6_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_352-13_0_6_node_149 | 0.4 | n |  | TRUE
25 | bus_LV_352-13_0_6_node_151 | 0.4 | n |  | TRUE
26 | bus_LV_352-13_0_6_node_135 | 0.4 | n |  | TRUE
27 | bus_LV_352-13_0_6_node_134 | 0.4 | n |  | TRUE
28 | bus_LV_352-13_0_6_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_352-13_0_6_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_352-13_0_6_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_352-13_0_6_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_352-13_0_6_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_352-13_0_6_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_352-13_0_6_node_16 | 0.4 | n |  | TRUE
35 | bus_LV_352-13_0_6_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_352-13_0_6_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_352-13_0_6_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_352-13_0_6_node_125 | 0.4 | n |  | TRUE
39 | bus_LV_352-13_0_6_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_352-13_0_6_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_352-13_0_6_node_42 | 0.4 | n |  | TRUE
42 | bus_LV_352-13_0_6_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_352-13_0_6_node_145 | 0.4 | n |  | TRUE
44 | bus_LV_352-13_0_6_node_123 | 0.4 | n |  | TRUE
45 | bus_LV_352-13_0_6_node_19 | 0.4 | n |  | TRUE
46 | bus_LV_352-13_0_6_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_352-13_0_6_node_147 | 0.4 | n |  | TRUE
48 | bus_LV_352-13_0_6_node_148 | 0.4 | n |  | TRUE
49 | bus_LV_352-13_0_6_node_146 | 0.4 | n |  | TRUE
50 | bus_LV_352-13_0_6_node_150 | 0.4 | n |  | TRUE
51 | bus_LV_352-13_0_6_node_143 | 0.4 | n |  | TRUE
52 | bus_LV_352-13_0_6_node_144 | 0.4 | n |  | TRUE
53 | bus_LV_352-13_0_6_node_27 | 0.4 | n |  | TRUE
54 | bus_LV_352-13_0_6_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_352-13_0_6_node_29 | 0.4 | n |  | TRUE
56 | bus_LV_352-13_0_6_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_352-13_0_6_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_352-13_0_6_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_352-13_0_6_node_31 | 0.4 | n |  | TRUE
60 | bus_LV_352-13_0_6_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_352-13_0_6_node_34 | 0.4 | n |  | TRUE
62 | bus_LV_352-13_0_6_node_85 | 0.4 | n |  | TRUE
63 | bus_LV_352-13_0_6_node_75 | 0.4 | n |  | TRUE
64 | bus_LV_352-13_0_6_node_70 | 0.4 | n |  | TRUE
65 | bus_LV_352-13_0_6_node_93 | 0.4 | n |  | TRUE
66 | bus_LV_352-13_0_6_node_73 | 0.4 | n |  | TRUE
67 | bus_LV_352-13_0_6_node_92 | 0.4 | n |  | TRUE
68 | bus_LV_352-13_0_6_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_352-13_0_6_node_68 | 0.4 | n |  | TRUE
70 | bus_LV_352-13_0_6_node_35 | 0.4 | n |  | TRUE
71 | bus_LV_352-13_0_6_node_36 | 0.4 | n |  | TRUE
72 | bus_LV_352-13_0_6_node_37 | 0.4 | n |  | TRUE
73 | bus_LV_352-13_0_6_node_38 | 0.4 | n |  | TRUE
74 | bus_LV_352-13_0_6_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_352-13_0_6_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_352-13_0_6_node_50 | 0.4 | n |  | TRUE
77 | bus_LV_352-13_0_6_node_41 | 0.4 | n |  | TRUE
78 | bus_LV_352-13_0_6_node_51 | 0.4 | n |  | TRUE
79 | bus_LV_352-13_0_6_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_352-13_0_6_node_46 | 0.4 | n |  | TRUE
81 | bus_LV_352-13_0_6_node_47 | 0.4 | n |  | TRUE
82 | bus_LV_352-13_0_6_node_48 | 0.4 | n |  | TRUE
83 | bus_LV_352-13_0_6_node_49 | 0.4 | n |  | TRUE
84 | bus_LV_352-13_0_6_node_154 | 0.4 | n |  | TRUE
85 | bus_LV_352-13_0_6_node_157 | 0.4 | n |  | TRUE
86 | bus_LV_352-13_0_6_node_155 | 0.4 | n |  | TRUE
87 | bus_LV_352-13_0_6_node_158 | 0.4 | n |  | TRUE
88 | bus_LV_352-13_0_6_node_162 | 0.4 | n |  | TRUE
89 | bus_LV_352-13_0_6_node_163 | 0.4 | n |  | TRUE
90 | bus_LV_352-13_0_6_node_54 | 0.4 | n |  | TRUE
91 | bus_LV_352-13_0_6_node_159 | 0.4 | n |  | TRUE
92 | bus_LV_352-13_0_6_node_160 | 0.4 | n |  | TRUE
93 | bus_LV_352-13_0_6_node_57 | 0.4 | n |  | TRUE
94 | bus_LV_352-13_0_6_node_58 | 0.4 | n |  | TRUE
95 | bus_LV_352-13_0_6_node_121 | 0.4 | n |  | TRUE
96 | bus_LV_352-13_0_6_node_156 | 0.4 | n |  | TRUE
97 | bus_LV_352-13_0_6_node_120 | 0.4 | n |  | TRUE
98 | bus_LV_352-13_0_6_node_130 | 0.4 | n |  | TRUE
99 | bus_LV_352-13_0_6_node_63 | 0.4 | n |  | TRUE
100 | bus_LV_352-13_0_6_node_129 | 0.4 | n |  | TRUE
101 | bus_LV_352-13_0_6_node_59 | 0.4 | n |  | TRUE
102 | bus_LV_352-13_0_6_node_60 | 0.4 | n |  | TRUE
103 | bus_LV_352-13_0_6_node_61 | 0.4 | n |  | TRUE
104 | bus_LV_352-13_0_6_node_62 | 0.4 | n |  | TRUE
105 | bus_LV_352-13_0_6_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_352-13_0_6_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_352-13_0_6_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_352-13_0_6_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_352-13_0_6_node_88 | 0.4 | n |  | TRUE
110 | bus_LV_352-13_0_6_node_64 | 0.4 | n |  | TRUE
111 | bus_LV_352-13_0_6_node_66 | 0.4 | n |  | TRUE
112 | bus_LV_352-13_0_6_node_91 | 0.4 | n |  | TRUE
113 | bus_LV_352-13_0_6_node_71 | 0.4 | n |  | TRUE
114 | bus_LV_352-13_0_6_node_72 | 0.4 | n |  | TRUE
115 | bus_LV_352-13_0_6_node_74 | 0.4 | n |  | TRUE
116 | bus_LV_352-13_0_6_node_89 | 0.4 | n |  | TRUE
117 | bus_LV_352-13_0_6_node_131 | 0.4 | n |  | TRUE
118 | bus_LV_352-13_0_6_node_95 | 0.4 | n |  | TRUE
119 | bus_LV_352-13_0_6_node_96 | 0.4 | n |  | TRUE
120 | bus_LV_352-13_0_6_node_118 | 0.4 | n |  | TRUE
121 | bus_LV_352-13_0_6_node_119 | 0.4 | n |  | TRUE
122 | bus_LV_352-13_0_6_node_132 | 0.4 | n |  | TRUE
123 | bus_LV_352-13_0_6_node_98 | 0.4 | n |  | TRUE
124 | bus_LV_352-13_0_6_node_99 | 0.4 | n |  | TRUE
125 | bus_LV_352-13_0_6_node_101 | 0.4 | n |  | TRUE
126 | bus_LV_352-13_0_6_node_100 | 0.4 | n |  | TRUE
127 | bus_LV_352-13_0_6_node_102 | 0.4 | n |  | TRUE
128 | bus_LV_352-13_0_6_node_114 | 0.4 | n |  | TRUE
129 | bus_LV_352-13_0_6_node_126 | 0.4 | n |  | TRUE
130 | bus_LV_352-13_0_6_node_107 | 0.4 | n |  | TRUE
131 | bus_LV_352-13_0_6_node_112 | 0.4 | n |  | TRUE
132 | bus_LV_352-13_0_6_node_103 | 0.4 | n |  | TRUE
133 | bus_LV_352-13_0_6_node_104 | 0.4 | n |  | TRUE
134 | bus_LV_352-13_0_6_node_105 | 0.4 | n |  | TRUE
135 | bus_LV_352-13_0_6_node_106 | 0.4 | n |  | TRUE
136 | bus_LV_352-13_0_6_node_139 | 0.4 | n |  | TRUE
137 | bus_LV_352-13_0_6_node_138 | 0.4 | n |  | TRUE
138 | bus_LV_352-13_0_6_node_108 | 0.4 | n |  | TRUE
139 | bus_LV_352-13_0_6_node_109 | 0.4 | n |  | TRUE
140 | bus_LV_352-13_0_6_node_110 | 0.4 | n |  | TRUE
141 | bus_LV_352-13_0_6_node_111 | 0.4 | n |  | TRUE
142 | bus_LV_352-13_0_6_node_113 | 0.4 | n |  | TRUE
143 | bus_LV_352-13_0_6_node_115 | 0.4 | n |  | TRUE
144 | bus_LV_352-13_0_6_node_153 | 0.4 | n |  | TRUE
145 | bus_LV_352-13_0_6_node_116 | 0.4 | n |  | TRUE
146 | bus_LV_352-13_0_6_node_117 | 0.4 | n |  | TRUE
147 | bus_LV_352-13_0_6_node_124 | 0.4 | n |  | TRUE
148 | bus_LV_352-13_0_6_node_128 | 0.4 | n |  | TRUE
149 | bus_LV_352-13_0_6_node_122 | 0.4 | n |  | TRUE
150 | bus_LV_352-13_0_6_node_127 | 0.4 | n |  | TRUE
151 | bus_LV_352-13_0_6_node_140 | 0.4 | n |  | TRUE
152 | bus_LV_352-13_0_6_node_141 | 0.4 | n |  | TRUE
153 | bus_LV_352-13_0_6_node_133 | 0.4 | n |  | TRUE
154 | bus_LV_352-13_0_6_node_136 | 0.4 | n |  | TRUE
155 | bus_LV_352-13_0_6_node_137 | 0.4 | n |  | TRUE
156 | bus_LV_352-13_0_6_node_142 | 0.4 | n |  | TRUE
157 | bus_LV_352-13_0_6_node_152 | 0.4 | n |  | TRUE
158 | bus_LV_352-13_0_6_node_170 | 0.4 | n |  | TRUE
159 | bus_LV_352-13_0_6_node_169 | 0.4 | n |  | TRUE
160 | bus_LV_352-13_0_6_node_161 | 0.4 | n |  | TRUE
161 | bus_LV_352-13_0_6_node_167 | 0.4 | n |  | TRUE
162 | bus_LV_352-13_0_6_node_165 | 0.4 | n |  | TRUE
163 | bus_LV_352-13_0_6_node_164 | 0.4 | n |  | TRUE
164 | bus_LV_352-13_0_6_node_166 | 0.4 | n |  | TRUE
165 | bus_LV_352-13_0_6_node_168 | 0.4 | n |  | TRUE
166 | bus_MV_602_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_352-13_0_6_load_0 | 0 | 0.007626 | 0.0019113 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_352-13_0_6_load_1 | 1 | 0.0046255 | 0.0011593 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_352-13_0_6_load_2 | 2 | 0.0027505 | 0.00068934 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_352-13_0_6_load_52 | 3 | 0.0025923 | 0.00064969 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_352-13_0_6_load_53 | 4 | 0.0023144 | 0.00058004 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_352-13_0_6_load_3 | 5 | 0.0049803 | 0.0012482 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_352-13_0_6_load_4 | 6 | 0.0043299 | 0.0010852 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_352-13_0_6_load_5 | 7 | 0.0071465 | 0.0017911 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_352-13_0_6_load_6 | 8 | 0.0037 | 0.00092732 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_352-13_0_6_load_83 | 9 | 0.0028993 | 0.00072664 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_352-13_0_6_load_79 | 10 | 0.0073341 | 0.0018381 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_352-13_0_6_load_86 | 11 | 0.0065024 | 0.0016297 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_352-13_0_6_load_80 | 12 | 0.0016167 | 0.00040519 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_352-13_0_6_load_81 | 13 | 0.0045065 | 0.0011294 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_352-13_0_6_load_76 | 15 | 0.00020868 | 5.2301e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_352-13_0_6_load_77 | 16 | 0.00021589 | 5.4107e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_352-13_0_6_load_33 | 17 | 0.0002211 | 5.5413e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_352-13_0_6_load_78 | 18 | 0.00020642 | 5.1734e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_352-13_0_6_load_7 | 19 | 0.0050983 | 0.0012778 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_352-13_0_6_load_8 | 20 | 0.0016319 | 0.000409 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_352-13_0_6_load_10 | 23 | 0.0028371 | 0.00071105 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_352-13_0_6_load_149 | 24 | 0.0028272 | 0.00070857 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_352-13_0_6_load_151 | 25 | 0.0027907 | 0.00069942 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_352-13_0_6_load_135 | 26 | 0.0026924 | 0.00067478 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_352-13_0_6_load_134 | 27 | 0.0024942 | 0.0006251 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_352-13_0_6_load_12 | 28 | 0.0086369 | 0.0021646 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_352-13_0_6_load_13 | 29 | 0.010593 | 0.0026549 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_352-13_0_6_load_15 | 31 | 0.010899 | 0.0027316 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_352-13_0_6_load_24 | 33 | 0.010642 | 0.0026671 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_352-13_0_6_load_55 | 36 | 0.0024978 | 0.000626 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_352-13_0_6_load_125 | 38 | 0.0042155 | 0.0010565 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_352-13_0_6_load_20 | 40 | 0.0085347 | 0.002139 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_352-13_0_6_load_42 | 41 | 0.0028562 | 0.00071584 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_352-13_0_6_load_145 | 43 | 0.0038147 | 0.00095604 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_352-13_0_6_load_19 | 45 | 0.01072 | 0.0026867 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_352-13_0_6_load_22 | 46 | 0.0059586 | 0.0014934 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_352-13_0_6_load_146 | 49 | 0.0039091 | 0.0009797 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_352-13_0_6_load_150 | 50 | 0.0065477 | 0.001641 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_352-13_0_6_load_143 | 51 | 0.0050519 | 0.0012661 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_352-13_0_6_load_27 | 53 | 0.0056684 | 0.0014206 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_352-13_0_6_load_28 | 54 | 0.010579 | 0.0026514 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_352-13_0_6_load_29 | 55 | 0.010141 | 0.0025416 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_352-13_0_6_load_67 | 56 | 0.0063012 | 0.0015792 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_352-13_0_6_load_65 | 57 | 0.0045777 | 0.0011473 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_352-13_0_6_load_30 | 58 | 0.00032415 | 8.124e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_352-13_0_6_load_31 | 59 | 0.0017312 | 0.00043388 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_352-13_0_6_load_32 | 60 | 0.0019743 | 0.00049482 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_352-13_0_6_load_34 | 61 | 0.0043674 | 0.0010946 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_352-13_0_6_load_85 | 62 | 0.0019227 | 0.00048186 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_352-13_0_6_load_75 | 63 | 0.0018168 | 0.00045533 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_352-13_0_6_load_70 | 64 | 0.0019087 | 0.00047837 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_352-13_0_6_load_93 | 65 | 0.0041602 | 0.0010426 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_352-13_0_6_load_73 | 66 | 0.0018356 | 0.00046004 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_352-13_0_6_load_92 | 67 | 0.0045263 | 0.0011344 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_352-13_0_6_load_69 | 68 | 0.0020026 | 0.0005019 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_352-13_0_6_load_68 | 69 | 0.0042732 | 0.001071 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_352-13_0_6_load_35 | 70 | 0.0018432 | 0.00046194 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_352-13_0_6_load_36 | 71 | 0.0019899 | 0.00049871 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_352-13_0_6_load_37 | 72 | 0.0019214 | 0.00048156 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_352-13_0_6_load_38 | 73 | 0.0026506 | 0.00066431 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_352-13_0_6_load_39 | 74 | 0.0016982 | 0.00042562 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_352-13_0_6_load_40 | 75 | 0.002191 | 0.00054911 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_352-13_0_6_load_50 | 76 | 0.002175 | 0.00054512 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_352-13_0_6_load_41 | 77 | 0.0018054 | 0.00045248 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_352-13_0_6_load_51 | 78 | 0.0017645 | 0.00044222 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_352-13_0_6_load_45 | 79 | 0.0024882 | 0.0006236 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_352-13_0_6_load_46 | 80 | 0.0025923 | 0.00064969 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_352-13_0_6_load_47 | 81 | 0.0017784 | 0.00044572 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_352-13_0_6_load_48 | 82 | 0.0015279 | 0.00038293 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_352-13_0_6_load_49 | 83 | 0.0015471 | 0.00038775 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_352-13_0_6_load_154 | 84 | 0.0016573 | 0.00041536 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_352-13_0_6_load_157 | 85 | 0.0015248 | 0.00038216 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_352-13_0_6_load_155 | 86 | 0.0021076 | 0.00052823 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_352-13_0_6_load_158 | 87 | 0.0037291 | 0.0009346 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_352-13_0_6_load_162 | 88 | 0.0016562 | 0.00041509 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_352-13_0_6_load_163 | 89 | 0.0026751 | 0.00067043 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_352-13_0_6_load_54 | 90 | 0.0029514 | 0.00073968 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_352-13_0_6_load_159 | 91 | 0.0030704 | 0.00076952 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_352-13_0_6_load_160 | 92 | 0.0025126 | 0.00062971 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_352-13_0_6_load_57 | 93 | 0.0033592 | 0.0008419 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_352-13_0_6_load_121 | 95 | 0.0041505 | 0.0010402 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_352-13_0_6_load_156 | 96 | 0.0015974 | 0.00040033 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_352-13_0_6_load_120 | 97 | 0.004382 | 0.0010982 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_352-13_0_6_load_130 | 98 | 0.0017353 | 0.00043492 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_352-13_0_6_load_63 | 99 | 0.0015487 | 0.00038814 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_352-13_0_6_load_129 | 100 | 0.0036643 | 0.00091836 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_352-13_0_6_load_59 | 101 | 0.0018953 | 0.00047501 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_352-13_0_6_load_60 | 102 | 0.0017966 | 0.00045026 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_352-13_0_6_load_61 | 103 | 0.0014098 | 0.00035333 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_352-13_0_6_load_90 | 105 | 0.0057543 | 0.0014422 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_352-13_0_6_load_87 | 106 | 0.0024303 | 0.00060908 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_352-13_0_6_load_97 | 107 | 0.0049383 | 0.0012377 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_352-13_0_6_load_94 | 108 | 0.0032426 | 0.00081268 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_352-13_0_6_load_88 | 109 | 0.002058 | 0.00051579 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_352-13_0_6_load_64 | 110 | 0.0042002 | 0.0010527 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_352-13_0_6_load_66 | 111 | 0.0066134 | 0.0016575 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_352-13_0_6_load_91 | 112 | 0.004202 | 0.0010531 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_352-13_0_6_load_71 | 113 | 0.0021439 | 0.00053731 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_352-13_0_6_load_72 | 114 | 0.0018911 | 0.00047397 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_352-13_0_6_load_74 | 115 | 0.0020165 | 0.00050539 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_352-13_0_6_load_89 | 116 | 0.0023843 | 0.00059757 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_352-13_0_6_load_131 | 117 | 0.004601 | 0.0011531 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_352-13_0_6_load_95 | 118 | 0.0036009 | 0.00090248 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_352-13_0_6_load_96 | 119 | 0.0024438 | 0.00061247 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_352-13_0_6_load_118 | 120 | 0.003071 | 0.00076966 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_352-13_0_6_load_119 | 121 | 0.0036817 | 0.00092273 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_352-13_0_6_load_132 | 122 | 0.0058497 | 0.0014661 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_352-13_0_6_load_98 | 123 | 0.0040046 | 0.0010037 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_352-13_0_6_load_99 | 124 | 0.0036201 | 0.00090728 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_352-13_0_6_load_101 | 125 | 0.0034596 | 0.00086707 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_352-13_0_6_load_100 | 126 | 0.0047734 | 0.0011963 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_352-13_0_6_load_102 | 127 | 0.0046038 | 0.0011538 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_352-13_0_6_load_126 | 129 | 0.0045957 | 0.0011518 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_352-13_0_6_load_112 | 131 | 0.0035983 | 0.00090182 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_352-13_0_6_load_103 | 132 | 0.0033456 | 0.0008385 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_352-13_0_6_load_104 | 133 | 0.0033809 | 0.00084733 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_352-13_0_6_load_105 | 134 | 0.003124 | 0.00078295 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_352-13_0_6_load_106 | 135 | 0.0032941 | 0.00082557 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_352-13_0_6_load_138 | 137 | 0.0036985 | 0.00092693 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_352-13_0_6_load_108 | 138 | 0.0047878 | 0.0011999 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_352-13_0_6_load_109 | 139 | 0.0046946 | 0.0011766 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_352-13_0_6_load_111 | 141 | 0.0050499 | 0.0012656 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_352-13_0_6_load_113 | 142 | 0.0037998 | 0.00095232 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_352-13_0_6_load_115 | 143 | 0.0046358 | 0.0011618 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_352-13_0_6_load_153 | 144 | 0.0033506 | 0.00083974 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_352-13_0_6_load_116 | 145 | 0.0039724 | 0.00099557 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_352-13_0_6_load_124 | 147 | 0.0042364 | 0.0010617 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_352-13_0_6_load_128 | 148 | 0.00417 | 0.0010451 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_352-13_0_6_load_127 | 150 | 0.0033624 | 0.00084269 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_352-13_0_6_load_140 | 151 | 0.0024679 | 0.00061852 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_352-13_0_6_load_141 | 152 | 0.0027657 | 0.00069316 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_352-13_0_6_load_133 | 153 | 0.0032316 | 0.00080991 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_352-13_0_6_load_136 | 154 | 0.0037654 | 0.00094369 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_352-13_0_6_load_137 | 155 | 0.0031773 | 0.00079631 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_352-13_0_6_load_152 | 157 | 0.0025352 | 0.00063539 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_352-13_0_6_load_170 | 158 | 0.001427 | 0.00035765 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_352-13_0_6_load_169 | 159 | 0.0013706 | 0.00034351 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_352-13_0_6_load_161 | 160 | 0.0039423 | 0.00098804 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_352-13_0_6_load_167 | 161 | 0.0025347 | 0.00063525 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_352-13_0_6_load_165 | 162 | 0.002629 | 0.00065889 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_352-13_0_6_load_164 | 163 | 0.0029054 | 0.00072817 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_352-13_0_6_load_166 | 164 | 0.0094477 | 0.0023678 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_352-13_0_6_load_168 | 165 | 0.0024226 | 0.00060717 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_352-13_0_6_line_0 |  | 0 | 1 | 0.015999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_352-13_0_6_line_1 |  | 1 | 2 | 0.00069445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_352-13_0_6_line_2 |  | 2 | 3 | 0.0068324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_352-13_0_6_line_3 |  | 3 | 4 | 0.00035778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_352-13_0_6_line_4 |  | 4 | 90 | 0.0058752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_352-13_0_6_line_5 |  | 5 | 6 | 0.017698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_352-13_0_6_line_6 |  | 5 | 7 | 0.0092683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_352-13_0_6_line_7 |  | 6 | 8 | 0.0084794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_352-13_0_6_line_8 |  | 7 | 9 | 0.037094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_352-13_0_6_line_9 |  | 7 | 10 | 0.046471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_352-13_0_6_line_10 |  | 8 | 13 | 0.0084852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_352-13_0_6_line_11 |  | 9 | 11 | 0.020105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_352-13_0_6_line_12 |  | 9 | 12 | 0.0073931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_352-13_0_6_line_13 |  | 10 | 18 | 0.008823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_352-13_0_6_line_14 |  | 11 | 14 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_352-13_0_6_line_15 |  | 12 | 115 | 0.015972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_352-13_0_6_line_16 |  | 14 | 35 | 0.03405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_352-13_0_6_line_17 |  | 15 | 16 | 0.0050625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_352-13_0_6_line_18 |  | 15 | 17 | 0.013295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_352-13_0_6_line_19 |  | 16 | 18 | 0.0062245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_352-13_0_6_line_20 |  | 17 | 59 | 0.0036325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_352-13_0_6_line_21 |  | 19 | 20 | 0.002039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_352-13_0_6_line_22 |  | 19 | 21 | 0.020787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_352-13_0_6_line_23 |  | 21 | 22 | 0.020943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_352-13_0_6_line_24 |  | 22 | 24 | 0.0074841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_352-13_0_6_line_25 |  | 22 | 26 | 0.025521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_352-13_0_6_line_26 |  | 23 | 24 | 0.026283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_352-13_0_6_line_27 |  | 23 | 25 | 0.017862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_352-13_0_6_line_28 |  | 26 | 27 | 0.02782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_352-13_0_6_line_29 |  | 27 | 153 | 0.026856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_352-13_0_6_line_30 |  | 28 | 29 | 0.016203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_352-13_0_6_line_31 |  | 28 | 30 | 0.0124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_352-13_0_6_line_32 |  | 29 | 31 | 0.015308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_352-13_0_6_line_33 |  | 30 | 32 | 0.026104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_352-13_0_6_line_34 |  | 31 | 33 | 0.016371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_352-13_0_6_line_35 |  | 32 | 37 | 0.032992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_352-13_0_6_line_36 |  | 32 | 38 | 0.016232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_352-13_0_6_line_37 |  | 34 | 35 | 0.013995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_352-13_0_6_line_38 |  | 34 | 36 | 0.022663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_352-13_0_6_line_39 |  | 35 | 41 | 0.0066724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_352-13_0_6_line_40 |  | 36 | 42 | 0.010335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_352-13_0_6_line_41 |  | 37 | 39 | 0.013077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_352-13_0_6_line_42 |  | 37 | 40 | 0.01337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_352-13_0_6_line_43 |  | 38 | 44 | 0.011516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_352-13_0_6_line_44 |  | 39 | 43 | 0.005321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_352-13_0_6_line_45 |  | 40 | 45 | 0.0095899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_352-13_0_6_line_46 |  | 41 | 77 | 0.0078789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_352-13_0_6_line_47 |  | 42 | 93 | 0.025464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_352-13_0_6_line_48 |  | 42 | 94 | 0.003878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_352-13_0_6_line_49 |  | 44 | 129 | 0.011918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_352-13_0_6_line_50 |  | 44 | 149 | 0.009177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_352-13_0_6_line_51 |  | 46 | 47 | 0.010292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_352-13_0_6_line_52 |  | 47 | 48 | 0.028836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_352-13_0_6_line_53 |  | 47 | 49 | 0.0020224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_352-13_0_6_line_54 |  | 48 | 50 | 0.022815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_352-13_0_6_line_55 |  | 48 | 136 | 0.005929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_352-13_0_6_line_56 |  | 49 | 52 | 0.011368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_352-13_0_6_line_57 |  | 51 | 52 | 0.021796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_352-13_0_6_line_58 |  | 53 | 54 | 0.027022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_352-13_0_6_line_59 |  | 54 | 55 | 0.014523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_352-13_0_6_line_60 |  | 55 | 56 | 0.014123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_352-13_0_6_line_61 |  | 56 | 57 | 0.0075502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_352-13_0_6_line_62 |  | 57 | 110 | 0.0061032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_352-13_0_6_line_63 |  | 58 | 59 | 0.0030163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_352-13_0_6_line_64 |  | 58 | 60 | 0.0019587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_352-13_0_6_line_65 |  | 60 | 61 | 0.011341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_352-13_0_6_line_66 |  | 61 | 65 | 0.0049094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_352-13_0_6_line_67 |  | 62 | 63 | 0.0060028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_352-13_0_6_line_68 |  | 62 | 64 | 0.0061774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_352-13_0_6_line_69 |  | 63 | 66 | 0.01394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_352-13_0_6_line_70 |  | 64 | 68 | 0.0061602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_352-13_0_6_line_71 |  | 65 | 67 | 0.013349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_352-13_0_6_line_72 |  | 66 | 113 | 0.0061374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_352-13_0_6_line_73 |  | 67 | 112 | 0.0049892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_352-13_0_6_line_74 |  | 68 | 69 | 0.015953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_352-13_0_6_line_75 |  | 69 | 111 | 0.0032046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_352-13_0_6_line_76 |  | 70 | 71 | 0.006113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_352-13_0_6_line_77 |  | 70 | 72 | 0.0061594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_352-13_0_6_line_78 |  | 71 | 73 | 0.017524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_352-13_0_6_line_79 |  | 72 | 74 | 0.0060835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_352-13_0_6_line_80 |  | 73 | 75 | 0.0078527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_352-13_0_6_line_81 |  | 74 | 76 | 0.018781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_352-13_0_6_line_82 |  | 75 | 77 | 0.0064917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_352-13_0_6_line_83 |  | 76 | 78 | 0.0065108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_352-13_0_6_line_84 |  | 78 | 88 | 0.006194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_352-13_0_6_line_85 |  | 79 | 80 | 0.012536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_352-13_0_6_line_86 |  | 79 | 81 | 0.0072129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_352-13_0_6_line_87 |  | 80 | 82 | 0.0075928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_352-13_0_6_line_88 |  | 81 | 83 | 0.00079738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_352-13_0_6_line_89 |  | 82 | 84 | 0.0061701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_352-13_0_6_line_90 |  | 83 | 85 | 0.0056964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_352-13_0_6_line_91 |  | 84 | 86 | 0.015158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_352-13_0_6_line_92 |  | 85 | 87 | 0.001788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_352-13_0_6_line_93 |  | 86 | 96 | 0.0040083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_352-13_0_6_line_94 |  | 87 | 160 | 0.0057318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_352-13_0_6_line_95 |  | 88 | 89 | 0.011053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_352-13_0_6_line_96 |  | 89 | 161 | 0.013808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_352-13_0_6_line_97 |  | 90 | 91 | 0.00039805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_352-13_0_6_line_98 |  | 91 | 92 | 0.0057457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_352-13_0_6_line_99 |  | 92 | 160 | 0.008367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_352-13_0_6_line_100 |  | 93 | 95 | 0.013313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_352-13_0_6_line_101 |  | 94 | 96 | 0.012372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_352-13_0_6_line_102 |  | 95 | 97 | 0.013284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_352-13_0_6_line_103 |  | 97 | 149 | 0.0094952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_352-13_0_6_line_104 |  | 98 | 99 | 0.0043796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_352-13_0_6_line_105 |  | 98 | 100 | 0.029265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_352-13_0_6_line_106 |  | 99 | 103 | 0.0032841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_352-13_0_6_line_107 |  | 100 | 150 | 0.013502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_352-13_0_6_line_108 |  | 101 | 102 | 0.0099592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_352-13_0_6_line_109 |  | 101 | 103 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_352-13_0_6_line_110 |  | 102 | 104 | 0.009533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_352-13_0_6_line_111 |  | 104 | 105 | 0.028604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_352-13_0_6_line_112 |  | 104 | 106 | 0.015584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_352-13_0_6_line_113 |  | 105 | 107 | 0.028249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_352-13_0_6_line_114 |  | 105 | 108 | 0.016224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_352-13_0_6_line_115 |  | 106 | 109 | 0.014962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_352-13_0_6_line_116 |  | 107 | 117 | 0.010907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_352-13_0_6_line_117 |  | 108 | 118 | 0.0045266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_352-13_0_6_line_118 |  | 109 | 116 | 0.0063161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_352-13_0_6_line_119 |  | 110 | 111 | 0.0028064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_352-13_0_6_line_120 |  | 113 | 114 | 0.006164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_352-13_0_6_line_121 |  | 114 | 115 | 0.0060224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_352-13_0_6_line_122 |  | 117 | 122 | 0.010613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_352-13_0_6_line_123 |  | 118 | 119 | 0.014822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_352-13_0_6_line_124 |  | 119 | 120 | 0.017709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_352-13_0_6_line_125 |  | 120 | 121 | 0.024097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_352-13_0_6_line_126 |  | 121 | 151 | 0.023131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_352-13_0_6_line_127 |  | 122 | 153 | 0.022791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_352-13_0_6_line_128 |  | 123 | 124 | 0.012492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_352-13_0_6_line_129 |  | 124 | 125 | 0.012653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_352-13_0_6_line_130 |  | 125 | 128 | 0.0044731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_352-13_0_6_line_131 |  | 126 | 127 | 0.012166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_352-13_0_6_line_132 |  | 127 | 129 | 0.012386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_352-13_0_6_line_133 |  | 128 | 130 | 0.022572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_352-13_0_6_line_134 |  | 128 | 131 | 0.013442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_352-13_0_6_line_135 |  | 130 | 136 | 0.021935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_352-13_0_6_line_136 |  | 130 | 134 | 0.019925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_352-13_0_6_line_137 |  | 131 | 140 | 0.010606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_352-13_0_6_line_138 |  | 132 | 133 | 0.012451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_352-13_0_6_line_139 |  | 132 | 134 | 0.012248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_352-13_0_6_line_140 |  | 133 | 135 | 0.017562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_352-13_0_6_line_141 |  | 136 | 137 | 0.02171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_352-13_0_6_line_142 |  | 137 | 154 | 0.012855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_352-13_0_6_line_143 |  | 138 | 139 | 0.012282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_352-13_0_6_line_144 |  | 138 | 140 | 0.021559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_352-13_0_6_line_145 |  | 139 | 141 | 0.021617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_352-13_0_6_line_146 |  | 140 | 142 | 0.017128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_352-13_0_6_line_147 |  | 141 | 143 | 0.011729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_352-13_0_6_line_148 |  | 142 | 144 | 0.015817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_352-13_0_6_line_149 |  | 143 | 145 | 0.012121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_352-13_0_6_line_150 |  | 145 | 146 | 0.014226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_352-13_0_6_line_151 |  | 146 | 147 | 0.0061543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
152 | LV_352-13_0_6_line_152 |  | 146 | 148 | 0.018826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_352-13_0_6_line_153 |  | 147 | 149 | 0.016134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
154 | LV_352-13_0_6_line_154 |  | 148 | 150 | 0.013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_352-13_0_6_line_155 |  | 151 | 152 | 0.02411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_352-13_0_6_line_156 |  | 152 | 156 | 0.014593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_352-13_0_6_line_157 |  | 154 | 155 | 0.012401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_352-13_0_6_line_158 |  | 156 | 157 | 0.03256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_352-13_0_6_line_159 |  | 157 | 158 | 0.0018067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_352-13_0_6_line_160 |  | 158 | 159 | 0.0063731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_352-13_0_6_line_161 |  | 159 | 165 | 0.00079128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_352-13_0_6_line_162 |  | 161 | 162 | 0.0059639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_352-13_0_6_line_163 |  | 162 | 163 | 0.0062793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_352-13_0_6_line_164 |  | 163 | 164 | 0.0067784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_352-13_0_6_trafo_55 | 0.63 MVA 20/0.4 kV | 166 | 36 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2603848.7833 | 1202557.563 | 2603864.6157 | 1202555.2623
1 | 2603864.6157 | 1202555.2623 | 2603864.6157 | 1202555.2623 | 2603865.3014 | 1202555.1526
2 | 2603865.3014 | 1202555.1526 | 2603872.048 | 1202554.073
3 | 2603872.048 | 1202554.073 | 2603872.4013 | 1202554.0165
4 | 2603878.2027 | 1202553.0882 | 2603872.4013 | 1202554.0165
5 | 2603987.5402 | 1202428.783 | 2603997.0803 | 1202426.267 | 2604004.8848 | 1202426.9172
6 | 2603978.5784 | 1202431.1464 | 2603987.5402 | 1202428.783
7 | 2604013.3349 | 1202427.6211 | 2604004.8848 | 1202426.9172
8 | 2603979.4273 | 1202468.2312 | 2603978.5784 | 1202431.1464
9 | 2603978.5784 | 1202431.1464 | 2603939.5732 | 1202405.8852
10 | 2604013.3349 | 1202427.6211 | 2604021.7909 | 1202428.3255
11 | 2603979.4273 | 1202468.2312 | 2603999.4714 | 1202469.7922 | 2603999.4714 | 1202469.7922
12 | 2603972.045 | 1202467.9628 | 2603975.8605 | 1202467.9534 | 2603979.4273 | 1202468.2312
13 | 2603937.4405 | 1202397.3236 | 2603939.5732 | 1202405.8852
14 | 2604013.2641 | 1202474.7484 | 2603999.4714 | 1202469.7922
15 | 2603972.045 | 1202467.9628 | 2603956.0731 | 1202468.0019
16 | 2603998.3599 | 1202505.3773 | 2604013.2641 | 1202474.7484
17 | 2603926.5039 | 1202400.1141 | 2603931.4092 | 1202398.8625
18 | 2603926.5039 | 1202400.1141 | 2603913.6211 | 1202403.4012
19 | 2603937.4405 | 1202397.3236 | 2603931.4092 | 1202398.8625
20 | 2603910.1014 | 1202404.2993 | 2603913.6211 | 1202403.4012
21 | 2604121.3026 | 1202683.7006 | 2604120.257 | 1202681.9501
22 | 2604109.5248 | 1202664.1485 | 2604114.2676 | 1202671.9225 | 2604120.257 | 1202681.9501
23 | 2604106.6925 | 1202644.0357 | 2604105.5695 | 1202650.6051 | 2604105.7496 | 1202654.3073 | 2604106.5618 | 1202657.3761 | 2604107.8227 | 1202660.6121 | 2604109.5248 | 1202664.1485
24 | 2604106.6925 | 1202644.0357 | 2604113.5326 | 1202645.0297 | 2604114.1034 | 1202645.069
25 | 2604106.6925 | 1202644.0357 | 2604099.6095 | 1202642.3077 | 2604091.4313 | 1202639.8009 | 2604083.3983 | 1202636.3158 | 2604082.5577 | 1202635.9429
26 | 2604140.2949 | 1202644.0029 | 2604131.437 | 1202645.1308 | 2604125.8288 | 1202645.3938 | 2604119.9012 | 1202645.4676 | 2604114.1034 | 1202645.069
27 | 2604140.2949 | 1202644.0029 | 2604157.993 | 1202641.5889
28 | 2604057.127 | 1202624.6624 | 2604082.5577 | 1202635.9429
29 | 2604057.127 | 1202624.6624 | 2604038.4942 | 1202616.3972 | 2604032.3258 | 1202614.4386
30 | 2604041.8014 | 1202508.7749 | 2604042.196 | 1202507.8632 | 2604045.873 | 1202505.4199 | 2604049.5478 | 1202495.2703
31 | 2604036.8765 | 1202520.1552 | 2604041.8014 | 1202508.7749
32 | 2604049.5478 | 1202495.2703 | 2604049.5551 | 1202495.2502 | 2604055.6742 | 1202493.6201 | 2604058.9442 | 1202485.2844 | 2604058.9442 | 1202485.2844
33 | 2604036.8765 | 1202520.1552 | 2604046.3655 | 1202519.9614 | 2604045.7498 | 1202530.4667 | 2604051.3487 | 1202532.8606
34 | 2604069.5248 | 1202473.6015 | 2604066.5037 | 1202480.2089 | 2604058.9442 | 1202485.2844
35 | 2604051.3487 | 1202532.8606 | 2604054.4403 | 1202529.4831 | 2604054.1881 | 1202519.7888 | 2604072.8998 | 1202519.4344
36 | 2604051.3487 | 1202532.8606 | 2604044.8221 | 1202547.7226
37 | 2603998.3599 | 1202505.3773 | 2603992.3325 | 1202518.0135
38 | 2603992.3325 | 1202518.0135 | 2603989.3229 | 1202523.9481 | 2603979.124 | 1202536.288
39 | 2603998.3599 | 1202505.3773 | 2603991.6881 | 1202505.4627
40 | 2603972.5462 | 1202544.2592 | 2603978.707 | 1202536.7925 | 2603979.124 | 1202536.288
41 | 2604072.8998 | 1202519.4344 | 2604073.1977 | 1202529.062 | 2604075.1362 | 1202531.9093
42 | 2604072.8998 | 1202519.4344 | 2604086.2675 | 1202519.1675
43 | 2604040.1916 | 1202558.2669 | 2604044.8221 | 1202547.7226
44 | 2604079.9514 | 1202534.2027 | 2604075.1362 | 1202531.9093
45 | 2604095.8555 | 1202518.9761 | 2604086.2675 | 1202519.1675
46 | 2603991.6881 | 1202505.4627 | 2603983.8098 | 1202505.5636
47 | 2603972.5462 | 1202544.2592 | 2603991.7007 | 1202553.1543 | 2603996.0453 | 1202553.0854
48 | 2603972.5462 | 1202544.2592 | 2603969.9647 | 1202547.1591
49 | 2604040.1916 | 1202558.2669 | 2604051.2776 | 1202562.642
50 | 2604040.1916 | 1202558.2669 | 2604031.6867 | 1202554.7594
51 | 2604120.6472 | 1202544.0466 | 2604124.5046 | 1202534.5051
52 | 2604147.379 | 1202555.0485 | 2604120.6472 | 1202544.0466
53 | 2604120.6472 | 1202544.0466 | 2604119.8625 | 1202545.9106
54 | 2604147.379 | 1202555.0485 | 2604155.7013 | 1202558.4672 | 2604161.5878 | 1202545.9662
55 | 2604147.379 | 1202555.0485 | 2604145.7923 | 1202560.7616
56 | 2604115.6318 | 1202556.461 | 2604118.2845 | 1202549.6591 | 2604119.8625 | 1202545.9106
57 | 2604115.6318 | 1202556.461 | 2604113.867 | 1202555.7594 | 2604095.3602 | 1202548.4533
58 | 2603816.2064 | 1202489.6704 | 2603842.6247 | 1202483.9901
59 | 2603842.6247 | 1202483.9901 | 2603856.823 | 1202480.9373
60 | 2603870.6685 | 1202478.1678 | 2603866.7112 | 1202478.8112 | 2603856.823 | 1202480.9373
61 | 2603870.6685 | 1202478.1678 | 2603878.1209 | 1202476.9561
62 | 2603884.145 | 1202475.9767 | 2603878.1209 | 1202476.9561
63 | 2603907.1788 | 1202405.045 | 2603910.1014 | 1202404.2993
64 | 2603907.1788 | 1202405.045 | 2603905.2809 | 1202405.5293
65 | 2603894.19 | 1202407.8396 | 2603899.6301 | 1202406.9711 | 2603905.2809 | 1202405.5293
66 | 2603894.19 | 1202407.8396 | 2603889.3419 | 1202408.6135
67 | 2603918.002 | 1202470.472 | 2603923.9269 | 1202469.5087
68 | 2603918.002 | 1202470.472 | 2603911.9046 | 1202471.4634
69 | 2603937.7494 | 1202468.0468 | 2603932.8442 | 1202468.0589 | 2603923.9269 | 1202469.5087
70 | 2603911.9046 | 1202471.4634 | 2603905.8243 | 1202472.4519
71 | 2603876.1595 | 1202410.7179 | 2603889.3419 | 1202408.6135
72 | 2603943.8868 | 1202468.0318 | 2603937.7494 | 1202468.0468
73 | 2603871.2327 | 1202411.5044 | 2603876.1595 | 1202410.7179
74 | 2603890.0781 | 1202475.012 | 2603905.8243 | 1202472.4519
75 | 2603886.915 | 1202475.5263 | 2603890.0781 | 1202475.012
76 | 2603945.8312 | 1202506.0497 | 2603951.9437 | 1202505.9715
77 | 2603945.8312 | 1202506.0497 | 2603939.6723 | 1202506.1285
78 | 2603969.4666 | 1202505.7472 | 2603951.9437 | 1202505.9715
79 | 2603933.5893 | 1202506.2064 | 2603939.6723 | 1202506.1285
80 | 2603969.4666 | 1202505.7472 | 2603977.3186 | 1202505.6467
81 | 2603914.9747 | 1202508.3135 | 2603927.2874 | 1202506.2871 | 2603933.5893 | 1202506.2064
82 | 2603983.8098 | 1202505.5636 | 2603977.3186 | 1202505.6467
83 | 2603908.5504 | 1202509.3708 | 2603914.9747 | 1202508.3135
84 | 2603908.5504 | 1202509.3708 | 2603902.4386 | 1202510.3767
85 | 2603925.8927 | 1202545.6083 | 2603913.505 | 1202547.5298
86 | 2603906.3773 | 1202548.6353 | 2603913.505 | 1202547.5298
87 | 2603933.4209 | 1202544.6434 | 2603929.8953 | 1202544.9874 | 2603925.8927 | 1202545.6083
88 | 2603905.5894 | 1202548.7576 | 2603906.3773 | 1202548.6353
89 | 2603939.5618 | 1202544.044 | 2603933.4209 | 1202544.6434
90 | 2603905.5894 | 1202548.7576 | 2603899.9603 | 1202549.6307
91 | 2603939.5618 | 1202544.044 | 2603954.6483 | 1202542.5717
92 | 2603898.1933 | 1202549.9048 | 2603899.9603 | 1202549.6307
93 | 2603954.6483 | 1202542.5717 | 2603958.6376 | 1202542.1823 | 2603958.6376 | 1202542.1823
94 | 2603898.1933 | 1202549.9048 | 2603895.0638 | 1202550.3902 | 2603892.5312 | 1202550.7954
95 | 2603902.4386 | 1202510.3767 | 2603891.5322 | 1202512.1716
96 | 2603891.5322 | 1202512.1716 | 2603884.8301 | 1202513.2747 | 2603877.9545 | 1202514.6692
97 | 2603878.2027 | 1202553.0882 | 2603878.5957 | 1202553.0253
98 | 2603884.2693 | 1202552.1174 | 2603878.5957 | 1202553.0253
99 | 2603884.2693 | 1202552.1174 | 2603892.5312 | 1202550.7954
100 | 2604009.357 | 1202552.8743 | 2603996.0453 | 1202553.0854
101 | 2603969.9647 | 1202547.1591 | 2603958.6376 | 1202542.1823
102 | 2604009.357 | 1202552.8743 | 2604022.6389 | 1202552.6636
103 | 2604031.6867 | 1202554.7594 | 2604026.6888 | 1202552.5993 | 2604022.6389 | 1202552.6636
104 | 2603949.1962 | 1202574.5937 | 2603947.1582 | 1202578.4702
105 | 2603949.1962 | 1202574.5937 | 2603978.4583 | 1202574.988
106 | 2603947.1582 | 1202578.4702 | 2603945.6299 | 1202581.377
107 | 2603978.4583 | 1202574.988 | 2603991.9593 | 1202575.1699
108 | 2603936.7667 | 1202599.2483 | 2603934.3125 | 1202608.9004
109 | 2603945.6299 | 1202581.377 | 2603937.2653 | 1202597.2872 | 2603936.7667 | 1202599.2483
110 | 2603931.9633 | 1202618.1395 | 2603934.3125 | 1202608.9004
111 | 2603960.4773 | 1202615.0118 | 2603946.1177 | 1202616.4699 | 2603931.9633 | 1202618.1395
112 | 2603931.9633 | 1202618.1395 | 2603916.6524 | 1202621.045
113 | 2603960.4773 | 1202615.0118 | 2603988.5183 | 1202611.5882
114 | 2603960.4773 | 1202615.0118 | 2603961.3163 | 1202631.2142
115 | 2603916.6524 | 1202621.045 | 2603901.9522 | 1202623.8346
116 | 2603999.3624 | 1202610.4665 | 2603996.3426 | 1202610.6329 | 2603988.5183 | 1202611.5882
117 | 2603961.3163 | 1202631.2142 | 2603961.5504 | 1202635.7348
118 | 2603895.7469 | 1202625.0121 | 2603901.9522 | 1202623.8346
119 | 2603886.915 | 1202475.5263 | 2603884.145 | 1202475.9767
120 | 2603943.8868 | 1202468.0318 | 2603950.0508 | 1202468.0167
121 | 2603950.0508 | 1202468.0167 | 2603956.0731 | 1202468.0019
122 | 2604009.9568 | 1202610.4215 | 2604005.5121 | 1202610.1276 | 2603999.3624 | 1202610.4665
123 | 2603962.3913 | 1202650.5326 | 2603961.7473 | 1202639.537 | 2603961.5504 | 1202635.7348
124 | 2603963.4267 | 1202668.211 | 2603962.3913 | 1202650.5326
125 | 2603964.6294 | 1202692.2777 | 2603964.4703 | 1202687.8872 | 2603963.6512 | 1202672.0447 | 2603963.4267 | 1202668.211
126 | 2603964.6294 | 1202692.2777 | 2603964.9561 | 1202701.2948 | 2603965.2361 | 1202703.7407 | 2603967.3756 | 1202715.1882
127 | 2604009.9568 | 1202610.4215 | 2604014.1711 | 1202610.7003 | 2604023.4003 | 1202612.0627 | 2604030.8104 | 1202613.9575 | 2604032.3258 | 1202614.4386
128 | 2604093.2139 | 1202575.0717 | 2604104.8337 | 1202579.6587
129 | 2604104.8337 | 1202579.6587 | 2604116.6027 | 1202584.3046
130 | 2604120.7634 | 1202585.9471 | 2604116.6027 | 1202584.3046
131 | 2604074.1158 | 1202571.6552 | 2604062.799 | 1202567.189
132 | 2604051.2776 | 1202562.642 | 2604062.799 | 1202567.189
133 | 2604135.925 | 1202580.2766 | 2604130.5923 | 1202578.0606 | 2604126.2254 | 1202588.1075 | 2604120.7634 | 1202585.9471
134 | 2604120.7634 | 1202585.9471 | 2604115.4851 | 1202598.3096
135 | 2604135.925 | 1202580.2766 | 2604137.7083 | 1202576.1978 | 2604140.1471 | 1202570.6187 | 2604141.7552 | 1202566.9511 | 2604145.7923 | 1202560.7616
136 | 2604135.925 | 1202580.2766 | 2604154.2024 | 1202588.211
137 | 2604111.3205 | 1202608.0638 | 2604115.4851 | 1202598.3096
138 | 2604165.4376 | 1202593.0883 | 2604176.8587 | 1202598.0463
139 | 2604165.4376 | 1202593.0883 | 2604154.2024 | 1202588.211
140 | 2604192.2142 | 1202597.6579 | 2604190.9189 | 1202600.2584 | 2604183.2483 | 1202600.8201 | 2604176.8587 | 1202598.0463
141 | 2604145.7923 | 1202560.7616 | 2604165.9693 | 1202568.775
142 | 2604165.9693 | 1202568.775 | 2604177.9162 | 1202573.5198
143 | 2604091.1755 | 1202600.7764 | 2604079.7973 | 1202596.153
144 | 2604111.3205 | 1202608.0638 | 2604108.9692 | 1202608.0066 | 2604091.1755 | 1202600.7764
145 | 2604059.77 | 1202588.0152 | 2604079.7973 | 1202596.153
146 | 2604111.3205 | 1202608.0638 | 2604128.4419 | 1202608.5228
147 | 2604048.7452 | 1202584.0263 | 2604055.8861 | 1202586.4371 | 2604059.77 | 1202588.0152
148 | 2604143.8058 | 1202606.1181 | 2604136.423 | 1202608.7367 | 2604128.4419 | 1202608.5228
149 | 2604048.7452 | 1202584.0263 | 2604037.2608 | 1202580.1491
150 | 2604023.782 | 1202575.5987 | 2604037.2608 | 1202580.1491
151 | 2604023.782 | 1202575.5987 | 2604025.9647 | 1202569.8445
152 | 2604023.782 | 1202575.5987 | 2604004.9577 | 1202575.3451
153 | 2604031.6867 | 1202554.7594 | 2604025.9647 | 1202569.8445
154 | 2603991.9593 | 1202575.1699 | 2604004.9577 | 1202575.3451
155 | 2603977.0442 | 1202736.6409 | 2603971.0861 | 1202729.1027 | 2603970.0905 | 1202727.4011 | 2603969.5056 | 1202725.7443 | 2603968.9516 | 1202723.6206 | 2603967.3756 | 1202715.1882
156 | 2603981.3751 | 1202750.0763 | 2603981.3247 | 1202745.7295 | 2603981.0293 | 1202743.6615 | 2603980.3686 | 1202741.7156 | 2603979.2972 | 1202739.4915 | 2603977.0442 | 1202736.6409
157 | 2604177.9162 | 1202573.5198 | 2604189.4412 | 1202578.097
158 | 2603981.3751 | 1202750.0763 | 2604006.5952 | 1202729.4829
159 | 2604006.5952 | 1202729.4829 | 2604007.9947 | 1202728.3402
160 | 2604012.9311 | 1202724.3094 | 2604007.9947 | 1202728.3402
161 | 2604012.9311 | 1202724.3094 | 2604013.544 | 1202723.8089
162 | 2603872.1096 | 1202515.8546 | 2603877.9545 | 1202514.6692
163 | 2603865.9557 | 1202517.1028 | 2603872.1096 | 1202515.8546
164 | 2603859.3125 | 1202518.4501 | 2603865.9557 | 1202517.1028

## bus_geodata
| x | y | coords
0 | 2603848.7833 | 1202557.563
1 | 2603864.6157 | 1202555.2623
2 | 2603865.3014 | 1202555.1526
3 | 2603872.048 | 1202554.073
4 | 2603872.4013 | 1202554.0165
5 | 2603987.5402 | 1202428.783
6 | 2604004.8848 | 1202426.9172
7 | 2603978.5784 | 1202431.1464
8 | 2604013.3349 | 1202427.6211
9 | 2603979.4273 | 1202468.2312
10 | 2603939.5732 | 1202405.8852
11 | 2603999.4714 | 1202469.7922
12 | 2603972.045 | 1202467.9628
13 | 2604021.7909 | 1202428.3255
14 | 2604013.2641 | 1202474.7484
15 | 2603926.5039 | 1202400.1141
16 | 2603931.4092 | 1202398.8625
17 | 2603913.6211 | 1202403.4012
18 | 2603937.4405 | 1202397.3236
19 | 2604120.257 | 1202681.9501
20 | 2604121.3026 | 1202683.7006
21 | 2604109.5248 | 1202664.1485
22 | 2604106.6925 | 1202644.0357
23 | 2604140.2949 | 1202644.0029
24 | 2604114.1034 | 1202645.069
25 | 2604157.993 | 1202641.5889
26 | 2604082.5577 | 1202635.9429
27 | 2604057.127 | 1202624.6624
28 | 2604041.8014 | 1202508.7749
29 | 2604049.5478 | 1202495.2703
30 | 2604036.8765 | 1202520.1552
31 | 2604058.9442 | 1202485.2844
32 | 2604051.3487 | 1202532.8606
33 | 2604069.5248 | 1202473.6015
34 | 2603992.3325 | 1202518.0135
35 | 2603998.3599 | 1202505.3773
36 | 2603979.124 | 1202536.288
37 | 2604072.8998 | 1202519.4344
38 | 2604044.8221 | 1202547.7226
39 | 2604075.1362 | 1202531.9093
40 | 2604086.2675 | 1202519.1675
41 | 2603991.6881 | 1202505.4627
42 | 2603972.5462 | 1202544.2592
43 | 2604079.9514 | 1202534.2027
44 | 2604040.1916 | 1202558.2669
45 | 2604095.8555 | 1202518.9761
46 | 2604124.5046 | 1202534.5051
47 | 2604120.6472 | 1202544.0466
48 | 2604147.379 | 1202555.0485
49 | 2604119.8625 | 1202545.9106
50 | 2604161.5878 | 1202545.9662
51 | 2604095.3602 | 1202548.4533
52 | 2604115.6318 | 1202556.461
53 | 2603816.2064 | 1202489.6704
54 | 2603842.6247 | 1202483.9901
55 | 2603856.823 | 1202480.9373
56 | 2603870.6685 | 1202478.1678
57 | 2603878.1209 | 1202476.9561
58 | 2603907.1788 | 1202405.045
59 | 2603910.1014 | 1202404.2993
60 | 2603905.2809 | 1202405.5293
61 | 2603894.19 | 1202407.8396
62 | 2603918.002 | 1202470.472
63 | 2603923.9269 | 1202469.5087
64 | 2603911.9046 | 1202471.4634
65 | 2603889.3419 | 1202408.6135
66 | 2603937.7494 | 1202468.0468
67 | 2603876.1595 | 1202410.7179
68 | 2603905.8243 | 1202472.4519
69 | 2603890.0781 | 1202475.012
70 | 2603945.8312 | 1202506.0497
71 | 2603951.9437 | 1202505.9715
72 | 2603939.6723 | 1202506.1285
73 | 2603969.4666 | 1202505.7472
74 | 2603933.5893 | 1202506.2064
75 | 2603977.3186 | 1202505.6467
76 | 2603914.9747 | 1202508.3135
77 | 2603983.8098 | 1202505.5636
78 | 2603908.5504 | 1202509.3708
79 | 2603913.505 | 1202547.5298
80 | 2603925.8927 | 1202545.6083
81 | 2603906.3773 | 1202548.6353
82 | 2603933.4209 | 1202544.6434
83 | 2603905.5894 | 1202548.7576
84 | 2603939.5618 | 1202544.044
85 | 2603899.9603 | 1202549.6307
86 | 2603954.6483 | 1202542.5717
87 | 2603898.1933 | 1202549.9048
88 | 2603902.4386 | 1202510.3767
89 | 2603891.5322 | 1202512.1716
90 | 2603878.2027 | 1202553.0882
91 | 2603878.5957 | 1202553.0253
92 | 2603884.2693 | 1202552.1174
93 | 2603996.0453 | 1202553.0854
94 | 2603969.9647 | 1202547.1591
95 | 2604009.357 | 1202552.8743
96 | 2603958.6376 | 1202542.1823
97 | 2604022.6389 | 1202552.6636
98 | 2603949.1962 | 1202574.5937
99 | 2603947.1582 | 1202578.4702
100 | 2603978.4583 | 1202574.988
101 | 2603936.7667 | 1202599.2483
102 | 2603934.3125 | 1202608.9004
103 | 2603945.6299 | 1202581.377
104 | 2603931.9633 | 1202618.1395
105 | 2603960.4773 | 1202615.0118
106 | 2603916.6524 | 1202621.045
107 | 2603988.5183 | 1202611.5882
108 | 2603961.3163 | 1202631.2142
109 | 2603901.9522 | 1202623.8346
110 | 2603884.145 | 1202475.9767
111 | 2603886.915 | 1202475.5263
112 | 2603871.2327 | 1202411.5044
113 | 2603943.8868 | 1202468.0318
114 | 2603950.0508 | 1202468.0167
115 | 2603956.0731 | 1202468.0019
116 | 2603895.7469 | 1202625.0121
117 | 2603999.3625 | 1202610.4665
118 | 2603961.5504 | 1202635.7348
119 | 2603962.3913 | 1202650.5326
120 | 2603963.4267 | 1202668.211
121 | 2603964.6294 | 1202692.2777
122 | 2604009.9568 | 1202610.4215
123 | 2604093.2139 | 1202575.0717
124 | 2604104.8337 | 1202579.6587
125 | 2604116.6027 | 1202584.3046
126 | 2604074.1158 | 1202571.6552
127 | 2604062.799 | 1202567.189
128 | 2604120.7634 | 1202585.9471
129 | 2604051.2776 | 1202562.642
130 | 2604135.925 | 1202580.2766
131 | 2604115.4851 | 1202598.3096
132 | 2604165.4376 | 1202593.0883
133 | 2604176.8587 | 1202598.0463
134 | 2604154.2024 | 1202588.211
135 | 2604192.2142 | 1202597.6579
136 | 2604145.7923 | 1202560.7616
137 | 2604165.9693 | 1202568.775
138 | 2604091.1755 | 1202600.7764
139 | 2604079.7973 | 1202596.153
140 | 2604111.3205 | 1202608.0638
141 | 2604059.77 | 1202588.0152
142 | 2604128.4419 | 1202608.5228
143 | 2604048.7452 | 1202584.0263
144 | 2604143.8058 | 1202606.1181
145 | 2604037.2608 | 1202580.1491
146 | 2604023.782 | 1202575.5987
147 | 2604025.9647 | 1202569.8445
148 | 2604004.9577 | 1202575.3451
149 | 2604031.6867 | 1202554.7594
150 | 2603991.9593 | 1202575.1699
151 | 2603967.3756 | 1202715.1882
152 | 2603977.0442 | 1202736.6409
153 | 2604032.3258 | 1202614.4386
154 | 2604177.9162 | 1202573.5198
155 | 2604189.4412 | 1202578.097
156 | 2603981.3751 | 1202750.0763
157 | 2604006.5952 | 1202729.4829
158 | 2604007.9947 | 1202728.3402
159 | 2604012.9311 | 1202724.3094
160 | 2603892.5312 | 1202550.7954
161 | 2603877.9545 | 1202514.6692
162 | 2603872.1096 | 1202515.8546
163 | 2603865.9557 | 1202517.1028
164 | 2603859.3125 | 1202518.4501
165 | 2604013.544 | 1202723.8089
166 | 2603972.5462 | 1202544.2592

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1