## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_355-38_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_355-38_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_355-38_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_355-38_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_355-38_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_355-38_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_355-38_0_4_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_355-38_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_355-38_0_4_node_92 | 0.4 | n |  | TRUE
9 | bus_LV_355-38_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_355-38_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_355-38_0_4_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_355-38_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_355-38_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_355-38_0_4_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_355-38_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_355-38_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_355-38_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_355-38_0_4_node_7 | 0.4 | n |  | TRUE
19 | bus_LV_355-38_0_4_node_87 | 0.4 | n |  | TRUE
20 | bus_LV_355-38_0_4_node_89 | 0.4 | n |  | TRUE
21 | bus_LV_355-38_0_4_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_355-38_0_4_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_355-38_0_4_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_355-38_0_4_node_91 | 0.4 | n |  | TRUE
25 | bus_LV_355-38_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_355-38_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_355-38_0_4_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_355-38_0_4_node_76 | 0.4 | n |  | TRUE
29 | bus_LV_355-38_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_355-38_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_355-38_0_4_node_90 | 0.4 | n |  | TRUE
32 | bus_LV_355-38_0_4_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_355-38_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_355-38_0_4_node_96 | 0.4 | n |  | TRUE
35 | bus_LV_355-38_0_4_node_75 | 0.4 | n |  | TRUE
36 | bus_LV_355-38_0_4_node_86 | 0.4 | n |  | TRUE
37 | bus_LV_355-38_0_4_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_355-38_0_4_node_85 | 0.4 | n |  | TRUE
39 | bus_LV_355-38_0_4_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_355-38_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_355-38_0_4_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_355-38_0_4_node_28 | 0.4 | n |  | TRUE
43 | bus_LV_355-38_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_355-38_0_4_node_40 | 0.4 | n |  | TRUE
45 | bus_LV_355-38_0_4_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_355-38_0_4_node_93 | 0.4 | n |  | TRUE
47 | bus_LV_355-38_0_4_node_94 | 0.4 | n |  | TRUE
48 | bus_LV_355-38_0_4_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_355-38_0_4_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_355-38_0_4_node_50 | 0.4 | n |  | TRUE
51 | bus_LV_355-38_0_4_node_100 | 0.4 | n |  | TRUE
52 | bus_LV_355-38_0_4_node_101 | 0.4 | n |  | TRUE
53 | bus_LV_355-38_0_4_node_97 | 0.4 | n |  | TRUE
54 | bus_LV_355-38_0_4_node_95 | 0.4 | n |  | TRUE
55 | bus_LV_355-38_0_4_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_355-38_0_4_node_47 | 0.4 | n |  | TRUE
57 | bus_LV_355-38_0_4_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_355-38_0_4_node_80 | 0.4 | n |  | TRUE
59 | bus_LV_355-38_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_355-38_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_355-38_0_4_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_355-38_0_4_node_36 | 0.4 | n |  | TRUE
63 | bus_LV_355-38_0_4_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_355-38_0_4_node_34 | 0.4 | n |  | TRUE
65 | bus_LV_355-38_0_4_node_102 | 0.4 | n |  | TRUE
66 | bus_LV_355-38_0_4_node_37 | 0.4 | n |  | TRUE
67 | bus_LV_355-38_0_4_node_84 | 0.4 | n |  | TRUE
68 | bus_LV_355-38_0_4_node_38 | 0.4 | n |  | TRUE
69 | bus_LV_355-38_0_4_node_41 | 0.4 | n |  | TRUE
70 | bus_LV_355-38_0_4_node_42 | 0.4 | n |  | TRUE
71 | bus_LV_355-38_0_4_node_44 | 0.4 | n |  | TRUE
72 | bus_LV_355-38_0_4_node_78 | 0.4 | n |  | TRUE
73 | bus_LV_355-38_0_4_node_99 | 0.4 | n |  | TRUE
74 | bus_LV_355-38_0_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_355-38_0_4_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_355-38_0_4_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_355-38_0_4_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_355-38_0_4_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_355-38_0_4_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_355-38_0_4_node_48 | 0.4 | n |  | TRUE
81 | bus_LV_355-38_0_4_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_355-38_0_4_node_51 | 0.4 | n |  | TRUE
83 | bus_LV_355-38_0_4_node_53 | 0.4 | n |  | TRUE
84 | bus_LV_355-38_0_4_node_56 | 0.4 | n |  | TRUE
85 | bus_LV_355-38_0_4_node_55 | 0.4 | n |  | TRUE
86 | bus_LV_355-38_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_355-38_0_4_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_355-38_0_4_node_69 | 0.4 | n |  | TRUE
89 | bus_LV_355-38_0_4_node_58 | 0.4 | n |  | TRUE
90 | bus_LV_355-38_0_4_node_60 | 0.4 | n |  | TRUE
91 | bus_LV_355-38_0_4_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_355-38_0_4_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_355-38_0_4_node_63 | 0.4 | n |  | TRUE
94 | bus_LV_355-38_0_4_node_64 | 0.4 | n |  | TRUE
95 | bus_LV_355-38_0_4_node_65 | 0.4 | n |  | TRUE
96 | bus_LV_355-38_0_4_node_70 | 0.4 | n |  | TRUE
97 | bus_LV_355-38_0_4_node_71 | 0.4 | n |  | TRUE
98 | bus_MV_608_0_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_355-38_0_4_load_0 | 0 | 0.0028314 | 0.0007096 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_355-38_0_4_load_4 | 4 | 0.0020877 | 0.00052323 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_355-38_0_4_load_16 | 6 | 0.0028337 | 0.00071019 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_355-38_0_4_load_92 | 8 | 0.00039416 | 9.8786e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_355-38_0_4_load_32 | 11 | 0.0083241 | 0.0020862 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_355-38_0_4_load_30 | 14 | 0.025491 | 0.0063887 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_355-38_0_4_load_18 | 17 | 0.0028352 | 0.00071057 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_355-38_0_4_load_89 | 20 | 0.0019097 | 0.00047862 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_355-38_0_4_load_29 | 21 | 0.0020941 | 0.00052484 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_355-38_0_4_load_91 | 24 | 0.00058641 | 0.00014697 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_355-38_0_4_load_19 | 26 | 0.0028434 | 0.00071263 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_355-38_0_4_load_76 | 28 | 0.060998 | 0.015287 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_355-38_0_4_load_90 | 31 | 0.076967 | 0.01929 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_355-38_0_4_load_98 | 32 | 0.0010546 | 0.00026432 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_355-38_0_4_load_96 | 34 | 0.0015306 | 0.0003836 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_355-38_0_4_load_75 | 35 | 0.0027309 | 0.00068443 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_355-38_0_4_load_74 | 37 | 0.0039304 | 0.00098506 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_355-38_0_4_load_85 | 38 | 0.0015528 | 0.00038918 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_355-38_0_4_load_22 | 41 | 0.0016882 | 0.00042311 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_355-38_0_4_load_40 | 44 | 0.0007797 | 0.00019541 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_355-38_0_4_load_35 | 45 | 0.00082094 | 0.00020575 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_355-38_0_4_load_93 | 46 | 0.0018781 | 0.0004707 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_355-38_0_4_load_79 | 49 | 0.011027 | 0.0027637 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_355-38_0_4_load_100 | 51 | 0.023826 | 0.0059712 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_355-38_0_4_load_101 | 52 | 0.011358 | 0.0028467 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_355-38_0_4_load_97 | 53 | 0.0019323 | 0.00048428 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_355-38_0_4_load_95 | 54 | 0.00054754 | 0.00013723 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_355-38_0_4_load_88 | 55 | 0.0024649 | 0.00061775 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_355-38_0_4_load_80 | 58 | 0.095351 | 0.023897 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_355-38_0_4_load_46 | 59 | 0.0019329 | 0.00048442 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_355-38_0_4_load_45 | 60 | 0.00076435 | 0.00019156 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_355-38_0_4_load_43 | 61 | 0.00076359 | 0.00019137 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_355-38_0_4_load_34 | 64 | 0.0073328 | 0.0018378 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_355-38_0_4_load_102 | 65 | 0.0069891 | 0.0017516 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_355-38_0_4_load_84 | 67 | 0.0015528 | 0.00038917 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_355-38_0_4_load_38 | 68 | 0.00077719 | 0.00019478 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_355-38_0_4_load_41 | 69 | 0.0026632 | 0.00066747 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_355-38_0_4_load_44 | 71 | 0.00055574 | 0.00013928 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_355-38_0_4_load_99 | 73 | 0.0027554 | 0.00069057 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_355-38_0_4_load_59 | 76 | 0.0094481 | 0.0023679 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_355-38_0_4_load_72 | 77 | 0.00099592 | 0.0002496 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_355-38_0_4_load_81 | 79 | 0.095615 | 0.023963 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_355-38_0_4_load_48 | 80 | 0.0014323 | 0.00035896 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_355-38_0_4_load_49 | 81 | 0.0058769 | 0.0014729 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_355-38_0_4_load_51 | 82 | 0.00247 | 0.00061904 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_355-38_0_4_load_53 | 83 | 0.0057145 | 0.0014322 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_355-38_0_4_load_55 | 85 | 0.0030939 | 0.00077539 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_355-38_0_4_load_73 | 86 | 0.0010513 | 0.00026349 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_355-38_0_4_load_57 | 87 | 0.0054985 | 0.001378 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_355-38_0_4_load_58 | 89 | 0.0054356 | 0.0013623 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_355-38_0_4_load_60 | 90 | 0.0095728 | 0.0023992 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_355-38_0_4_load_83 | 91 | 0.025261 | 0.0063309 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_355-38_0_4_load_82 | 92 | 0.00055661 | 0.0001395 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_355-38_0_4_load_63 | 93 | 0.00077456 | 0.00019412 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_355-38_0_4_load_64 | 94 | 0.0013326 | 0.00033398 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_355-38_0_4_load_70 | 96 | 0.00096113 | 0.00024088 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_355-38_0_4_load_71 | 97 | 0.001396 | 0.00034987 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 51 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_355-38_0_4_line_0 |  | 0 | 1 | 0.022319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_355-38_0_4_line_1 |  | 0 | 2 | 0.01545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_355-38_0_4_line_2 |  | 1 | 3 | 0.015252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_355-38_0_4_line_3 |  | 1 | 4 | 0.01302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_355-38_0_4_line_4 |  | 2 | 5 | 0.021923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_355-38_0_4_line_5 |  | 2 | 6 | 0.019876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_355-38_0_4_line_6 |  | 2 | 7 | 0.097529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_355-38_0_4_line_7 |  | 3 | 8 | 0.003911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_355-38_0_4_line_8 |  | 4 | 9 | 0.020946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_355-38_0_4_line_9 |  | 5 | 32 | 0.003505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_355-38_0_4_line_10 |  | 6 | 15 | 0.01575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_355-38_0_4_line_11 |  | 7 | 31 | 0.029741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_355-38_0_4_line_12 |  | 9 | 21 | 0.014357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_355-38_0_4_line_13 |  | 9 | 22 | 0.0409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_355-38_0_4_line_14 |  | 10 | 11 | 0.003863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_355-38_0_4_line_15 |  | 10 | 12 | 0.076279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_355-38_0_4_line_16 |  | 10 | 13 | 0.063276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_355-38_0_4_line_17 |  | 10 | 14 | 0.011001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_355-38_0_4_line_18 |  | 12 | 27 | 0.030105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_355-38_0_4_line_19 |  | 12 | 28 | 0.05539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_355-38_0_4_line_20 |  | 13 | 25 | 0.020735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_355-38_0_4_line_21 |  | 13 | 26 | 0.015594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_355-38_0_4_line_22 |  | 14 | 33 | 0.0075186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_355-38_0_4_line_23 |  | 15 | 16 | 0.021773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_355-38_0_4_line_24 |  | 15 | 17 | 0.019589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_355-38_0_4_line_25 |  | 16 | 34 | 0.00637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_355-38_0_4_line_26 |  | 17 | 29 | 0.013874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_355-38_0_4_line_27 |  | 18 | 19 | 0.054031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_355-38_0_4_line_28 |  | 18 | 20 | 0.012634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_355-38_0_4_line_29 |  | 19 | 35 | 0.043305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_355-38_0_4_line_30 |  | 20 | 22 | 0.0073109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_355-38_0_4_line_31 |  | 21 | 39 | 0.025455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_355-38_0_4_line_32 |  | 22 | 23 | 0.026693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_355-38_0_4_line_33 |  | 23 | 24 | 0.007902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_355-38_0_4_line_34 |  | 25 | 46 | 0.008736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_355-38_0_4_line_35 |  | 25 | 47 | 0.016805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_355-38_0_4_line_36 |  | 26 | 29 | 0.021446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_355-38_0_4_line_37 |  | 27 | 48 | 0.028374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_355-38_0_4_line_38 |  | 27 | 49 | 0.041116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_355-38_0_4_line_39 |  | 27 | 50 | 0.04948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_355-38_0_4_line_40 |  | 29 | 30 | 0.021189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_355-38_0_4_line_41 |  | 30 | 53 | 0.005986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_355-38_0_4_line_42 |  | 33 | 63 | 0.018506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_355-38_0_4_line_43 |  | 33 | 64 | 0.003693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_355-38_0_4_line_44 |  | 35 | 70 | 0.010719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_355-38_0_4_line_45 |  | 36 | 37 | 0.019765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_355-38_0_4_line_46 |  | 36 | 38 | 0.0024893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_355-38_0_4_line_47 |  | 37 | 70 | 0.023858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_355-38_0_4_line_48 |  | 38 | 67 | 0.017466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_355-38_0_4_line_49 |  | 39 | 40 | 0.077019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_355-38_0_4_line_50 |  | 40 | 41 | 0.016158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_355-38_0_4_line_51 |  | 42 | 43 | 0.019183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_355-38_0_4_line_52 |  | 42 | 44 | 0.03997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_355-38_0_4_line_53 |  | 42 | 45 | 0.017415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_355-38_0_4_line_54 |  | 43 | 55 | 0.0188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_355-38_0_4_line_55 |  | 44 | 61 | 0.0014055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_355-38_0_4_line_56 |  | 45 | 62 | 0.012345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_355-38_0_4_line_57 |  | 47 | 54 | 0.004622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_355-38_0_4_line_58 |  | 48 | 51 | 0.082225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_355-38_0_4_line_59 |  | 48 | 52 | 0.019598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_355-38_0_4_line_60 |  | 50 | 83 | 0.024151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_355-38_0_4_line_61 |  | 50 | 80 | 0.021648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_355-38_0_4_line_62 |  | 56 | 57 | 0.018051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_355-38_0_4_line_63 |  | 56 | 58 | 0.02227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_355-38_0_4_line_64 |  | 57 | 75 | 0.043124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_355-38_0_4_line_65 |  | 57 | 76 | 0.023911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_355-38_0_4_line_66 |  | 58 | 79 | 0.012596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_355-38_0_4_line_67 |  | 59 | 60 | 0.043607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_355-38_0_4_line_68 |  | 60 | 71 | 0.012837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_355-38_0_4_line_69 |  | 61 | 71 | 0.00015821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_355-38_0_4_line_70 |  | 62 | 66 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_355-38_0_4_line_71 |  | 63 | 65 | 0.003512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_355-38_0_4_line_72 |  | 66 | 67 | 0.0036755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_355-38_0_4_line_73 |  | 68 | 69 | 0.023201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_355-38_0_4_line_74 |  | 69 | 70 | 0.00078095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_355-38_0_4_line_75 |  | 72 | 73 | 0.039533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_355-38_0_4_line_76 |  | 72 | 74 | 0.068807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_355-38_0_4_line_77 |  | 74 | 77 | 0.024975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_355-38_0_4_line_78 |  | 74 | 78 | 0.027879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_355-38_0_4_line_79 |  | 75 | 91 | 0.022287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_355-38_0_4_line_80 |  | 75 | 92 | 0.02355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_355-38_0_4_line_81 |  | 76 | 90 | 0.036616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_355-38_0_4_line_82 |  | 77 | 96 | 0.011291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_355-38_0_4_line_83 |  | 78 | 88 | 0.013351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_355-38_0_4_line_84 |  | 78 | 92 | 0.055742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_355-38_0_4_line_85 |  | 80 | 81 | 0.02111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_355-38_0_4_line_86 |  | 81 | 82 | 0.031155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_355-38_0_4_line_87 |  | 82 | 84 | 0.014701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_355-38_0_4_line_88 |  | 82 | 85 | 0.029958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_355-38_0_4_line_89 |  | 83 | 86 | 0.025825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_355-38_0_4_line_90 |  | 84 | 87 | 0.02185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_355-38_0_4_line_91 |  | 86 | 88 | 0.0093945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_355-38_0_4_line_92 |  | 87 | 89 | 0.015895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_355-38_0_4_line_93 |  | 88 | 95 | 0.028579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_355-38_0_4_line_94 |  | 93 | 94 | 0.0081139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_355-38_0_4_line_95 |  | 93 | 95 | 0.01228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_355-38_0_4_line_96 |  | 96 | 97 | 0.0014249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_355-38_0_4_trafo_100 | 0.63 MVA 20/0.4 kV | 98 | 51 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2598513.8004 | 1198226.3469 | 2598503.4688 | 1198232.9643 | 2598495.8933 | 1198237.8244 | 2598495.0096 | 1198238.3896
1 | 2598481.9986 | 1198246.7218 | 2598492.8327 | 1198239.7819 | 2598495.0096 | 1198238.3896
2 | 2598513.8004 | 1198226.3469 | 2598520.6315 | 1198228.2128 | 2598526.4507 | 1198233.9922
3 | 2598513.8004 | 1198226.3469 | 2598522.5332 | 1198220.7639 | 2598524.768 | 1198219.3295
4 | 2598500.4143 | 1198258.1119 | 2598495.563 | 1198255.7341 | 2598488.8451 | 1198249.4659 | 2598481.9986 | 1198246.7218
5 | 2598481.9986 | 1198246.7218 | 2598473.7227 | 1198252.0157 | 2598466.368 | 1198256.7313 | 2598465.2588 | 1198257.4385
6 | 2598410.4964 | 1198250.6878 | 2598422.7474 | 1198245.9596 | 2598423.6077 | 1198245.6037 | 2598424.3995 | 1198245.1143 | 2598446.5766 | 1198227.0541 | 2598455.0402 | 1198239.6141 | 2598469.5439 | 1198230.3386 | 2598472.1877 | 1198235.5184 | 2598473.2619 | 1198237.6192 | 2598476.759 | 1198244.4775 | 2598481.9986 | 1198246.7218
7 | 2598526.4507 | 1198233.9922 | 2598530.0674 | 1198232.4793
8 | 2598542.4048 | 1198208.0298 | 2598533.2227 | 1198213.9131 | 2598525.5482 | 1198218.8288 | 2598524.768 | 1198219.3295
9 | 2598500.4143 | 1198258.1119 | 2598503.3226 | 1198256.1434
10 | 2598451.9937 | 1198265.929 | 2598463.0714 | 1198258.8333 | 2598465.2588 | 1198257.4385
11 | 2598386.7407 | 1198232.7071 | 2598410.4964 | 1198250.6878
12 | 2598542.4048 | 1198208.0298 | 2598552.3101 | 1198201.6905 | 2598554.4958 | 1198200.2875
13 | 2598511.5351 | 1198183.0689 | 2598519.5474 | 1198188.4474 | 2598531.6649 | 1198196.6598 | 2598532.9905 | 1198199.3164 | 2598536.0685 | 1198205.33 | 2598542.4048 | 1198208.0298
14 | 2598369.4026 | 1198316.1899 | 2598372.6307 | 1198314.0545
15 | 2598319.1454 | 1198290.5574 | 2598323.1738 | 1198291.2344 | 2598326.6848 | 1198293.101 | 2598329.2744 | 1198295.2125 | 2598331.0798 | 1198297.78 | 2598332.1314 | 1198300.1921 | 2598332.4591 | 1198301.0147 | 2598337.7323 | 1198314.0201 | 2598349.0457 | 1198306.8129 | 2598359.1106 | 1198300.4066 | 2598369.4026 | 1198316.1899
16 | 2598392.6242 | 1198303.9546 | 2598384.5967 | 1198298.7652 | 2598378.144 | 1198288.2836 | 2598359.1106 | 1198300.4066 | 2598369.4026 | 1198316.1899
17 | 2598369.4026 | 1198316.1899 | 2598375.4076 | 1198325.4069
18 | 2598290.0662 | 1198296.0467 | 2598293.477 | 1198294.1892 | 2598294.482 | 1198293.633 | 2598297.916 | 1198292.4869 | 2598301.9972 | 1198291.4296 | 2598305.7739 | 1198290.7948 | 2598309.307 | 1198290.3602 | 2598312.5357 | 1198290.3148 | 2598314.5917 | 1198290.2808 | 2598319.1454 | 1198290.5574
19 | 2598319.1454 | 1198290.5574 | 2598305.2683 | 1198344.1809
20 | 2598406.8983 | 1198318.4138 | 2598401.6356 | 1198315.4026 | 2598394.8786 | 1198305.5881 | 2598392.6242 | 1198303.9546
21 | 2598392.6242 | 1198303.9546 | 2598403.5342 | 1198296.9589 | 2598405.7529 | 1198295.5405
22 | 2598379.5118 | 1198331.7064 | 2598375.4076 | 1198325.4069
23 | 2598468.2853 | 1198278.7536 | 2598464.1646 | 1198274.9416 | 2598454.8737 | 1198271.5312 | 2598451.9937 | 1198265.929
24 | 2598451.9937 | 1198265.929 | 2598443.9615 | 1198271.0783 | 2598436.7059 | 1198275.7273 | 2598435.5 | 1198276.4975
25 | 2598468.2853 | 1198278.7536 | 2598473.7137 | 1198275.3948
26 | 2598423.8163 | 1198283.9796 | 2598433.3103 | 1198277.896 | 2598435.5 | 1198276.4975
27 | 2598452.1789 | 1198162.5404 | 2598460.8312 | 1198168.9971 | 2598473.7563 | 1198178.6321 | 2598495.4632 | 1198194.8794
28 | 2598495.4632 | 1198194.8794 | 2598501.158 | 1198190.6979 | 2598505.6447 | 1198187.3994
29 | 2598452.1789 | 1198162.5404 | 2598450.9838 | 1198164.1416 | 2598442.8951 | 1198158.1072 | 2598440.0465 | 1198155.9846 | 2598437.5864 | 1198154.151 | 2598452.3514 | 1198134.4808
30 | 2598511.5351 | 1198183.0689 | 2598505.6447 | 1198187.3994
31 | 2598575.9353 | 1198186.5654 | 2598562.954 | 1198194.8731 | 2598555.7058 | 1198199.5107 | 2598554.4958 | 1198200.2875
32 | 2598511.5351 | 1198183.0689 | 2598519.5474 | 1198188.4474 | 2598529.6565 | 1198174.7264
33 | 2598529.6565 | 1198174.7264 | 2598532.3312 | 1198182.163
34 | 2598406.8983 | 1198318.4138 | 2598414.2147 | 1198313.6092
35 | 2598406.8983 | 1198318.4138 | 2598413.4861 | 1198322.1918 | 2598418.9783 | 1198329.6165
36 | 2598423.8163 | 1198283.9796 | 2598414.231 | 1198290.1189 | 2598407.5007 | 1198294.4231 | 2598405.7529 | 1198295.5405
37 | 2598299.5466 | 1198270.4636 | 2598293.477 | 1198294.1892 | 2598290.0662 | 1198296.0467
38 | 2598290.0662 | 1198296.0467 | 2598281.2897 | 1198336.2152
39 | 2598246.9512 | 1198320.5395 | 2598290.0662 | 1198296.0467
40 | 2598438.9354 | 1198297.7829 | 2598433.9392 | 1198294.1378 | 2598428.3932 | 1198285.6015 | 2598423.8163 | 1198283.9796
41 | 2598438.9354 | 1198297.7829 | 2598444.0822 | 1198294.702
42 | 2598379.5118 | 1198331.7064 | 2598389.6209 | 1198347.223
43 | 2598379.5118 | 1198331.7064 | 2598382.6866 | 1198329.8045
44 | 2598458.7864 | 1198125.908 | 2598452.3514 | 1198134.4808
45 | 2598493.7537 | 1198151.9903 | 2598477.9103 | 1198140.1726
46 | 2598493.7537 | 1198151.9903 | 2598495.2476 | 1198149.9991
47 | 2598458.7864 | 1198125.908 | 2598477.9103 | 1198140.1726
48 | 2598505.7296 | 1198136.0276 | 2598495.2476 | 1198149.9991
49 | 2598575.9353 | 1198186.5654 | 2598566.436 | 1198172.4047 | 2598556.8528 | 1198158.1328 | 2598562.2432 | 1198154.1738 | 2598567.4527 | 1198157.7077 | 2598576.0743 | 1198163.5531 | 2598592.3753 | 1198153.0767
50 | 2598592.3753 | 1198153.0767 | 2598602.4662 | 1198165.6958
51 | 2598510.3934 | 1198097.8015 | 2598525.558 | 1198109.6038
52 | 2598510.3934 | 1198097.8015 | 2598476.5428 | 1198076.5467
53 | 2598510.3934 | 1198097.8015 | 2598499.9431 | 1198111.7322
54 | 2598525.558 | 1198109.6038 | 2598539.001 | 1198119.4278 | 2598540.7163 | 1198120.7244
55 | 2598475.3524 | 1198075.7992 | 2598476.5428 | 1198076.5467
56 | 2598492.5349 | 1198121.6077 | 2598499.9431 | 1198111.7322
57 | 2598418.9783 | 1198329.6165 | 2598422.8611 | 1198327.0918
58 | 2598299.5466 | 1198270.4636 | 2598304.3992 | 1198251.5187 | 2598307.0558 | 1198248.0605 | 2598308.4781 | 1198242.5571 | 2598307.2512 | 1198239.4003 | 2598310.9268 | 1198231.2615 | 2598331.9566 | 1198196.837
59 | 2598299.5466 | 1198270.4636 | 2598284.6863 | 1198257.6389
60 | 2598246.9512 | 1198320.5395 | 2598238.5534 | 1198299.6865 | 2598237.8681 | 1198298.1627
61 | 2598246.9512 | 1198320.5395 | 2598228.9665 | 1198324.6027 | 2598228.4163 | 1198327.7651
62 | 2598301.8914 | 1198165.996 | 2598306.7927 | 1198156.534 | 2598310.2022 | 1198149.9628
63 | 2598310.2022 | 1198149.9628 | 2598332.1108 | 1198153.9613
64 | 2598301.8914 | 1198165.996 | 2598299.0603 | 1198171.4553 | 2598282.2336 | 1198204.4001
65 | 2598301.8914 | 1198165.996 | 2598278.3451 | 1198161.8364
66 | 2598344.5018 | 1198156.2228 | 2598332.1108 | 1198153.9613
67 | 2598475.5264 | 1198034.1052 | 2598457.4067 | 1198064.5311 | 2598464.3465 | 1198068.8886
68 | 2598475.2184 | 1198075.7151 | 2598464.3465 | 1198068.8886
69 | 2598475.2184 | 1198075.7151 | 2598475.3524 | 1198075.7992
70 | 2598492.5349 | 1198121.6077 | 2598507.9354 | 1198133.0876
71 | 2598389.6209 | 1198347.223 | 2598392.6511 | 1198345.4323
72 | 2598507.9354 | 1198133.0876 | 2598505.7296 | 1198136.0276
73 | 2598459.2552 | 1198125.2834 | 2598472.968 | 1198107.0163 | 2598473.2561 | 1198107.2311
74 | 2598458.7864 | 1198125.908 | 2598459.2552 | 1198125.2834
75 | 2598223.561 | 1198180.2162 | 2598229.6149 | 1198180.3589 | 2598235.1455 | 1198187.3831 | 2598236.973 | 1198211.8734
76 | 2598211.5309 | 1198233.8597 | 2598209.1105 | 1198213.0938 | 2598208.2004 | 1198200.4207 | 2598208.2749 | 1198195.1845 | 2598208.409 | 1198185.6016 | 2598209.0544 | 1198179.776 | 2598223.561 | 1198180.2162
77 | 2598211.5309 | 1198233.8597 | 2598186.8009 | 1198237.3509
78 | 2598211.5309 | 1198233.8597 | 2598212.0736 | 1198240.5298 | 2598213.0818 | 1198250.1012 | 2598215.9754 | 1198250.0225 | 2598218.7626 | 1198250.7776 | 2598221.2227 | 1198252.2999 | 2598223.1423 | 1198254.456
79 | 2598260.773 | 1198198.6035 | 2598276.7044 | 1198201.856 | 2598282.2336 | 1198204.4001
80 | 2598282.2336 | 1198204.4001 | 2598275.5364 | 1198217.5092 | 2598269.5862 | 1198224.0318
81 | 2598278.3451 | 1198161.8364 | 2598266.3963 | 1198159.7255 | 2598261.6612 | 1198183.7455
82 | 2598175.6209 | 1198238.9293 | 2598175.6209 | 1198238.9293 | 2598186.8009 | 1198237.3509
83 | 2598223.1423 | 1198254.456 | 2598224.2929 | 1198256.868 | 2598224.7506 | 1198259.4915 | 2598224.5001 | 1198262.1486 | 2598223.5414 | 1198264.6502 | 2598221.9506 | 1198266.7963
84 | 2598223.1423 | 1198254.456 | 2598230.3446 | 1198250.207 | 2598246.5691 | 1198241.2639 | 2598266.3864 | 1198227.5395 | 2598269.5862 | 1198224.0318
85 | 2598228.4163 | 1198327.7651 | 2598224.7978 | 1198348.5628
86 | 2598219.4574 | 1198379.2571 | 2598224.7978 | 1198348.5628
87 | 2598217.1013 | 1198393.7656 | 2598219.4574 | 1198379.2571
88 | 2598219.4574 | 1198379.2571 | 2598247.3711 | 1198368.3791
89 | 2598237.8681 | 1198298.1627 | 2598234.0195 | 1198289.6047 | 2598227.276 | 1198275.5326 | 2598226.8404 | 1198274.8179
90 | 2598217.1013 | 1198393.7656 | 2598231.5468 | 1198395.3286 | 2598238.3646 | 1198392.6627
91 | 2598221.9506 | 1198266.7963 | 2598226.8404 | 1198274.8179
92 | 2598238.3646 | 1198392.6627 | 2598253.1686 | 1198386.874
93 | 2598201.4114 | 1198284.6233 | 2598207.3262 | 1198278.4737 | 2598211.1165 | 1198272.5138 | 2598213.3392 | 1198269.7005 | 2598216.4688 | 1198269.6773 | 2598219.4383 | 1198268.6647 | 2598221.9506 | 1198266.7963
94 | 2598189.1785 | 1198285.328 | 2598187.1798 | 1198286.0396 | 2598185.6343 | 1198286.7961 | 2598184.0889 | 1198287.9861 | 2598182.7263 | 1198289.4317 | 2598182.5373 | 1198289.7077
95 | 2598201.4114 | 1198284.6233 | 2598191.5884 | 1198284.871 | 2598189.2737 | 1198285.2941 | 2598189.1785 | 1198285.328
96 | 2598175.6209 | 1198238.9293 | 2598175.32 | 1198237.5365

## bus_geodata
| x | y | coords
0 | 2598495.0096 | 1198238.3896
1 | 2598513.8004 | 1198226.3469
2 | 2598481.9986 | 1198246.7218
3 | 2598526.4507 | 1198233.9922
4 | 2598524.768 | 1198219.3295
5 | 2598500.4143 | 1198258.1119
6 | 2598465.2588 | 1198257.4385
7 | 2598410.4964 | 1198250.6878
8 | 2598530.0674 | 1198232.4793
9 | 2598542.4048 | 1198208.0298
10 | 2598369.4026 | 1198316.1899
11 | 2598372.6307 | 1198314.0545
12 | 2598319.1454 | 1198290.5574
13 | 2598392.6242 | 1198303.9546
14 | 2598375.4076 | 1198325.4069
15 | 2598451.9937 | 1198265.929
16 | 2598468.2853 | 1198278.7536
17 | 2598435.5 | 1198276.4975
18 | 2598495.4632 | 1198194.8794
19 | 2598452.1789 | 1198162.5404
20 | 2598505.6447 | 1198187.3994
21 | 2598554.4958 | 1198200.2875
22 | 2598511.5351 | 1198183.0689
23 | 2598529.6565 | 1198174.7264
24 | 2598532.3312 | 1198182.163
25 | 2598406.8982 | 1198318.4138
26 | 2598405.7529 | 1198295.5405
27 | 2598290.0662 | 1198296.0467
28 | 2598305.2683 | 1198344.1809
29 | 2598423.8163 | 1198283.9796
30 | 2598438.9354 | 1198297.7829
31 | 2598386.7407 | 1198232.7071
32 | 2598503.3226 | 1198256.1434
33 | 2598379.5118 | 1198331.7064
34 | 2598473.7137 | 1198275.3948
35 | 2598452.3514 | 1198134.4808
36 | 2598493.7537 | 1198151.9903
37 | 2598477.9103 | 1198140.1726
38 | 2598495.2476 | 1198149.9991
39 | 2598575.9353 | 1198186.5654
40 | 2598592.3752 | 1198153.0767
41 | 2598602.4662 | 1198165.6958
42 | 2598510.3934 | 1198097.8015
43 | 2598525.558 | 1198109.6038
44 | 2598476.5428 | 1198076.5467
45 | 2598499.9431 | 1198111.7322
46 | 2598414.2147 | 1198313.6092
47 | 2598418.9783 | 1198329.6165
48 | 2598299.5466 | 1198270.4636
49 | 2598281.2897 | 1198336.2152
50 | 2598246.9512 | 1198320.5395
51 | 2598331.9566 | 1198196.837
52 | 2598284.6863 | 1198257.6389
53 | 2598444.0822 | 1198294.702
54 | 2598422.8611 | 1198327.0918
55 | 2598540.7163 | 1198120.7244
56 | 2598310.2022 | 1198149.9628
57 | 2598301.8914 | 1198165.996
58 | 2598332.1108 | 1198153.9613
59 | 2598475.5264 | 1198034.1052
60 | 2598464.3465 | 1198068.8886
61 | 2598475.3524 | 1198075.7992
62 | 2598492.5349 | 1198121.6077
63 | 2598389.6209 | 1198347.223
64 | 2598382.6866 | 1198329.8045
65 | 2598392.6511 | 1198345.4323
66 | 2598507.9354 | 1198133.0876
67 | 2598505.7296 | 1198136.0276
68 | 2598473.2561 | 1198107.2311
69 | 2598459.2552 | 1198125.2834
70 | 2598458.7864 | 1198125.908
71 | 2598475.2184 | 1198075.7151
72 | 2598223.561 | 1198180.2162
73 | 2598236.973 | 1198211.8734
74 | 2598211.5309 | 1198233.8597
75 | 2598282.2336 | 1198204.4001
76 | 2598278.3451 | 1198161.8364
77 | 2598186.8009 | 1198237.3509
78 | 2598223.1423 | 1198254.456
79 | 2598344.5018 | 1198156.2228
80 | 2598228.4163 | 1198327.7651
81 | 2598224.7978 | 1198348.5628
82 | 2598219.4574 | 1198379.2571
83 | 2598237.8681 | 1198298.1627
84 | 2598217.1013 | 1198393.7656
85 | 2598247.3711 | 1198368.3791
86 | 2598226.8404 | 1198274.8179
87 | 2598238.3646 | 1198392.6627
88 | 2598221.9506 | 1198266.7963
89 | 2598253.1686 | 1198386.874
90 | 2598261.6612 | 1198183.7455
91 | 2598260.773 | 1198198.6035
92 | 2598269.5862 | 1198224.0318
93 | 2598189.1785 | 1198285.328
94 | 2598182.5373 | 1198289.7077
95 | 2598201.4114 | 1198284.6233
96 | 2598175.6209 | 1198238.9293
97 | 2598175.32 | 1198237.5365
98 | 2598331.9566 | 1198196.837

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1