## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_356-29_1_3_node_17 | 0.4 | n |  | TRUE
1 | bus_LV_356-29_1_3_node_18 | 0.4 | n |  | TRUE
2 | bus_LV_356-29_1_3_node_19 | 0.4 | n |  | TRUE
3 | bus_LV_356-29_1_3_node_20 | 0.4 | n |  | TRUE
4 | bus_LV_356-29_1_3_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_356-29_1_3_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_356-29_1_3_node_23 | 0.4 | n |  | TRUE
7 | bus_LV_356-29_1_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_356-29_1_3_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_356-29_1_3_node_58 | 0.4 | n |  | TRUE
10 | bus_LV_356-29_1_3_node_57 | 0.4 | n |  | TRUE
11 | bus_LV_356-29_1_3_node_55 | 0.4 | n |  | TRUE
12 | bus_LV_356-29_1_3_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_356-29_1_3_node_26 | 0.4 | n |  | TRUE
14 | bus_LV_356-29_1_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_356-29_1_3_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_356-29_1_3_node_62 | 0.4 | n |  | TRUE
17 | bus_LV_356-29_1_3_node_56 | 0.4 | n |  | TRUE
18 | bus_LV_356-29_1_3_node_63 | 0.4 | n |  | TRUE
19 | bus_LV_356-29_1_3_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_356-29_1_3_node_61 | 0.4 | n |  | TRUE
21 | bus_LV_356-29_1_3_node_115 | 0.4 | n |  | TRUE
22 | bus_LV_356-29_1_3_node_97 | 0.4 | n |  | TRUE
23 | bus_LV_356-29_1_3_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_356-29_1_3_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_356-29_1_3_node_89 | 0.4 | n |  | TRUE
26 | bus_LV_356-29_1_3_node_94 | 0.4 | n |  | TRUE
27 | bus_LV_356-29_1_3_node_60 | 0.4 | n |  | TRUE
28 | bus_LV_356-29_1_3_node_130 | 0.4 | n |  | TRUE
29 | bus_LV_356-29_1_3_node_131 | 0.4 | n |  | TRUE
30 | bus_LV_356-29_1_3_node_128 | 0.4 | n |  | TRUE
31 | bus_LV_356-29_1_3_node_116 | 0.4 | n |  | TRUE
32 | bus_LV_356-29_1_3_node_117 | 0.4 | n |  | TRUE
33 | bus_LV_356-29_1_3_node_92 | 0.4 | n |  | TRUE
34 | bus_LV_356-29_1_3_node_87 | 0.4 | n |  | TRUE
35 | bus_LV_356-29_1_3_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_356-29_1_3_node_65 | 0.4 | n |  | TRUE
37 | bus_LV_356-29_1_3_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_356-29_1_3_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_356-29_1_3_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_356-29_1_3_node_71 | 0.4 | n |  | TRUE
41 | bus_LV_356-29_1_3_node_69 | 0.4 | n |  | TRUE
42 | bus_LV_356-29_1_3_node_81 | 0.4 | n |  | TRUE
43 | bus_LV_356-29_1_3_node_91 | 0.4 | n |  | TRUE
44 | bus_LV_356-29_1_3_node_82 | 0.4 | n |  | TRUE
45 | bus_LV_356-29_1_3_node_86 | 0.4 | n |  | TRUE
46 | bus_LV_356-29_1_3_node_80 | 0.4 | n |  | TRUE
47 | bus_LV_356-29_1_3_node_90 | 0.4 | n |  | TRUE
48 | bus_LV_356-29_1_3_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_356-29_1_3_node_84 | 0.4 | n |  | TRUE
50 | bus_LV_356-29_1_3_node_72 | 0.4 | n |  | TRUE
51 | bus_LV_356-29_1_3_node_73 | 0.4 | n |  | TRUE
52 | bus_LV_356-29_1_3_node_74 | 0.4 | n |  | TRUE
53 | bus_LV_356-29_1_3_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_356-29_1_3_node_76 | 0.4 | n |  | TRUE
55 | bus_LV_356-29_1_3_node_78 | 0.4 | n |  | TRUE
56 | bus_LV_356-29_1_3_node_79 | 0.4 | n |  | TRUE
57 | bus_LV_356-29_1_3_node_111 | 0.4 | n |  | TRUE
58 | bus_LV_356-29_1_3_node_112 | 0.4 | n |  | TRUE
59 | bus_LV_356-29_1_3_node_83 | 0.4 | n |  | TRUE
60 | bus_LV_356-29_1_3_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_356-29_1_3_node_88 | 0.4 | n |  | TRUE
62 | bus_LV_356-29_1_3_node_93 | 0.4 | n |  | TRUE
63 | bus_LV_356-29_1_3_node_95 | 0.4 | n |  | TRUE
64 | bus_LV_356-29_1_3_node_96 | 0.4 | n |  | TRUE
65 | bus_LV_356-29_1_3_node_109 | 0.4 | n |  | TRUE
66 | bus_LV_356-29_1_3_node_107 | 0.4 | n |  | TRUE
67 | bus_LV_356-29_1_3_node_98 | 0.4 | n |  | TRUE
68 | bus_LV_356-29_1_3_node_99 | 0.4 | n |  | TRUE
69 | bus_LV_356-29_1_3_node_101 | 0.4 | n |  | TRUE
70 | bus_LV_356-29_1_3_node_102 | 0.4 | n |  | TRUE
71 | bus_LV_356-29_1_3_node_103 | 0.4 | n |  | TRUE
72 | bus_LV_356-29_1_3_node_118 | 0.4 | n |  | TRUE
73 | bus_LV_356-29_1_3_node_119 | 0.4 | n |  | TRUE
74 | bus_LV_356-29_1_3_node_104 | 0.4 | n |  | TRUE
75 | bus_LV_356-29_1_3_node_105 | 0.4 | n |  | TRUE
76 | bus_LV_356-29_1_3_node_106 | 0.4 | n |  | TRUE
77 | bus_LV_356-29_1_3_node_108 | 0.4 | n |  | TRUE
78 | bus_LV_356-29_1_3_node_110 | 0.4 | n |  | TRUE
79 | bus_LV_356-29_1_3_node_132 | 0.4 | n |  | TRUE
80 | bus_LV_356-29_1_3_node_133 | 0.4 | n |  | TRUE
81 | bus_LV_356-29_1_3_node_113 | 0.4 | n |  | TRUE
82 | bus_LV_356-29_1_3_node_114 | 0.4 | n |  | TRUE
83 | bus_LV_356-29_1_3_node_126 | 0.4 | n |  | TRUE
84 | bus_LV_356-29_1_3_node_134 | 0.4 | n |  | TRUE
85 | bus_LV_356-29_1_3_node_124 | 0.4 | n |  | TRUE
86 | bus_LV_356-29_1_3_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_356-29_1_3_node_121 | 0.4 | n |  | TRUE
88 | bus_LV_356-29_1_3_node_122 | 0.4 | n |  | TRUE
89 | bus_LV_356-29_1_3_node_123 | 0.4 | n |  | TRUE
90 | bus_LV_356-29_1_3_node_125 | 0.4 | n |  | TRUE
91 | bus_LV_356-29_1_3_node_127 | 0.4 | n |  | TRUE
92 | bus_LV_356-29_1_3_node_129 | 0.4 | n |  | TRUE
93 | bus_MV_456_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_356-29_1_3_load_17 | 0 | 0.0017804 | 0.00044622 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_356-29_1_3_load_18 | 1 | 0.001819 | 0.00045589 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_356-29_1_3_load_20 | 3 | 0.0048919 | 0.001226 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_356-29_1_3_load_21 | 4 | 0.0054011 | 0.0013536 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_356-29_1_3_load_22 | 5 | 0.0019035 | 0.00047707 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_356-29_1_3_load_23 | 6 | 0.0037162 | 0.00093136 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_356-29_1_3_load_58 | 9 | 0.0045577 | 0.0011423 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_356-29_1_3_load_57 | 10 | 0.0026285 | 0.00065875 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_356-29_1_3_load_55 | 11 | 0.0017545 | 0.00043972 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_356-29_1_3_load_27 | 14 | 0.0048888 | 0.0012252 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_356-29_1_3_load_28 | 15 | 0.0077119 | 0.0019328 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_356-29_1_3_load_56 | 17 | 0.0044811 | 0.0011231 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_356-29_1_3_load_63 | 18 | 0.0026641 | 0.00066768 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_356-29_1_3_load_32 | 19 | 0.0039055 | 0.0009788 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_356-29_1_3_load_97 | 22 | 0.0054927 | 0.0013766 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_356-29_1_3_load_33 | 24 | 0.0037737 | 0.00094579 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_356-29_1_3_load_89 | 25 | 0.0024051 | 0.00060278 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_356-29_1_3_load_94 | 26 | 0.0052276 | 0.0013101 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_356-29_1_3_load_60 | 27 | 0.0042844 | 0.0010738 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_356-29_1_3_load_131 | 29 | 0.002409 | 0.00060375 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_356-29_1_3_load_128 | 30 | 0.0039132 | 0.00098074 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_356-29_1_3_load_116 | 31 | 0.0034094 | 0.00085447 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_356-29_1_3_load_117 | 32 | 0.0027704 | 0.00069433 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_356-29_1_3_load_92 | 33 | 0.0025461 | 0.00063812 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_356-29_1_3_load_64 | 35 | 0.0040811 | 0.0010228 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_356-29_1_3_load_65 | 36 | 0.0048808 | 0.0012233 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_356-29_1_3_load_67 | 37 | 0.0019618 | 0.00049167 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_356-29_1_3_load_70 | 38 | 0.0066113 | 0.001657 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_356-29_1_3_load_68 | 39 | 0.0018563 | 0.00046523 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_356-29_1_3_load_91 | 43 | 0.0040042 | 0.0010035 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_356-29_1_3_load_86 | 45 | 0.0033667 | 0.00084378 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_356-29_1_3_load_80 | 46 | 0.004184 | 0.0010486 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_356-29_1_3_load_90 | 47 | 0.0065228 | 0.0016348 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_356-29_1_3_load_77 | 48 | 0.0039325 | 0.00098558 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_356-29_1_3_load_84 | 49 | 0.0055358 | 0.0013874 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_356-29_1_3_load_72 | 50 | 0.0065001 | 0.0016291 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_356-29_1_3_load_73 | 51 | 0.0045838 | 0.0011488 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_356-29_1_3_load_74 | 52 | 0.0048414 | 0.0012134 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_356-29_1_3_load_78 | 55 | 0.0047054 | 0.0011793 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_356-29_1_3_load_79 | 56 | 0.0068312 | 0.0017121 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_356-29_1_3_load_111 | 57 | 0.0022307 | 0.00055907 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_356-29_1_3_load_112 | 58 | 0.0046971 | 0.0011772 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_356-29_1_3_load_83 | 59 | 0.001593 | 0.00039925 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_356-29_1_3_load_85 | 60 | 0.0007378 | 0.00018491 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_356-29_1_3_load_88 | 61 | 0.0058609 | 0.0014689 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_356-29_1_3_load_93 | 62 | 0.011407 | 0.0028588 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_356-29_1_3_load_95 | 63 | 0.0030826 | 0.00077258 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_356-29_1_3_load_96 | 64 | 0.0022931 | 0.0005747 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_356-29_1_3_load_109 | 65 | 0.0031241 | 0.00078298 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_356-29_1_3_load_107 | 66 | 0.013988 | 0.0035058 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_356-29_1_3_load_98 | 67 | 0.008407 | 0.002107 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_356-29_1_3_load_99 | 68 | 0.0041462 | 0.0010391 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_356-29_1_3_load_102 | 70 | 0.0078132 | 0.0019582 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_356-29_1_3_load_103 | 71 | 0.0033572 | 0.00084139 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_356-29_1_3_load_118 | 72 | 0.002763 | 0.00069248 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_356-29_1_3_load_119 | 73 | 0.0018344 | 0.00045974 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_356-29_1_3_load_104 | 74 | 0.0086972 | 0.0021797 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_356-29_1_3_load_105 | 75 | 0.0038871 | 0.0009742 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_356-29_1_3_load_106 | 76 | 0.0050128 | 0.0012563 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_356-29_1_3_load_108 | 77 | 0.0063576 | 0.0015934 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_356-29_1_3_load_110 | 78 | 0.0063536 | 0.0015924 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_356-29_1_3_load_132 | 79 | 0.0022627 | 0.00056708 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_356-29_1_3_load_133 | 80 | 0.0063593 | 0.0015938 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_356-29_1_3_load_113 | 81 | 0.0035454 | 0.00088855 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_356-29_1_3_load_114 | 82 | 0.0063655 | 0.0015953 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_356-29_1_3_load_126 | 83 | 0.0022584 | 0.00056601 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_356-29_1_3_load_134 | 84 | 0.013033 | 0.0032663 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_356-29_1_3_load_124 | 85 | 0.0024012 | 0.00060181 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_356-29_1_3_load_120 | 86 | 0.0024057 | 0.00060293 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_356-29_1_3_load_121 | 87 | 0.0023997 | 0.00060142 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_356-29_1_3_load_122 | 88 | 0.002407 | 0.00060325 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_356-29_1_3_load_123 | 89 | 0.0015569 | 0.00039019 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_356-29_1_3_load_125 | 90 | 0.0022993 | 0.00057626 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_356-29_1_3_load_127 | 91 | 0.0022979 | 0.0005759 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_356-29_1_3_load_129 | 92 | 0.0024045 | 0.00060264 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 66 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_356-29_1_3_line_0 |  | 0 | 1 | 0.008078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_356-29_1_3_line_1 |  | 0 | 2 | 0.021661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_356-29_1_3_line_2 |  | 1 | 3 | 0.020166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_356-29_1_3_line_3 |  | 2 | 4 | 0.022754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_356-29_1_3_line_4 |  | 2 | 5 | 0.0027279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_356-29_1_3_line_5 |  | 3 | 6 | 0.022087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_356-29_1_3_line_6 |  | 4 | 7 | 0.0087445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_356-29_1_3_line_7 |  | 5 | 8 | 0.026139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_356-29_1_3_line_8 |  | 7 | 9 | 0.030773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_356-29_1_3_line_9 |  | 7 | 10 | 0.0091877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_356-29_1_3_line_10 |  | 8 | 11 | 0.039584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_356-29_1_3_line_11 |  | 8 | 12 | 0.004473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_356-29_1_3_line_12 |  | 9 | 16 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_356-29_1_3_line_13 |  | 10 | 17 | 0.028704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_356-29_1_3_line_14 |  | 11 | 18 | 0.0021285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_356-29_1_3_line_15 |  | 12 | 19 | 0.041371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_356-29_1_3_line_16 |  | 13 | 14 | 0.045974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_356-29_1_3_line_17 |  | 13 | 15 | 0.019904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_356-29_1_3_line_18 |  | 14 | 20 | 0.023088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_356-29_1_3_line_19 |  | 16 | 22 | 0.051638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_356-29_1_3_line_20 |  | 16 | 26 | 0.014002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
21 | LV_356-29_1_3_line_21 |  | 18 | 25 | 0.0061036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_356-29_1_3_line_22 |  | 19 | 23 | 0.015928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_356-29_1_3_line_23 |  | 20 | 21 | 0.00985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_356-29_1_3_line_24 |  | 20 | 22 | 0.0038925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_356-29_1_3_line_25 |  | 21 | 31 | 0.020436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_356-29_1_3_line_26 |  | 21 | 32 | 0.027513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_356-29_1_3_line_27 |  | 23 | 24 | 0.017322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_356-29_1_3_line_28 |  | 25 | 34 | 0.017107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_356-29_1_3_line_29 |  | 26 | 33 | 0.0014172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_356-29_1_3_line_30 |  | 27 | 28 | 0.038904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_356-29_1_3_line_31 |  | 28 | 29 | 0.020347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_356-29_1_3_line_32 |  | 28 | 30 | 0.010331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_356-29_1_3_line_33 |  | 29 | 87 | 0.0091285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_356-29_1_3_line_34 |  | 30 | 92 | 0.0077935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_356-29_1_3_line_35 |  | 31 | 83 | 0.00085471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_356-29_1_3_line_36 |  | 32 | 84 | 0.0055589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_356-29_1_3_line_37 |  | 33 | 62 | 0.0051489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_356-29_1_3_line_38 |  | 34 | 61 | 0.020819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_356-29_1_3_line_39 |  | 34 | 60 | 0.0019459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_356-29_1_3_line_40 |  | 35 | 36 | 0.0027756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_356-29_1_3_line_41 |  | 36 | 37 | 0.0030918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_356-29_1_3_line_42 |  | 37 | 38 | 0.0065457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_356-29_1_3_line_43 |  | 38 | 44 | 0.011488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_356-29_1_3_line_44 |  | 39 | 40 | 0.0057261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_356-29_1_3_line_45 |  | 40 | 45 | 0.017893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_356-29_1_3_line_46 |  | 41 | 42 | 0.018726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_356-29_1_3_line_47 |  | 41 | 43 | 0.0096413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_356-29_1_3_line_48 |  | 42 | 46 | 0.005562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_356-29_1_3_line_49 |  | 43 | 47 | 0.01715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_356-29_1_3_line_50 |  | 44 | 48 | 0.023808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_356-29_1_3_line_51 |  | 45 | 49 | 0.013501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_356-29_1_3_line_52 |  | 46 | 56 | 0.012616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_356-29_1_3_line_53 |  | 48 | 53 | 0.011748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_356-29_1_3_line_54 |  | 49 | 59 | 0.012504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_356-29_1_3_line_55 |  | 50 | 51 | 0.0058474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_356-29_1_3_line_56 |  | 50 | 52 | 0.0031002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_356-29_1_3_line_57 |  | 51 | 53 | 0.013357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_356-29_1_3_line_58 |  | 52 | 54 | 0.0098295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_356-29_1_3_line_59 |  | 53 | 55 | 0.0077573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_356-29_1_3_line_60 |  | 54 | 56 | 0.018666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_356-29_1_3_line_61 |  | 55 | 57 | 0.0083586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_356-29_1_3_line_62 |  | 57 | 58 | 0.00058363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_356-29_1_3_line_63 |  | 58 | 81 | 0.020498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_356-29_1_3_line_64 |  | 59 | 60 | 0.0076338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_356-29_1_3_line_65 |  | 62 | 63 | 0.00081506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_356-29_1_3_line_66 |  | 63 | 64 | 0.01779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_356-29_1_3_line_67 |  | 64 | 65 | 0.0034877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_356-29_1_3_line_68 |  | 65 | 66 | 0.014875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_356-29_1_3_line_69 |  | 66 | 75 | 0.0074591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_356-29_1_3_line_70 |  | 67 | 68 | 0.021373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_356-29_1_3_line_71 |  | 68 | 69 | 0.033081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_356-29_1_3_line_72 |  | 69 | 70 | 0.008505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_356-29_1_3_line_73 |  | 69 | 71 | 0.013689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_356-29_1_3_line_74 |  | 71 | 72 | 0.0070067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_356-29_1_3_line_75 |  | 72 | 73 | 0.0061383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_356-29_1_3_line_76 |  | 73 | 86 | 0.012954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_356-29_1_3_line_77 |  | 74 | 75 | 0.016148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_356-29_1_3_line_78 |  | 74 | 76 | 0.0063734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_356-29_1_3_line_79 |  | 76 | 77 | 0.020635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_356-29_1_3_line_80 |  | 77 | 78 | 0.0089466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_356-29_1_3_line_81 |  | 78 | 79 | 0.0097086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_356-29_1_3_line_82 |  | 79 | 80 | 0.01134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_356-29_1_3_line_83 |  | 80 | 82 | 0.0092805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_356-29_1_3_line_84 |  | 81 | 82 | 0.00056374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_356-29_1_3_line_85 |  | 83 | 85 | 0.0084877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_356-29_1_3_line_86 |  | 85 | 88 | 0.00064608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_356-29_1_3_line_87 |  | 86 | 87 | 0.0070013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_356-29_1_3_line_88 |  | 88 | 89 | 0.019343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_356-29_1_3_line_89 |  | 89 | 90 | 0.0018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_356-29_1_3_line_90 |  | 90 | 91 | 0.00069544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_356-29_1_3_line_91 |  | 91 | 92 | 0.023388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_356-29_1_3_trafo_107 | 0.63 MVA 20/0.4 kV | 93 | 66 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2605279.0996 | 1198434.8571 | 2605286.3172 | 1198438.4848
1 | 2605260.3197 | 1198424.1355 | 2605263.8811 | 1198426.6733 | 2605270.5481 | 1198430.5589 | 2605279.0996 | 1198434.8571
2 | 2605304.3353 | 1198447.5412 | 2605286.3172 | 1198438.4848
3 | 2605260.3197 | 1198424.1355 | 2605260.4371 | 1198446.681 | 2605260.3413 | 1198446.8656
4 | 2605260.3197 | 1198424.1355 | 2605258.2904 | 1198422.3124
5 | 2605324.0698 | 1198457.4602 | 2605304.3353 | 1198447.5412
6 | 2605254.8271 | 1198453.1907 | 2605257.9811 | 1198451.4147 | 2605260.3413 | 1198446.8656
7 | 2605243.1305 | 1198401.1639 | 2605251.8828 | 1198415.2012 | 2605256.0588 | 1198420.3075 | 2605258.2904 | 1198422.3124
8 | 2605254.8271 | 1198453.1907 | 2605255.2008 | 1198461.3509 | 2605255.1268 | 1198483.9551
9 | 2605254.8271 | 1198453.1907 | 2605245.6404 | 1198453.0518
10 | 2605243.1305 | 1198401.1639 | 2605231.0289 | 1198403.399 | 2605203.7513 | 1198403.3986
11 | 2605243.1305 | 1198401.1639 | 2605247.578 | 1198400.5785
12 | 2605255.4601 | 1198496.003 | 2605255.1075 | 1198489.8327 | 2605255.1268 | 1198483.9551
13 | 2605216.9392 | 1198452.6178 | 2605245.6404 | 1198453.0518
14 | 2605201.6227 | 1198403.3986 | 2605203.7513 | 1198403.3986
15 | 2605247.578 | 1198400.5785 | 2605262.0255 | 1198397.7117 | 2605277.1205 | 1198394.4898 | 2605288.0932 | 1198392.2113
16 | 2605376.4962 | 1198500.8897 | 2605367.1407 | 1198506.3732 | 2605361.1335 | 1198505.6564 | 2605334.0656 | 1198495.0268
17 | 2605371.3558 | 1198518.6168 | 2605378.1038 | 1198508.3173 | 2605376.4962 | 1198500.8897
18 | 2605310.9785 | 1198494.8508 | 2605334.0656 | 1198495.0268
19 | 2605255.4601 | 1198496.003 | 2605307.0869 | 1198494.9316
20 | 2605255.4601 | 1198496.003 | 2605241.4842 | 1198496.8507
21 | 2605201.6227 | 1198403.3986 | 2605195.5191 | 1198403.3985
22 | 2605303.6701 | 1198388.8878 | 2605289.6489 | 1198391.8882 | 2605288.0932 | 1198392.2113
23 | 2605310.9785 | 1198494.8508 | 2605308.2671 | 1198504.3202
24 | 2605310.9785 | 1198494.8508 | 2605307.0869 | 1198494.9316
25 | 2605308.2671 | 1198504.3202 | 2605314.6651 | 1198523.7286
26 | 2605308.2671 | 1198504.3202 | 2605297.2303 | 1198508.1459 | 2605281.7293 | 1198511.366
27 | 2605303.6701 | 1198388.8878 | 2605320.4821 | 1198384.7152
28 | 2605178.4118 | 1198403.3983 | 2605195.5191 | 1198403.3985
29 | 2605240.0696 | 1198496.9365 | 2605241.4842 | 1198496.8507
30 | 2605339.3781 | 1198592.7393 | 2605377.5065 | 1198585.0086
31 | 2605339.3781 | 1198592.7393 | 2605319.4872 | 1198597.0243
32 | 2605339.3781 | 1198592.7393 | 2605337.2141 | 1198585.8448 | 2605336.0039 | 1198582.9852
33 | 2605310.5564 | 1198598.913 | 2605314.2458 | 1198598.1534 | 2605319.4872 | 1198597.0243
34 | 2605332.9664 | 1198575.8081 | 2605336.0039 | 1198582.9852
35 | 2605314.6651 | 1198523.7286 | 2605314.9326 | 1198524.5404
36 | 2605276.2866 | 1198512.4966 | 2605281.7293 | 1198511.366
37 | 2605240.0696 | 1198496.9365 | 2605234.9301 | 1198497.2483
38 | 2605178.7671 | 1198424.2097 | 2605178.4118 | 1198403.3983
39 | 2605178.4118 | 1198403.3983 | 2605176.4665 | 1198403.3477
40 | 2605090.913 | 1198417.6549 | 2605089.9821 | 1198420.2697
41 | 2605089.9821 | 1198420.2697 | 2605088.9451 | 1198423.1824
42 | 2605088.9451 | 1198423.1824 | 2605086.7497 | 1198429.349
43 | 2605082.8933 | 1198440.1704 | 2605084.7251 | 1198435.0358 | 2605086.7497 | 1198429.349
44 | 2605125.1122 | 1198399.9622 | 2605119.4838 | 1198398.909
45 | 2605125.1122 | 1198399.9622 | 2605142.8557 | 1198402.2671
46 | 2605060.9011 | 1198414.3159 | 2605058.2307 | 1198420.7505 | 2605053.3179 | 1198431.441
47 | 2605060.9011 | 1198414.3159 | 2605051.626 | 1198416.9476
48 | 2605053.3179 | 1198431.441 | 2605051.6582 | 1198436.7495
49 | 2605035.1482 | 1198415.3321 | 2605046.0948 | 1198418.5169 | 2605051.626 | 1198416.9476
50 | 2605082.8933 | 1198440.1704 | 2605076.5926 | 1198463.1294
51 | 2605142.8557 | 1198402.2671 | 2605144.8396 | 1198402.5248 | 2605156.3358 | 1198402.8239
52 | 2605047.8937 | 1198448.7904 | 2605051.6582 | 1198436.7495
53 | 2605073.4834 | 1198474.4586 | 2605076.5926 | 1198463.1294
54 | 2605168.8352 | 1198403.1491 | 2605156.3358 | 1198402.8239
55 | 2605054.8613 | 1198469.7657 | 2605060.5314 | 1198471.1946
56 | 2605054.8613 | 1198469.7657 | 2605051.8551 | 1198469.0081
57 | 2605073.4834 | 1198474.4586 | 2605060.5314 | 1198471.1946
58 | 2605042.3236 | 1198466.6062 | 2605051.8551 | 1198469.0081
59 | 2605073.4834 | 1198474.4586 | 2605080.989 | 1198476.4184
60 | 2605042.3236 | 1198466.6062 | 2605047.8937 | 1198448.7904
61 | 2605089.0764 | 1198478.5302 | 2605080.989 | 1198476.4184
62 | 2605089.6411 | 1198478.6777 | 2605089.0764 | 1198478.5302
63 | 2605109.4737 | 1198483.8563 | 2605089.6411 | 1198478.6777
64 | 2605168.8352 | 1198403.1491 | 2605176.4665 | 1198403.3477
65 | 2605234.9301 | 1198497.2483 | 2605234.1166 | 1198497.2976
66 | 2605216.3512 | 1198498.1227 | 2605220.5837 | 1198498.1184 | 2605234.1166 | 1198497.2976
67 | 2605216.3512 | 1198498.1227 | 2605212.8635 | 1198498.1263
68 | 2605197.988 | 1198498.1415 | 2605212.8635 | 1198498.1263
69 | 2605197.988 | 1198498.1415 | 2605190.529 | 1198498.1491
70 | 2605211.3233 | 1198618.6486 | 2605215.3333 | 1198617.7112 | 2605232.1045 | 1198613.6546
71 | 2605264.7282 | 1198608.3489 | 2605251.6754 | 1198610.3275 | 2605239.2398 | 1198611.9287 | 2605232.1045 | 1198613.6546
72 | 2605264.7282 | 1198608.3489 | 2605258.2303 | 1198602.8403
73 | 2605264.7282 | 1198608.3489 | 2605278.1362 | 1198605.5882
74 | 2605278.1362 | 1198605.5882 | 2605284.999 | 1198604.1752
75 | 2605284.999 | 1198604.1752 | 2605291.0112 | 1198602.9373
76 | 2605303.6989 | 1198600.325 | 2605291.0112 | 1198602.9373
77 | 2605174.3806 | 1198498.1655 | 2605190.529 | 1198498.1491
78 | 2605174.3806 | 1198498.1655 | 2605168.0071 | 1198498.172
79 | 2605168.0071 | 1198498.172 | 2605161.3351 | 1198498.1788 | 2605147.8771 | 1198494.4569
80 | 2605139.2542 | 1198492.0722 | 2605147.8771 | 1198494.4569
81 | 2605139.2542 | 1198492.0722 | 2605129.8968 | 1198489.4844
82 | 2605129.8968 | 1198489.4844 | 2605118.9668 | 1198486.4617
83 | 2605118.9668 | 1198486.4617 | 2605110.7713 | 1198484.1951 | 2605110.0191 | 1198483.9987
84 | 2605110.0191 | 1198483.9987 | 2605109.4737 | 1198483.8563
85 | 2605317.5104 | 1198532.6271 | 2605315.1551 | 1198525.2152 | 2605314.9326 | 1198524.5404
86 | 2605317.5104 | 1198532.6271 | 2605317.7061 | 1198533.2429
87 | 2605303.6989 | 1198600.325 | 2605310.5564 | 1198598.913
88 | 2605317.7061 | 1198533.2429 | 2605320.3566 | 1198541.584 | 2605323.7763 | 1198551.608
89 | 2605324.3637 | 1198553.3298 | 2605323.7763 | 1198551.608
90 | 2605324.3637 | 1198553.3298 | 2605324.5883 | 1198553.988
91 | 2605332.9664 | 1198575.8081 | 2605328.149 | 1198564.4253 | 2605324.5883 | 1198553.988

## bus_geodata
| x | y | coords
0 | 2605279.0996 | 1198434.8571
1 | 2605286.3172 | 1198438.4848
2 | 2605260.3197 | 1198424.1355
3 | 2605304.3353 | 1198447.5412
4 | 2605260.3413 | 1198446.8656
5 | 2605258.2904 | 1198422.3124
6 | 2605324.0698 | 1198457.4602
7 | 2605254.8271 | 1198453.1907
8 | 2605243.1305 | 1198401.1639
9 | 2605255.1268 | 1198483.9551
10 | 2605245.6404 | 1198453.0518
11 | 2605203.7513 | 1198403.3986
12 | 2605247.578 | 1198400.5785
13 | 2605376.4962 | 1198500.8897
14 | 2605334.0656 | 1198495.0268
15 | 2605371.3558 | 1198518.6168
16 | 2605255.4601 | 1198496.003
17 | 2605216.9392 | 1198452.6178
18 | 2605201.6227 | 1198403.3986
19 | 2605288.0932 | 1198392.2113
20 | 2605310.9785 | 1198494.8508
21 | 2605308.2671 | 1198504.3202
22 | 2605307.0869 | 1198494.9316
23 | 2605303.6701 | 1198388.8878
24 | 2605320.4821 | 1198384.7152
25 | 2605195.5191 | 1198403.3985
26 | 2605241.4842 | 1198496.8507
27 | 2605377.5065 | 1198585.0086
28 | 2605339.3781 | 1198592.7393
29 | 2605319.4872 | 1198597.0243
30 | 2605336.0039 | 1198582.9852
31 | 2605314.6651 | 1198523.7286
32 | 2605281.7293 | 1198511.366
33 | 2605240.0696 | 1198496.9365
34 | 2605178.4118 | 1198403.3983
35 | 2605090.913 | 1198417.6549
36 | 2605089.9821 | 1198420.2697
37 | 2605088.9451 | 1198423.1824
38 | 2605086.7497 | 1198429.349
39 | 2605119.4838 | 1198398.909
40 | 2605125.1122 | 1198399.9622
41 | 2605060.9011 | 1198414.3159
42 | 2605053.3179 | 1198431.441
43 | 2605051.626 | 1198416.9476
44 | 2605082.8933 | 1198440.1704
45 | 2605142.8557 | 1198402.2671
46 | 2605051.6582 | 1198436.7495
47 | 2605035.1482 | 1198415.3321
48 | 2605076.5926 | 1198463.1294
49 | 2605156.3358 | 1198402.8239
50 | 2605054.8613 | 1198469.7657
51 | 2605060.5314 | 1198471.1946
52 | 2605051.8551 | 1198469.0081
53 | 2605073.4834 | 1198474.4586
54 | 2605042.3236 | 1198466.6062
55 | 2605080.989 | 1198476.4184
56 | 2605047.8937 | 1198448.7904
57 | 2605089.0764 | 1198478.5302
58 | 2605089.6411 | 1198478.6777
59 | 2605168.8352 | 1198403.1491
60 | 2605176.4665 | 1198403.3477
61 | 2605178.7671 | 1198424.2097
62 | 2605234.9301 | 1198497.2483
63 | 2605234.1166 | 1198497.2976
64 | 2605216.3512 | 1198498.1227
65 | 2605212.8635 | 1198498.1263
66 | 2605197.988 | 1198498.1415
67 | 2605211.3233 | 1198618.6486
68 | 2605232.1045 | 1198613.6546
69 | 2605264.7282 | 1198608.3489
70 | 2605258.2303 | 1198602.8403
71 | 2605278.1362 | 1198605.5882
72 | 2605284.999 | 1198604.1752
73 | 2605291.0112 | 1198602.9373
74 | 2605174.3806 | 1198498.1655
75 | 2605190.529 | 1198498.1491
76 | 2605168.0071 | 1198498.172
77 | 2605147.8771 | 1198494.4569
78 | 2605139.2542 | 1198492.0722
79 | 2605129.8968 | 1198489.4844
80 | 2605118.9668 | 1198486.4617
81 | 2605109.4737 | 1198483.8563
82 | 2605110.0191 | 1198483.9987
83 | 2605314.9326 | 1198524.5404
84 | 2605276.2866 | 1198512.4966
85 | 2605317.5104 | 1198532.6271
86 | 2605303.6989 | 1198600.325
87 | 2605310.5564 | 1198598.913
88 | 2605317.7061 | 1198533.2429
89 | 2605323.7763 | 1198551.608
90 | 2605324.3637 | 1198553.3298
91 | 2605324.5883 | 1198553.988
92 | 2605332.9664 | 1198575.8081
93 | 2605255.4601 | 1198496.003

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1