## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_358-3_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_358-3_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_358-3_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_358-3_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_358-3_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_358-3_0_6_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_358-3_0_6_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_358-3_0_6_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_358-3_0_6_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_358-3_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_358-3_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_358-3_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_358-3_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_358-3_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_358-3_0_6_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_358-3_0_6_node_18 | 0.4 | n |  | TRUE
16 | bus_LV_358-3_0_6_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_358-3_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_358-3_0_6_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_358-3_0_6_node_144 | 0.4 | n |  | TRUE
20 | bus_LV_358-3_0_6_node_164 | 0.4 | n |  | TRUE
21 | bus_LV_358-3_0_6_node_145 | 0.4 | n |  | TRUE
22 | bus_LV_358-3_0_6_node_166 | 0.4 | n |  | TRUE
23 | bus_LV_358-3_0_6_node_45 | 0.4 | n |  | TRUE
24 | bus_LV_358-3_0_6_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_358-3_0_6_node_138 | 0.4 | n |  | TRUE
26 | bus_LV_358-3_0_6_node_137 | 0.4 | n |  | TRUE
27 | bus_LV_358-3_0_6_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_358-3_0_6_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_358-3_0_6_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_358-3_0_6_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_358-3_0_6_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_358-3_0_6_node_63 | 0.4 | n |  | TRUE
33 | bus_LV_358-3_0_6_node_84 | 0.4 | n |  | TRUE
34 | bus_LV_358-3_0_6_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_358-3_0_6_node_85 | 0.4 | n |  | TRUE
36 | bus_LV_358-3_0_6_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_358-3_0_6_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_358-3_0_6_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_358-3_0_6_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_358-3_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_358-3_0_6_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_358-3_0_6_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_358-3_0_6_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_358-3_0_6_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_358-3_0_6_node_115 | 0.4 | n |  | TRUE
46 | bus_LV_358-3_0_6_node_156 | 0.4 | n |  | TRUE
47 | bus_LV_358-3_0_6_node_48 | 0.4 | n |  | TRUE
48 | bus_LV_358-3_0_6_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_358-3_0_6_node_116 | 0.4 | n |  | TRUE
50 | bus_LV_358-3_0_6_node_105 | 0.4 | n |  | TRUE
51 | bus_LV_358-3_0_6_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_358-3_0_6_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_358-3_0_6_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_358-3_0_6_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_358-3_0_6_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_358-3_0_6_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_358-3_0_6_node_71 | 0.4 | n |  | TRUE
58 | bus_LV_358-3_0_6_node_72 | 0.4 | n |  | TRUE
59 | bus_LV_358-3_0_6_node_61 | 0.4 | n |  | TRUE
60 | bus_LV_358-3_0_6_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_358-3_0_6_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_358-3_0_6_node_62 | 0.4 | n |  | TRUE
63 | bus_LV_358-3_0_6_node_104 | 0.4 | n |  | TRUE
64 | bus_LV_358-3_0_6_node_91 | 0.4 | n |  | TRUE
65 | bus_LV_358-3_0_6_node_86 | 0.4 | n |  | TRUE
66 | bus_LV_358-3_0_6_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_358-3_0_6_node_41 | 0.4 | n |  | TRUE
68 | bus_LV_358-3_0_6_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_358-3_0_6_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_358-3_0_6_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_358-3_0_6_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_358-3_0_6_node_143 | 0.4 | n |  | TRUE
73 | bus_LV_358-3_0_6_node_142 | 0.4 | n |  | TRUE
74 | bus_LV_358-3_0_6_node_151 | 0.4 | n |  | TRUE
75 | bus_LV_358-3_0_6_node_90 | 0.4 | n |  | TRUE
76 | bus_LV_358-3_0_6_node_141 | 0.4 | n |  | TRUE
77 | bus_LV_358-3_0_6_node_150 | 0.4 | n |  | TRUE
78 | bus_LV_358-3_0_6_node_88 | 0.4 | n |  | TRUE
79 | bus_LV_358-3_0_6_node_87 | 0.4 | n |  | TRUE
80 | bus_LV_358-3_0_6_node_51 | 0.4 | n |  | TRUE
81 | bus_LV_358-3_0_6_node_54 | 0.4 | n |  | TRUE
82 | bus_LV_358-3_0_6_node_55 | 0.4 | n |  | TRUE
83 | bus_LV_358-3_0_6_node_89 | 0.4 | n |  | TRUE
84 | bus_LV_358-3_0_6_node_93 | 0.4 | n |  | TRUE
85 | bus_LV_358-3_0_6_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_358-3_0_6_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_358-3_0_6_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_358-3_0_6_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_358-3_0_6_node_60 | 0.4 | n |  | TRUE
90 | bus_LV_358-3_0_6_node_99 | 0.4 | n |  | TRUE
91 | bus_LV_358-3_0_6_node_101 | 0.4 | n |  | TRUE
92 | bus_LV_358-3_0_6_node_100 | 0.4 | n |  | TRUE
93 | bus_LV_358-3_0_6_node_147 | 0.4 | n |  | TRUE
94 | bus_LV_358-3_0_6_node_146 | 0.4 | n |  | TRUE
95 | bus_LV_358-3_0_6_node_165 | 0.4 | n |  | TRUE
96 | bus_LV_358-3_0_6_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_358-3_0_6_node_102 | 0.4 | n |  | TRUE
98 | bus_LV_358-3_0_6_node_103 | 0.4 | n |  | TRUE
99 | bus_LV_358-3_0_6_node_66 | 0.4 | n |  | TRUE
100 | bus_LV_358-3_0_6_node_67 | 0.4 | n |  | TRUE
101 | bus_LV_358-3_0_6_node_68 | 0.4 | n |  | TRUE
102 | bus_LV_358-3_0_6_node_69 | 0.4 | n |  | TRUE
103 | bus_LV_358-3_0_6_node_70 | 0.4 | n |  | TRUE
104 | bus_LV_358-3_0_6_node_98 | 0.4 | n |  | TRUE
105 | bus_LV_358-3_0_6_node_73 | 0.4 | n |  | TRUE
106 | bus_LV_358-3_0_6_node_74 | 0.4 | n |  | TRUE
107 | bus_LV_358-3_0_6_node_75 | 0.4 | n |  | TRUE
108 | bus_LV_358-3_0_6_node_76 | 0.4 | n |  | TRUE
109 | bus_LV_358-3_0_6_node_77 | 0.4 | n |  | TRUE
110 | bus_LV_358-3_0_6_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_358-3_0_6_node_94 | 0.4 | n |  | TRUE
112 | bus_LV_358-3_0_6_node_78 | 0.4 | n |  | TRUE
113 | bus_LV_358-3_0_6_node_79 | 0.4 | n |  | TRUE
114 | bus_LV_358-3_0_6_node_80 | 0.4 | n |  | TRUE
115 | bus_LV_358-3_0_6_node_81 | 0.4 | n |  | TRUE
116 | bus_LV_358-3_0_6_node_82 | 0.4 | n |  | TRUE
117 | bus_LV_358-3_0_6_node_83 | 0.4 | n |  | TRUE
118 | bus_LV_358-3_0_6_node_92 | 0.4 | n |  | TRUE
119 | bus_LV_358-3_0_6_node_139 | 0.4 | n |  | TRUE
120 | bus_LV_358-3_0_6_node_140 | 0.4 | n |  | TRUE
121 | bus_LV_358-3_0_6_node_96 | 0.4 | n |  | TRUE
122 | bus_LV_358-3_0_6_node_97 | 0.4 | n |  | TRUE
123 | bus_LV_358-3_0_6_node_161 | 0.4 | n |  | TRUE
124 | bus_LV_358-3_0_6_node_162 | 0.4 | n |  | TRUE
125 | bus_LV_358-3_0_6_node_106 | 0.4 | n |  | TRUE
126 | bus_LV_358-3_0_6_node_107 | 0.4 | n |  | TRUE
127 | bus_LV_358-3_0_6_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_358-3_0_6_node_109 | 0.4 | n |  | TRUE
129 | bus_LV_358-3_0_6_node_117 | 0.4 | n |  | TRUE
130 | bus_LV_358-3_0_6_node_120 | 0.4 | n |  | TRUE
131 | bus_LV_358-3_0_6_node_118 | 0.4 | n |  | TRUE
132 | bus_LV_358-3_0_6_node_110 | 0.4 | n |  | TRUE
133 | bus_LV_358-3_0_6_node_111 | 0.4 | n |  | TRUE
134 | bus_LV_358-3_0_6_node_112 | 0.4 | n |  | TRUE
135 | bus_LV_358-3_0_6_node_113 | 0.4 | n |  | TRUE
136 | bus_LV_358-3_0_6_node_114 | 0.4 | n |  | TRUE
137 | bus_LV_358-3_0_6_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_358-3_0_6_node_135 | 0.4 | n |  | TRUE
139 | bus_LV_358-3_0_6_node_119 | 0.4 | n |  | TRUE
140 | bus_LV_358-3_0_6_node_134 | 0.4 | n |  | TRUE
141 | bus_LV_358-3_0_6_node_133 | 0.4 | n |  | TRUE
142 | bus_LV_358-3_0_6_node_121 | 0.4 | n |  | TRUE
143 | bus_LV_358-3_0_6_node_122 | 0.4 | n |  | TRUE
144 | bus_LV_358-3_0_6_node_123 | 0.4 | n |  | TRUE
145 | bus_LV_358-3_0_6_node_124 | 0.4 | n |  | TRUE
146 | bus_LV_358-3_0_6_node_125 | 0.4 | n |  | TRUE
147 | bus_LV_358-3_0_6_node_129 | 0.4 | n |  | TRUE
148 | bus_LV_358-3_0_6_node_153 | 0.4 | n |  | TRUE
149 | bus_LV_358-3_0_6_node_127 | 0.4 | n |  | TRUE
150 | bus_LV_358-3_0_6_node_152 | 0.4 | n |  | TRUE
151 | bus_LV_358-3_0_6_node_126 | 0.4 | n |  | TRUE
152 | bus_LV_358-3_0_6_node_128 | 0.4 | n |  | TRUE
153 | bus_LV_358-3_0_6_node_130 | 0.4 | n |  | TRUE
154 | bus_LV_358-3_0_6_node_132 | 0.4 | n |  | TRUE
155 | bus_LV_358-3_0_6_node_131 | 0.4 | n |  | TRUE
156 | bus_LV_358-3_0_6_node_148 | 0.4 | n |  | TRUE
157 | bus_LV_358-3_0_6_node_149 | 0.4 | n |  | TRUE
158 | bus_LV_358-3_0_6_node_154 | 0.4 | n |  | TRUE
159 | bus_LV_358-3_0_6_node_155 | 0.4 | n |  | TRUE
160 | bus_LV_358-3_0_6_node_163 | 0.4 | n |  | TRUE
161 | bus_LV_358-3_0_6_node_160 | 0.4 | n |  | TRUE
162 | bus_LV_358-3_0_6_node_157 | 0.4 | n |  | TRUE
163 | bus_LV_358-3_0_6_node_158 | 0.4 | n |  | TRUE
164 | bus_LV_358-3_0_6_node_159 | 0.4 | n |  | TRUE
165 | bus_MV_599_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_358-3_0_6_load_0 | 0 | 0.0028579 | 0.00071625 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_358-3_0_6_load_1 | 1 | 0.0026745 | 0.00067029 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_358-3_0_6_load_3 | 3 | 0.0019654 | 0.00049258 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_358-3_0_6_load_4 | 4 | 0.0025919 | 0.00064959 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_358-3_0_6_load_20 | 5 | 0.0038024 | 0.00095297 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_358-3_0_6_load_11 | 7 | 0.0016444 | 0.00041213 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_358-3_0_6_load_12 | 8 | 0.0019197 | 0.00048113 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_358-3_0_6_load_5 | 9 | 0.0036934 | 0.00092565 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_358-3_0_6_load_6 | 10 | 0.0070063 | 0.0017559 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_358-3_0_6_load_7 | 11 | 0.0044962 | 0.0011268 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_358-3_0_6_load_8 | 12 | 0.0032066 | 0.00080366 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_358-3_0_6_load_9 | 13 | 0.0022056 | 0.00055276 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_358-3_0_6_load_17 | 14 | 0.0077504 | 0.0019424 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_358-3_0_6_load_18 | 15 | 0.0050752 | 0.001272 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_358-3_0_6_load_15 | 16 | 0.011746 | 0.0029439 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_358-3_0_6_load_13 | 17 | 0.0029557 | 0.00074077 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_358-3_0_6_load_14 | 18 | 0.0029109 | 0.00072953 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_358-3_0_6_load_144 | 19 | 0.0017653 | 0.00044242 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_358-3_0_6_load_164 | 20 | 0.0012236 | 0.00030665 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_358-3_0_6_load_145 | 21 | 0.0017762 | 0.00044516 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_358-3_0_6_load_166 | 22 | 0.027751 | 0.0069551 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_358-3_0_6_load_19 | 24 | 0.0055761 | 0.0013975 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_358-3_0_6_load_138 | 25 | 0.0027409 | 0.00068694 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_358-3_0_6_load_137 | 26 | 0.0096701 | 0.0024236 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_358-3_0_6_load_22 | 27 | 0.0020543 | 0.00051486 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_358-3_0_6_load_23 | 28 | 0.0017622 | 0.00044166 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_358-3_0_6_load_24 | 29 | 0.0018606 | 0.0004663 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_358-3_0_6_load_25 | 30 | 0.0028019 | 0.00070223 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_358-3_0_6_load_26 | 31 | 0.0020099 | 0.00050372 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_358-3_0_6_load_63 | 32 | 0.0017873 | 0.00044793 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_358-3_0_6_load_84 | 33 | 0.0024815 | 0.00062193 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_358-3_0_6_load_64 | 34 | 0.001767 | 0.00044285 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_358-3_0_6_load_85 | 35 | 0.0019186 | 0.00048085 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_358-3_0_6_load_27 | 36 | 0.0044637 | 0.0011187 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_358-3_0_6_load_28 | 37 | 0.001726 | 0.00043259 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_358-3_0_6_load_30 | 39 | 0.0037481 | 0.00093935 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_358-3_0_6_load_31 | 40 | 0.0030359 | 0.00076086 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_358-3_0_6_load_32 | 41 | 0.0029716 | 0.00074476 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_358-3_0_6_load_33 | 42 | 0.002633 | 0.0006599 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_358-3_0_6_load_47 | 43 | 0.0025203 | 0.00063164 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_358-3_0_6_load_53 | 44 | 0.0015592 | 0.00039077 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_358-3_0_6_load_115 | 45 | 0.0020978 | 0.00052575 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_358-3_0_6_load_156 | 46 | 0.0021337 | 0.00053475 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_358-3_0_6_load_48 | 47 | 0.0057219 | 0.001434 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_358-3_0_6_load_52 | 48 | 0.0030902 | 0.00077449 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_358-3_0_6_load_116 | 49 | 0.0028235 | 0.00070765 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_358-3_0_6_load_105 | 50 | 0.0034226 | 0.00085779 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_358-3_0_6_load_34 | 51 | 0.0024613 | 0.00061685 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_358-3_0_6_load_35 | 52 | 0.0033309 | 0.0008348 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_358-3_0_6_load_37 | 54 | 0.0018304 | 0.00045874 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_358-3_0_6_load_38 | 55 | 0.0034817 | 0.00087261 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_358-3_0_6_load_39 | 56 | 0.0030442 | 0.00076295 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_358-3_0_6_load_71 | 57 | 0.0020379 | 0.00051074 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_358-3_0_6_load_72 | 58 | 0.0030547 | 0.00076558 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_358-3_0_6_load_49 | 60 | 0.00086596 | 0.00021703 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_358-3_0_6_load_50 | 61 | 0.0053711 | 0.0013461 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_358-3_0_6_load_104 | 63 | 0.0030418 | 0.00076235 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_358-3_0_6_load_91 | 64 | 0.0022872 | 0.00057323 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_358-3_0_6_load_86 | 65 | 0.0051902 | 0.0013008 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_358-3_0_6_load_40 | 66 | 0.011665 | 0.0029235 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_358-3_0_6_load_43 | 69 | 0.0045089 | 0.00113 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_358-3_0_6_load_143 | 72 | 0.0074051 | 0.0018559 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_358-3_0_6_load_142 | 73 | 0.0040016 | 0.0010029 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_358-3_0_6_load_151 | 74 | 0.0047186 | 0.0011826 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_358-3_0_6_load_141 | 76 | 0.0053824 | 0.001349 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_358-3_0_6_load_150 | 77 | 0.004331 | 0.0010854 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_358-3_0_6_load_88 | 78 | 0.0097536 | 0.0024445 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_358-3_0_6_load_87 | 79 | 0.006354 | 0.0015925 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_358-3_0_6_load_51 | 80 | 0.0074894 | 0.001877 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_358-3_0_6_load_54 | 81 | 0.0015079 | 0.0003779 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_358-3_0_6_load_55 | 82 | 0.0016058 | 0.00040246 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_358-3_0_6_load_89 | 83 | 0.0031756 | 0.00079588 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_358-3_0_6_load_93 | 84 | 0.0031662 | 0.00079352 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_358-3_0_6_load_56 | 85 | 0.0040011 | 0.0010028 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_358-3_0_6_load_57 | 86 | 0.0034602 | 0.0008672 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_358-3_0_6_load_58 | 87 | 0.0032414 | 0.00081237 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_358-3_0_6_load_59 | 88 | 0.0065131 | 0.0016323 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_358-3_0_6_load_99 | 90 | 0.0051203 | 0.0012833 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_358-3_0_6_load_101 | 91 | 0.0032158 | 0.00080596 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_358-3_0_6_load_100 | 92 | 0.005778 | 0.0014481 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_358-3_0_6_load_146 | 94 | 0.0011297 | 0.00028314 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_358-3_0_6_load_165 | 95 | 0.0087457 | 0.0021919 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_358-3_0_6_load_65 | 96 | 0.0019153 | 0.00048003 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_358-3_0_6_load_102 | 97 | 0.0027156 | 0.0006806 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_358-3_0_6_load_103 | 98 | 0.022978 | 0.0057589 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_358-3_0_6_load_66 | 99 | 0.0027324 | 0.0006848 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_358-3_0_6_load_67 | 100 | 0.0024711 | 0.00061932 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_358-3_0_6_load_68 | 101 | 0.004244 | 0.0010636 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_358-3_0_6_load_69 | 102 | 0.0020818 | 0.00052175 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_358-3_0_6_load_70 | 103 | 0.0024082 | 0.00060356 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_358-3_0_6_load_98 | 104 | 0.0023055 | 0.00057782 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_358-3_0_6_load_73 | 105 | 0.0034992 | 0.00087698 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_358-3_0_6_load_74 | 106 | 0.0038094 | 0.00095472 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_358-3_0_6_load_75 | 107 | 0.0032771 | 0.00082131 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_358-3_0_6_load_76 | 108 | 0.0020059 | 0.00050272 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_358-3_0_6_load_77 | 109 | 0.0032665 | 0.00081866 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_358-3_0_6_load_95 | 110 | 0.0033132 | 0.00083038 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_358-3_0_6_load_94 | 111 | 0.0041682 | 0.0010447 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_358-3_0_6_load_78 | 112 | 0.0044926 | 0.0011259 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_358-3_0_6_load_79 | 113 | 0.0048786 | 0.0012227 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_358-3_0_6_load_81 | 115 | 0.0037936 | 0.00095076 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_358-3_0_6_load_82 | 116 | 0.0042928 | 0.0010759 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_358-3_0_6_load_83 | 117 | 0.0040576 | 0.0010169 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_358-3_0_6_load_92 | 118 | 0.0037972 | 0.00095168 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_358-3_0_6_load_140 | 120 | 0.0032995 | 0.00082692 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_358-3_0_6_load_96 | 121 | 0.00064945 | 0.00016277 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_358-3_0_6_load_97 | 122 | 0.0016867 | 0.00042271 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_358-3_0_6_load_161 | 123 | 0.0031655 | 0.00079335 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_358-3_0_6_load_162 | 124 | 0.0030843 | 0.000773 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_358-3_0_6_load_106 | 125 | 0.002813 | 0.000705 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_358-3_0_6_load_107 | 126 | 0.0027405 | 0.00068684 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_358-3_0_6_load_108 | 127 | 0.0059351 | 0.0014875 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_358-3_0_6_load_109 | 128 | 0.0037339 | 0.0009358 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_358-3_0_6_load_117 | 129 | 0.004107 | 0.0010293 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_358-3_0_6_load_120 | 130 | 0.00339 | 0.0008496 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_358-3_0_6_load_118 | 131 | 0.0045491 | 0.0011401 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_358-3_0_6_load_110 | 132 | 0.0025654 | 0.00064295 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_358-3_0_6_load_111 | 133 | 0.0030133 | 0.0007552 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_358-3_0_6_load_112 | 134 | 0.0020499 | 0.00051375 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_358-3_0_6_load_113 | 135 | 0.0035142 | 0.00088075 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_358-3_0_6_load_114 | 136 | 0.0025037 | 0.00062749 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_358-3_0_6_load_136 | 137 | 0.0012084 | 0.00030284 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_358-3_0_6_load_135 | 138 | 0.0014 | 0.00035087 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_358-3_0_6_load_119 | 139 | 0.0045857 | 0.0011493 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_358-3_0_6_load_134 | 140 | 0.0032085 | 0.00080412 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_358-3_0_6_load_133 | 141 | 0.0031004 | 0.00077704 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_358-3_0_6_load_121 | 142 | 0.0031726 | 0.00079513 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_358-3_0_6_load_122 | 143 | 0.0018656 | 0.00046756 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_358-3_0_6_load_123 | 144 | 0.002148 | 0.00053835 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_358-3_0_6_load_124 | 145 | 0.0079215 | 0.0019853 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_358-3_0_6_load_125 | 146 | 0.0016257 | 0.00040744 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_358-3_0_6_load_129 | 147 | 0.0054449 | 0.0013646 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_358-3_0_6_load_153 | 148 | 0.0020587 | 0.00051595 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_358-3_0_6_load_127 | 149 | 0.0027742 | 0.00069528 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_358-3_0_6_load_152 | 150 | 0.0028774 | 0.00072116 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_358-3_0_6_load_126 | 151 | 0.0028424 | 0.00071237 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_358-3_0_6_load_128 | 152 | 0.0035416 | 0.00088762 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_358-3_0_6_load_130 | 153 | 0.002903 | 0.00072755 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_358-3_0_6_load_132 | 154 | 0.0013928 | 0.00034908 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_358-3_0_6_load_131 | 155 | 0.0039851 | 0.00099876 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_358-3_0_6_load_148 | 156 | 0.0011389 | 0.00028544 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_358-3_0_6_load_149 | 157 | 0.0022141 | 0.00055491 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_358-3_0_6_load_154 | 158 | 0.0017398 | 0.00043602 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_358-3_0_6_load_163 | 160 | 0.0018702 | 0.00046871 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_358-3_0_6_load_160 | 161 | 0.0011818 | 0.00029618 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_358-3_0_6_load_157 | 162 | 0.0007378 | 0.00018491 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_358-3_0_6_load_158 | 163 | 0.0030479 | 0.00076388 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_358-3_0_6_load_159 | 164 | 0.0010681 | 0.00026768 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_358-3_0_6_line_0 |  | 0 | 1 | 0.021085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_358-3_0_6_line_1 |  | 0 | 2 | 0.0030166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_358-3_0_6_line_2 |  | 1 | 3 | 0.03378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_358-3_0_6_line_3 |  | 2 | 4 | 0.018062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_358-3_0_6_line_4 |  | 3 | 5 | 0.0095293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_358-3_0_6_line_5 |  | 4 | 6 | 0.044317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_358-3_0_6_line_6 |  | 6 | 7 | 0.0047417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_358-3_0_6_line_7 |  | 6 | 8 | 0.021385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_358-3_0_6_line_8 |  | 7 | 19 | 0.0077165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_358-3_0_6_line_9 |  | 8 | 20 | 0.0082019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_358-3_0_6_line_10 |  | 9 | 10 | 0.017446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_358-3_0_6_line_11 |  | 9 | 11 | 0.044557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_358-3_0_6_line_12 |  | 10 | 12 | 0.0017695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_358-3_0_6_line_13 |  | 11 | 13 | 0.043295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_358-3_0_6_line_14 |  | 12 | 14 | 0.018089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_358-3_0_6_line_15 |  | 14 | 15 | 0.0095487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_358-3_0_6_line_16 |  | 14 | 16 | 0.054043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_358-3_0_6_line_17 |  | 15 | 24 | 0.019504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_358-3_0_6_line_18 |  | 16 | 17 | 0.0053493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_358-3_0_6_line_19 |  | 17 | 18 | 0.0061023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_358-3_0_6_line_20 |  | 19 | 21 | 0.018027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_358-3_0_6_line_21 |  | 21 | 157 | 0.022433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_358-3_0_6_line_22 |  | 22 | 23 | 0.060772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_358-3_0_6_line_23 |  | 23 | 68 | 0.027262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_358-3_0_6_line_24 |  | 24 | 25 | 0.029419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_358-3_0_6_line_25 |  | 25 | 26 | 0.0040981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_358-3_0_6_line_26 |  | 26 | 119 | 0.023818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_358-3_0_6_line_27 |  | 27 | 28 | 0.0031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_358-3_0_6_line_28 |  | 27 | 29 | 0.0040996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_358-3_0_6_line_29 |  | 28 | 30 | 0.016295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_358-3_0_6_line_30 |  | 29 | 31 | 0.016707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_358-3_0_6_line_31 |  | 30 | 32 | 0.00039678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_358-3_0_6_line_32 |  | 31 | 33 | 0.0018055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_358-3_0_6_line_33 |  | 32 | 34 | 0.0075526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_358-3_0_6_line_34 |  | 33 | 35 | 0.0054737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_358-3_0_6_line_35 |  | 34 | 96 | 0.012423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_358-3_0_6_line_36 |  | 35 | 65 | 0.019678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_358-3_0_6_line_37 |  | 36 | 37 | 0.0091028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_358-3_0_6_line_38 |  | 36 | 38 | 0.023072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_358-3_0_6_line_39 |  | 37 | 39 | 0.0074369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_358-3_0_6_line_40 |  | 38 | 40 | 0.018171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_358-3_0_6_line_41 |  | 38 | 41 | 0.012236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_358-3_0_6_line_42 |  | 38 | 42 | 0.016415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_358-3_0_6_line_43 |  | 39 | 43 | 0.018375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_358-3_0_6_line_44 |  | 40 | 44 | 0.043668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_358-3_0_6_line_45 |  | 41 | 45 | 0.031413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_358-3_0_6_line_46 |  | 42 | 46 | 0.00025889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_358-3_0_6_line_47 |  | 43 | 47 | 0.014373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_358-3_0_6_line_48 |  | 44 | 48 | 0.0063033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_358-3_0_6_line_49 |  | 45 | 49 | 0.0093603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_358-3_0_6_line_50 |  | 46 | 50 | 0.011394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_358-3_0_6_line_51 |  | 47 | 79 | 0.045897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_358-3_0_6_line_52 |  | 48 | 81 | 0.001155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_358-3_0_6_line_53 |  | 49 | 138 | 0.002068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_358-3_0_6_line_54 |  | 50 | 89 | 0.0089889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_358-3_0_6_line_55 |  | 51 | 52 | 0.0064947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_358-3_0_6_line_56 |  | 51 | 53 | 0.020937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_358-3_0_6_line_57 |  | 52 | 54 | 0.014496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_358-3_0_6_line_58 |  | 53 | 55 | 0.029532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_358-3_0_6_line_59 |  | 53 | 56 | 0.035507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_358-3_0_6_line_60 |  | 54 | 59 | 0.033121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_358-3_0_6_line_61 |  | 56 | 60 | 0.020205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_358-3_0_6_line_62 |  | 57 | 58 | 0.03368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_358-3_0_6_line_63 |  | 58 | 71 | 0.019999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_358-3_0_6_line_64 |  | 59 | 62 | 0.007187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_358-3_0_6_line_65 |  | 60 | 61 | 0.014899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_358-3_0_6_line_66 |  | 61 | 80 | 0.012952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_358-3_0_6_line_67 |  | 62 | 93 | 0.031387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_358-3_0_6_line_68 |  | 62 | 94 | 0.015646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_358-3_0_6_line_69 |  | 63 | 64 | 0.022141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_358-3_0_6_line_70 |  | 63 | 65 | 0.0053921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_358-3_0_6_line_71 |  | 64 | 102 | 0.00028812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_358-3_0_6_line_72 |  | 66 | 67 | 0.041993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_358-3_0_6_line_73 |  | 66 | 68 | 0.018256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_358-3_0_6_line_74 |  | 67 | 69 | 0.024009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_358-3_0_6_line_75 |  | 67 | 70 | 0.005835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_358-3_0_6_line_76 |  | 68 | 71 | 0.009906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
77 | LV_358-3_0_6_line_77 |  | 69 | 72 | 0.011894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_358-3_0_6_line_78 |  | 70 | 73 | 0.033993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_358-3_0_6_line_79 |  | 70 | 74 | 0.012059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_358-3_0_6_line_80 |  | 71 | 75 | 0.006171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_358-3_0_6_line_81 |  | 73 | 76 | 0.0083234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_358-3_0_6_line_82 |  | 74 | 77 | 0.00046928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_358-3_0_6_line_83 |  | 75 | 78 | 0.016176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_358-3_0_6_line_84 |  | 76 | 116 | 0.0061296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_358-3_0_6_line_85 |  | 77 | 104 | 0.0067407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_358-3_0_6_line_86 |  | 78 | 80 | 0.021282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_358-3_0_6_line_87 |  | 81 | 82 | 0.0042017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_358-3_0_6_line_88 |  | 82 | 83 | 0.01468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_358-3_0_6_line_89 |  | 83 | 84 | 0.0057731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_358-3_0_6_line_90 |  | 84 | 118 | 0.018816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_358-3_0_6_line_91 |  | 85 | 86 | 0.025131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_358-3_0_6_line_92 |  | 85 | 87 | 0.022845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
93 | LV_358-3_0_6_line_93 |  | 86 | 88 | 0.012101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_358-3_0_6_line_94 |  | 87 | 89 | 0.0066929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_358-3_0_6_line_95 |  | 88 | 90 | 0.031413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_358-3_0_6_line_96 |  | 89 | 91 | 0.022209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_358-3_0_6_line_97 |  | 91 | 92 | 0.0033577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
98 | LV_358-3_0_6_line_98 |  | 92 | 109 | 0.0040512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_358-3_0_6_line_99 |  | 93 | 95 | 0.011668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_358-3_0_6_line_100 |  | 96 | 97 | 0.012323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_358-3_0_6_line_101 |  | 97 | 98 | 0.0071224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_358-3_0_6_line_102 |  | 99 | 100 | 0.011263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
103 | LV_358-3_0_6_line_103 |  | 99 | 101 | 0.0093744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_358-3_0_6_line_104 |  | 100 | 102 | 0.021298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_358-3_0_6_line_105 |  | 101 | 103 | 0.010265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_358-3_0_6_line_106 |  | 103 | 104 | 0.036298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_358-3_0_6_line_107 |  | 105 | 106 | 0.019371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_358-3_0_6_line_108 |  | 105 | 107 | 0.011777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
109 | LV_358-3_0_6_line_109 |  | 106 | 108 | 0.0037802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_358-3_0_6_line_110 |  | 107 | 109 | 0.035914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
111 | LV_358-3_0_6_line_111 |  | 108 | 110 | 0.019627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
112 | LV_358-3_0_6_line_112 |  | 110 | 111 | 0.0096506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_358-3_0_6_line_113 |  | 111 | 121 | 0.016041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_358-3_0_6_line_114 |  | 112 | 113 | 0.016986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_358-3_0_6_line_115 |  | 112 | 114 | 0.010654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_358-3_0_6_line_116 |  | 113 | 115 | 0.052266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
117 | LV_358-3_0_6_line_117 |  | 114 | 116 | 0.041973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
118 | LV_358-3_0_6_line_118 |  | 114 | 117 | 0.018615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_358-3_0_6_line_119 |  | 115 | 118 | 0.0075601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
120 | LV_358-3_0_6_line_120 |  | 117 | 119 | 0.017627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_358-3_0_6_line_121 |  | 119 | 120 | 0.014593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_358-3_0_6_line_122 |  | 120 | 156 | 0.030391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_358-3_0_6_line_123 |  | 121 | 122 | 2.5078e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_358-3_0_6_line_124 |  | 122 | 123 | 0.0016017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_358-3_0_6_line_125 |  | 123 | 124 | 0.025496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_358-3_0_6_line_126 |  | 124 | 159 | 0.012228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_358-3_0_6_line_127 |  | 125 | 126 | 0.011461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_358-3_0_6_line_128 |  | 126 | 127 | 0.02799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_358-3_0_6_line_129 |  | 126 | 128 | 0.018349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_358-3_0_6_line_130 |  | 127 | 129 | 0.010136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_358-3_0_6_line_131 |  | 128 | 130 | 0.011323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_358-3_0_6_line_132 |  | 129 | 131 | 0.016374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_358-3_0_6_line_133 |  | 131 | 139 | 0.015046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_358-3_0_6_line_134 |  | 132 | 133 | 0.0019289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_358-3_0_6_line_135 |  | 132 | 134 | 0.020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_358-3_0_6_line_136 |  | 133 | 135 | 0.023584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
137 | LV_358-3_0_6_line_137 |  | 134 | 136 | 0.00037089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_358-3_0_6_line_138 |  | 135 | 137 | 0.0078476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_358-3_0_6_line_139 |  | 137 | 138 | 0.012578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_358-3_0_6_line_140 |  | 139 | 140 | 0.014582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_358-3_0_6_line_141 |  | 140 | 141 | 0.0023787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_358-3_0_6_line_142 |  | 141 | 155 | 0.011104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_358-3_0_6_line_143 |  | 142 | 143 | 0.012635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_358-3_0_6_line_144 |  | 142 | 144 | 0.0049311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_358-3_0_6_line_145 |  | 143 | 145 | 0.013749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_358-3_0_6_line_146 |  | 144 | 146 | 0.0057197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_358-3_0_6_line_147 |  | 145 | 147 | 0.0075417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_358-3_0_6_line_148 |  | 146 | 148 | 0.0058087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_358-3_0_6_line_149 |  | 147 | 149 | 0.021621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_358-3_0_6_line_150 |  | 148 | 150 | 0.0050507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_358-3_0_6_line_151 |  | 149 | 151 | 0.00016446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_358-3_0_6_line_152 |  | 150 | 158 | 0.0012265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_358-3_0_6_line_153 |  | 151 | 152 | 0.0095625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_358-3_0_6_line_154 |  | 152 | 153 | 0.007337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_358-3_0_6_line_155 |  | 153 | 154 | 0.011306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_358-3_0_6_line_156 |  | 154 | 155 | 0.006015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_358-3_0_6_line_157 |  | 156 | 157 | 0.015666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_358-3_0_6_line_158 |  | 158 | 159 | 0.021472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_358-3_0_6_line_159 |  | 159 | 160 | 0.010811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_358-3_0_6_line_160 |  | 160 | 161 | 0.013622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_358-3_0_6_line_161 |  | 161 | 164 | 0.0039573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_358-3_0_6_line_162 |  | 162 | 163 | 0.017639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_358-3_0_6_line_163 |  | 163 | 164 | 0.0093418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_358-3_0_6_trafo_57 | 0.63 MVA 20/0.4 kV | 165 | 86 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2606534.289 | 1201168.0782 | 2606545.4276 | 1201164.583 | 2606547.6593 | 1201163.0847 | 2606549.1918 | 1201160.6405 | 2606549.9798 | 1201156.8838 | 2606549.9798 | 1201156.8838
1 | 2606531.4108 | 1201168.9813 | 2606534.289 | 1201168.0782
2 | 2606548.6817 | 1201123.274 | 2606547.8368 | 1201132.7352 | 2606548.3325 | 1201145.8872 | 2606549.9798 | 1201156.8838
3 | 2606531.4108 | 1201168.9813 | 2606545.9924 | 1201170.1422 | 2606549.3856 | 1201170.6712
4 | 2606548.6817 | 1201123.274 | 2606549.0003 | 1201119.7072 | 2606546.9889 | 1201114.5467 | 2606546.5945 | 1201114.4357
5 | 2606592.3307 | 1201175.4288 | 2606578.8026 | 1201178.3712 | 2606576.0172 | 1201178.068 | 2606553.2446 | 1201171.2729 | 2606549.3856 | 1201170.6712
6 | 2606592.3307 | 1201175.4288 | 2606592.9149 | 1201170.7232
7 | 2606592.3307 | 1201175.4288 | 2606597.1645 | 1201196.2603
8 | 2606593.8656 | 1201163.0656 | 2606592.9149 | 1201170.7232
9 | 2606599.0185 | 1201204.25 | 2606597.1645 | 1201196.2603
10 | 2606529.2695 | 1201016.8055 | 2606532.3937 | 1201013.2874 | 2606543.5534 | 1201007.1405
11 | 2606529.2695 | 1201016.8055 | 2606527.768 | 1201018.4963 | 2606526.2391 | 1201024.6758 | 2606524.7595 | 1201034.4572 | 2606521.7748 | 1201049.5399 | 2606519.7495 | 1201060.0082
12 | 2606543.5534 | 1201007.1405 | 2606545.1034 | 1201006.2868
13 | 2606504.0045 | 1201100.157 | 2606509.4939 | 1201088.4698 | 2606516.8337 | 1201071.9689 | 2606518.6826 | 1201065.5229 | 2606519.7495 | 1201060.0082
14 | 2606561.2255 | 1200998.3295 | 2606558.6609 | 1200998.8192 | 2606545.1034 | 1201006.2868
15 | 2606561.2255 | 1200998.3295 | 2606564.5076 | 1200997.7027 | 2606570.695 | 1200998.1986 | 2606570.695 | 1200998.1986
16 | 2606561.2255 | 1200998.3295 | 2606531.2788 | 1200953.3428
17 | 2606579.1852 | 1201015.362 | 2606578.7762 | 1201014.1049 | 2606575.1878 | 1201003.3063 | 2606570.695 | 1200998.1986
18 | 2606531.2788 | 1200953.3428 | 2606526.0268 | 1200954.3585
19 | 2606520.0355 | 1200955.5171 | 2606526.0268 | 1200954.3585
20 | 2606593.8656 | 1201163.0656 | 2606596.0865 | 1201145.1761
21 | 2606598.8503 | 1201122.9138 | 2606596.0865 | 1201145.1761
22 | 2606580.6956 | 1200908.1833 | 2606575.7628 | 1200887.7558 | 2606574.073 | 1200880.7613 | 2606604.8885 | 1200869.9891
23 | 2606612.4866 | 1200896.1448 | 2606610.9947 | 1200889.2395 | 2606606.7702 | 1200875.4163 | 2606604.8885 | 1200869.9891
24 | 2606579.1852 | 1201015.362 | 2606585.4745 | 1201034.6899 | 2606589.9783 | 1201042.5898
25 | 2606592.008 | 1201046.15 | 2606589.9783 | 1201042.5898
26 | 2606608.163 | 1201063.1745 | 2606601.995 | 1201058.8321 | 2606595.4186 | 1201052.1324 | 2606592.008 | 1201046.15
27 | 2606804.128 | 1200916.4887 | 2606807.1718 | 1200915.9016
28 | 2606804.128 | 1200916.4887 | 2606800.1026 | 1200917.2652
29 | 2606807.1718 | 1200915.9016 | 2606823.1717 | 1200912.8151
30 | 2606783.6977 | 1200920.4298 | 2606800.1026 | 1200917.2652
31 | 2606823.1717 | 1200912.8151 | 2606823.5613 | 1200912.74
32 | 2606783.6977 | 1200920.4298 | 2606781.9249 | 1200920.7718
33 | 2606830.9772 | 1200911.3094 | 2606823.5613 | 1200912.74
34 | 2606781.9249 | 1200920.7718 | 2606776.5503 | 1200921.8086
35 | 2606830.9772 | 1200911.3094 | 2606843.1758 | 1200908.9562
36 | 2606776.5503 | 1200921.8086 | 2606769.968 | 1200923.0784 | 2606756.9971 | 1200923.3843
37 | 2606806.4036 | 1201000.3093 | 2606813.7683 | 1200994.9592
38 | 2606787.7374 | 1201013.8694 | 2606806.4036 | 1201000.3093
39 | 2606819.7851 | 1200990.5882 | 2606813.7683 | 1200994.9592
40 | 2606787.7374 | 1201013.8694 | 2606781.7417 | 1201012.1062 | 2606774.5516 | 1201009.7635 | 2606770.4445 | 1201008.3026
41 | 2606787.7374 | 1201013.8694 | 2606799.809 | 1201011.8714
42 | 2606787.7374 | 1201013.8694 | 2606788.5104 | 1201016.9164 | 2606788.6114 | 1201021.7969 | 2606787.9896 | 1201026.4765 | 2606786.0807 | 1201029.6105
43 | 2606819.7851 | 1200990.5882 | 2606827.1127 | 1200985.2651 | 2606835.9225 | 1200982.2289
44 | 2606731.2135 | 1200989.2273 | 2606752.5586 | 1200999.6668 | 2606765.2087 | 1201006.4401 | 2606770.4445 | 1201008.3026
45 | 2606799.809 | 1201011.8714 | 2606813.3543 | 1201009.6294 | 2606830.6715 | 1201006.0503
46 | 2606786.0807 | 1201029.6105 | 2606785.946 | 1201029.8316
47 | 2606835.9225 | 1200982.2289 | 2606849.5115 | 1200977.5457
48 | 2606725.5511 | 1200986.4579 | 2606731.2135 | 1200989.2273
49 | 2606839.838 | 1201004.1557 | 2606830.6715 | 1201006.0503
50 | 2606776.3123 | 1201035.8331 | 2606779.0981 | 1201034.6154 | 2606785.946 | 1201029.8316 | 2606785.946 | 1201029.8316
51 | 2606894.0901 | 1200967.4317 | 2606867.1413 | 1200971.4698 | 2606849.5115 | 1200977.5457
52 | 2606725.5511 | 1200986.4579 | 2606724.5135 | 1200985.9505
53 | 2606841.8632 | 1201003.7372 | 2606839.838 | 1201004.1557
54 | 2606767.7844 | 1201037.6265 | 2606771.4374 | 1201037.9641 | 2606776.3123 | 1201035.8331
55 | 2606703.9741 | 1200859.3589 | 2606702.2161 | 1200856.856 | 2606700.9265 | 1200853.671
56 | 2606717.8681 | 1200874.8831 | 2606714.7654 | 1200872.3894 | 2606708.0145 | 1200865.1113 | 2606703.9741 | 1200859.3589
57 | 2606700.9265 | 1200853.671 | 2606698.861 | 1200848.57 | 2606696.7014 | 1200839.8407 | 2606696.7014 | 1200839.8407
58 | 2606717.8681 | 1200874.8831 | 2606724.9507 | 1200878.2483 | 2606732.6127 | 1200880.7138 | 2606744.2652 | 1200881.3271 | 2606746.2365 | 1200881.2354
59 | 2606703.848 | 1200895.1784 | 2606704.707 | 1200896.1466 | 2606722.167 | 1200889.9738 | 2606722.0852 | 1200888.2394 | 2606717.8681 | 1200874.8831
60 | 2606695.9009 | 1200806.7553 | 2606695.9118 | 1200831.1685 | 2606696.7014 | 1200839.8407
61 | 2606688.8506 | 1200908.7186 | 2606703.848 | 1200895.1784
62 | 2606670.488 | 1200882.3061 | 2606659.7673 | 1200883.8902 | 2606643.4204 | 1200895.3562 | 2606640.6291 | 1200896.0492
63 | 2606621.2193 | 1200900.8681 | 2606640.6291 | 1200896.0492
64 | 2606703.1091 | 1200806.7077 | 2606695.9009 | 1200806.7553
65 | 2606688.8506 | 1200908.7186 | 2606674.4783 | 1200912.6435
66 | 2606661.8488 | 1200915.1204 | 2606661.8488 | 1200915.1204 | 2606665.6774 | 1200915.0469 | 2606674.4783 | 1200912.6435
67 | 2606703.1091 | 1200806.7077 | 2606705.789 | 1200806.1438 | 2606709.0353 | 1200802.7344 | 2606710.6678 | 1200799.4789 | 2606713.4291 | 1200794.1903 | 2606715.5787 | 1200791.3356 | 2606720.0734 | 1200787.8831 | 2606724.1566 | 1200784.8416
68 | 2606703.1091 | 1200806.7077 | 2606704.2271 | 1200822.3139
69 | 2606729.472 | 1200924.0337 | 2606751.6065 | 1200923.5115
70 | 2606751.6065 | 1200923.5115 | 2606756.9971 | 1200923.3843
71 | 2606729.1839 | 1200924.0404 | 2606729.472 | 1200924.0337
72 | 2606628.3232 | 1200954.1379 | 2606618.7705 | 1200926.7349 | 2606616.191 | 1200914.021
73 | 2606612.4866 | 1200896.1448 | 2606614.4705 | 1200905.541 | 2606616.191 | 1200914.021
74 | 2606628.3232 | 1200954.1379 | 2606621.9173 | 1200958.3887 | 2606616.0782 | 1200959.494 | 2606605.7142 | 1200960.0421
75 | 2606629.9078 | 1200959.7538 | 2606628.3232 | 1200954.1379
76 | 2606621.2193 | 1200900.8681 | 2606612.4866 | 1200896.1448
77 | 2606593.8365 | 1200960.6703 | 2606605.7142 | 1200960.0421
78 | 2606629.9078 | 1200959.7538 | 2606632.0482 | 1200965.1924 | 2606633.1378 | 1200971.0634 | 2606633.4004 | 1200974.5656 | 2606633.3272 | 1200978.79 | 2606631.6387 | 1200993.1313
79 | 2606629.9078 | 1200959.7538 | 2606641.5938 | 1200956.777
80 | 2606621.2193 | 1200900.8681 | 2606626.7193 | 1200903.6978
81 | 2606630.6655 | 1201001.3976 | 2606631.6387 | 1200993.1313
82 | 2606641.5938 | 1200956.777 | 2606642.0485 | 1200956.6612
83 | 2606626.7193 | 1200903.6978 | 2606634.7369 | 1200908.1757 | 2606641.6186 | 1200909.4188
84 | 2606630.6655 | 1201001.3976 | 2606630.2386 | 1201005.023 | 2606630.0947 | 1201007.4979
85 | 2606648.4718 | 1200954.7328 | 2606647.594 | 1200955.2486 | 2606642.0485 | 1200956.6612
86 | 2606661.8488 | 1200915.1204 | 2606656.8437 | 1200912.1689 | 2606641.6186 | 1200909.4188
87 | 2606724.5135 | 1200985.9505 | 2606721.4148 | 1200984.4349 | 2606720.7031 | 1200984.1914
88 | 2606720.7031 | 1200984.1914 | 2606712.2542 | 1200981.3008 | 2606706.5342 | 1200980.7159
89 | 2606706.5342 | 1200980.7159 | 2606702.802 | 1200980.3342 | 2606700.7875 | 1200980.5021
90 | 2606682.5056 | 1200984.425 | 2606682.5056 | 1200984.425 | 2606692.6627 | 1200981.179 | 2606700.7875 | 1200980.5021
91 | 2606740.79 | 1201025.6849 | 2606729.0234 | 1201020.9964 | 2606718.5144 | 1201019.0615 | 2606716.7404 | 1201018.9306
92 | 2606740.79 | 1201025.6849 | 2606747.7693 | 1201028.4658 | 2606761.822 | 1201034.597
93 | 2606705.0525 | 1201020.6234 | 2606706.1603 | 1201019.8593 | 2606711.4745 | 1201018.5422 | 2606716.7404 | 1201018.9306
94 | 2606767.7844 | 1201037.6265 | 2606763.6844 | 1201035.4096 | 2606761.822 | 1201034.597
95 | 2606705.0525 | 1201020.6234 | 2606701.1559 | 1201023.3111 | 2606699.4941 | 1201025.566 | 2606697.5473 | 1201030.8556 | 2606695.6974 | 1201038.0797 | 2606694.4722 | 1201044.693 | 2606694.364 | 1201048.7499
96 | 2606767.7844 | 1201037.6265 | 2606763.8002 | 1201040.6792 | 2606758.4455 | 1201044.2085 | 2606749.4318 | 1201050.1157
97 | 2606749.4318 | 1201050.1157 | 2606746.6234 | 1201051.9562
98 | 2606746.6234 | 1201051.9562 | 2606743.235 | 1201054.1769
99 | 2606724.1566 | 1200784.8416 | 2606727.0096 | 1200786.0565 | 2606728.9489 | 1200787.5929 | 2606731.2906 | 1200789.9301 | 2606732.2087 | 1200792.577
100 | 2606855.2757 | 1200906.6221 | 2606843.1758 | 1200908.9562
101 | 2606862.2692 | 1200905.273 | 2606855.2757 | 1200906.6221
102 | 2606697.297 | 1200927.6639 | 2606703.8229 | 1200924.6387 | 2606707.8921 | 1200924.5427
103 | 2606697.297 | 1200927.6639 | 2606688.7921 | 1200931.6065
104 | 2606707.8921 | 1200924.5427 | 2606729.1839 | 1200924.0404
105 | 2606679.4786 | 1200935.9238 | 2606688.7921 | 1200931.6065
106 | 2606648.4718 | 1200954.7328 | 2606656.7717 | 1200949.8558 | 2606675.9508 | 1200937.5592 | 2606679.4786 | 1200935.9238
107 | 2606718.2957 | 1201093.823 | 2606717.2764 | 1201098.6474 | 2606716.2484 | 1201105.9724 | 2606716.4912 | 1201113.0112
108 | 2606722.4985 | 1201082.8539 | 2606721.0659 | 1201085.8336 | 2606718.6078 | 1201092.3455 | 2606718.2957 | 1201093.823
109 | 2606716.842 | 1201116.7707 | 2606716.5433 | 1201114.5218 | 2606716.4912 | 1201113.0112
110 | 2606722.4985 | 1201082.8539 | 2606725.4677 | 1201076.678 | 2606733.9551 | 1201062.3353 | 2606740.6983 | 1201055.8393 | 2606743.235 | 1201054.1769
111 | 2606716.842 | 1201116.7707 | 2606717.9623 | 1201125.2069 | 2606719.9281 | 1201136.1487
112 | 2606722.3149 | 1201145.4947 | 2606720.1938 | 1201137.6272 | 2606719.9281 | 1201136.1487
113 | 2606726.8618 | 1201160.8743 | 2606723.9534 | 1201151.5722 | 2606722.3149 | 1201145.4947
114 | 2606648.6316 | 1201049.7339 | 2606652.5151 | 1201048.104 | 2606655.5782 | 1201045.0613 | 2606657.3179 | 1201041.1945 | 2606658.2725 | 1201037.0877
115 | 2606638.1448 | 1201048.3327 | 2606643.0146 | 1201049.6166 | 2606648.6316 | 1201049.7339
116 | 2606676.5562 | 1200989.0877 | 2606671.3511 | 1200994.8072 | 2606666.752 | 1201003.3512 | 2606662.2451 | 1201017.9985 | 2606661.1114 | 1201024.6119 | 2606658.855 | 1201034.5815 | 2606658.2725 | 1201037.0877
117 | 2606638.1448 | 1201048.3327 | 2606638.1255 | 1201045.1421 | 2606637.5885 | 1201042.0399 | 2606632.2482 | 1201025.5807 | 2606630.4979 | 1201018.4305 | 2606629.8585 | 1201011.5594 | 2606630.0947 | 1201007.4979
118 | 2606638.1448 | 1201048.3327 | 2606636.4356 | 1201052.2552 | 2606633.9812 | 1201055.4431 | 2606628.9913 | 1201059.5621 | 2606625.408 | 1201060.95
119 | 2606682.5056 | 1200984.425 | 2606676.6169 | 1200989.021 | 2606676.5562 | 1200989.0877
120 | 2606608.163 | 1201063.1745 | 2606616.4437 | 1201063.4949 | 2606622.3515 | 1201062.1339 | 2606625.408 | 1201060.95
121 | 2606608.163 | 1201063.1745 | 2606605.3079 | 1201070.8978 | 2606604.5245 | 1201077.2078
122 | 2606604.5245 | 1201077.2078 | 2606600.7803 | 1201107.3673
123 | 2606726.8693 | 1201160.8983 | 2606726.8618 | 1201160.8743
124 | 2606727.3473 | 1201162.427 | 2606726.8693 | 1201160.8983
125 | 2606727.3473 | 1201162.427 | 2606729.649 | 1201169.7884 | 2606734.7319 | 1201184.6465 | 2606735.5295 | 1201186.5669
126 | 2606740.2199 | 1201197.8598 | 2606735.5295 | 1201186.5669
127 | 2606916.3521 | 1201048.1895 | 2606926.2975 | 1201042.4929
128 | 2606916.3521 | 1201048.1895 | 2606892.7728 | 1201063.2703
129 | 2606916.3521 | 1201048.1895 | 2606921.7643 | 1201054.3657 | 2606925.1018 | 1201057.6602 | 2606930.1839 | 1201059.6227
130 | 2606884.2343 | 1201068.7314 | 2606892.7728 | 1201063.2703
131 | 2606941.2714 | 1201057.7633 | 2606936.5169 | 1201059.2409 | 2606930.1839 | 1201059.6227 | 2606930.1839 | 1201059.6227
132 | 2606870.9397 | 1201078.2437 | 2606876.6532 | 1201073.5801 | 2606884.2343 | 1201068.7314
133 | 2606870.9397 | 1201078.2437 | 2606859.2837 | 1201087.758
134 | 2606887.4031 | 1200997.7317 | 2606885.489 | 1200997.9703
135 | 2606907.3206 | 1200995.2485 | 2606887.4031 | 1200997.7317
136 | 2606885.489 | 1200997.9703 | 2606878.3216 | 1200998.8639 | 2606862.0989 | 1201000.9871
137 | 2606907.6886 | 1200995.2026 | 2606907.3206 | 1200995.2485
138 | 2606854.3176 | 1201002.0055 | 2606862.0989 | 1201000.9871
139 | 2606841.8632 | 1201003.7372 | 2606843.2053 | 1201003.4598 | 2606854.3176 | 1201002.0055
140 | 2606859.2837 | 1201087.758 | 2606848.2141 | 1201096.7936 | 2606847.9975 | 1201096.9911
141 | 2606846.2401 | 1201098.5943 | 2606847.9975 | 1201096.9911
142 | 2606846.2401 | 1201098.5943 | 2606838.0369 | 1201106.0774
143 | 2606781.8243 | 1201159.1265 | 2606772.6333 | 1201167.7967
144 | 2606769.0463 | 1201171.1804 | 2606772.6333 | 1201167.7967
145 | 2606781.8243 | 1201159.1265 | 2606791.8258 | 1201149.6918
146 | 2606769.0463 | 1201171.1804 | 2606768.4254 | 1201171.7662 | 2606764.8535 | 1201175.0707
147 | 2606791.8258 | 1201149.6918 | 2606796.8755 | 1201144.9281 | 2606797.3082 | 1201144.513
148 | 2606760.5895 | 1201179.0153 | 2606764.8535 | 1201175.0707
149 | 2606812.91 | 1201129.5453 | 2606797.3082 | 1201144.513
150 | 2606760.5895 | 1201179.0153 | 2606756.8821 | 1201182.4452
151 | 2606813.0287 | 1201129.4314 | 2606812.91 | 1201129.5453
152 | 2606755.9818 | 1201183.2781 | 2606756.8821 | 1201182.4452
153 | 2606819.9291 | 1201122.8114 | 2606813.0287 | 1201129.4314
154 | 2606825.2407 | 1201117.7504 | 2606824.5036 | 1201118.4228 | 2606819.9291 | 1201122.8114
155 | 2606833.5931 | 1201110.1312 | 2606825.2407 | 1201117.7504
156 | 2606833.5931 | 1201110.1312 | 2606838.0369 | 1201106.0774
157 | 2606600.7803 | 1201107.3673 | 2606598.8503 | 1201122.9138
158 | 2606740.2199 | 1201197.8598 | 2606755.9818 | 1201183.2781
159 | 2606740.2199 | 1201197.8598 | 2606744.3233 | 1201207.8613
160 | 2606749.494 | 1201220.4643 | 2606744.3233 | 1201207.8613
161 | 2606750.9961 | 1201224.1255 | 2606749.494 | 1201220.4643
162 | 2606761.2782 | 1201249.0701 | 2606754.5561 | 1201232.7624
163 | 2606754.5561 | 1201232.7624 | 2606751.0438 | 1201224.2417 | 2606750.9961 | 1201224.1255

## bus_geodata
| x | y | coords
0 | 2606534.289 | 1201168.0782
1 | 2606549.9798 | 1201156.8838
2 | 2606531.4108 | 1201168.9813
3 | 2606548.6817 | 1201123.274
4 | 2606549.3856 | 1201170.6712
5 | 2606546.5945 | 1201114.4357
6 | 2606592.3307 | 1201175.4288
7 | 2606592.9149 | 1201170.7232
8 | 2606597.1645 | 1201196.2603
9 | 2606529.2695 | 1201016.8055
10 | 2606543.5534 | 1201007.1405
11 | 2606519.7495 | 1201060.0082
12 | 2606545.1034 | 1201006.2868
13 | 2606504.0045 | 1201100.157
14 | 2606561.2255 | 1200998.3295
15 | 2606570.695 | 1200998.1986
16 | 2606531.2788 | 1200953.3428
17 | 2606526.0268 | 1200954.3585
18 | 2606520.0355 | 1200955.5171
19 | 2606593.8656 | 1201163.0656
20 | 2606599.0185 | 1201204.25
21 | 2606596.0865 | 1201145.1761
22 | 2606580.6956 | 1200908.1833
23 | 2606604.8885 | 1200869.9891
24 | 2606579.1852 | 1201015.362
25 | 2606589.9783 | 1201042.5898
26 | 2606592.008 | 1201046.15
27 | 2606804.128 | 1200916.4887
28 | 2606807.1718 | 1200915.9016
29 | 2606800.1026 | 1200917.2652
30 | 2606823.1717 | 1200912.8151
31 | 2606783.6977 | 1200920.4298
32 | 2606823.5613 | 1200912.74
33 | 2606781.9249 | 1200920.7718
34 | 2606830.9772 | 1200911.3094
35 | 2606776.5503 | 1200921.8086
36 | 2606806.4036 | 1201000.3093
37 | 2606813.7683 | 1200994.9592
38 | 2606787.7374 | 1201013.8694
39 | 2606819.7851 | 1200990.5882
40 | 2606770.4445 | 1201008.3026
41 | 2606799.809 | 1201011.8714
42 | 2606786.0807 | 1201029.6105
43 | 2606835.9225 | 1200982.2289
44 | 2606731.2135 | 1200989.2273
45 | 2606830.6715 | 1201006.0503
46 | 2606785.946 | 1201029.8316
47 | 2606849.5115 | 1200977.5457
48 | 2606725.5511 | 1200986.4579
49 | 2606839.8381 | 1201004.1557
50 | 2606776.3123 | 1201035.8331
51 | 2606703.9741 | 1200859.3589
52 | 2606700.9265 | 1200853.671
53 | 2606717.8681 | 1200874.8831
54 | 2606696.7014 | 1200839.8407
55 | 2606746.2365 | 1200881.2354
56 | 2606703.848 | 1200895.1784
57 | 2606670.488 | 1200882.3061
58 | 2606640.6291 | 1200896.0492
59 | 2606695.9009 | 1200806.7553
60 | 2606688.8506 | 1200908.7186
61 | 2606674.4783 | 1200912.6435
62 | 2606703.1091 | 1200806.7077
63 | 2606751.6065 | 1200923.5115
64 | 2606729.472 | 1200924.0337
65 | 2606756.9971 | 1200923.3843
66 | 2606616.191 | 1200914.021
67 | 2606628.3232 | 1200954.1379
68 | 2606612.4866 | 1200896.1448
69 | 2606605.7142 | 1200960.0421
70 | 2606629.9078 | 1200959.7538
71 | 2606621.2193 | 1200900.8681
72 | 2606593.8365 | 1200960.6703
73 | 2606631.6387 | 1200993.1313
74 | 2606641.5938 | 1200956.777
75 | 2606626.7193 | 1200903.6978
76 | 2606630.6655 | 1201001.3976
77 | 2606642.0485 | 1200956.6612
78 | 2606641.6186 | 1200909.4188
79 | 2606894.0901 | 1200967.4317
80 | 2606661.8488 | 1200915.1204
81 | 2606724.5135 | 1200985.9505
82 | 2606720.7031 | 1200984.1914
83 | 2606706.5342 | 1200980.7159
84 | 2606700.7875 | 1200980.5021
85 | 2606740.79 | 1201025.6849
86 | 2606716.7404 | 1201018.9306
87 | 2606761.822 | 1201034.597
88 | 2606705.0525 | 1201020.6234
89 | 2606767.7844 | 1201037.6265
90 | 2606694.364 | 1201048.7499
91 | 2606749.4318 | 1201050.1157
92 | 2606746.6234 | 1201051.9562
93 | 2606724.1566 | 1200784.8416
94 | 2606704.2271 | 1200822.3139
95 | 2606732.2087 | 1200792.577
96 | 2606843.1758 | 1200908.9562
97 | 2606855.2757 | 1200906.6221
98 | 2606862.2692 | 1200905.273
99 | 2606697.297 | 1200927.6639
100 | 2606707.8921 | 1200924.5427
101 | 2606688.7921 | 1200931.6065
102 | 2606729.1839 | 1200924.0404
103 | 2606679.4786 | 1200935.9238
104 | 2606648.4718 | 1200954.7328
105 | 2606718.2957 | 1201093.823
106 | 2606716.4912 | 1201113.0112
107 | 2606722.4985 | 1201082.8539
108 | 2606716.842 | 1201116.7707
109 | 2606743.235 | 1201054.1769
110 | 2606719.9281 | 1201136.1487
111 | 2606722.3148 | 1201145.4947
112 | 2606648.6316 | 1201049.7339
113 | 2606658.2725 | 1201037.0877
114 | 2606638.1448 | 1201048.3327
115 | 2606676.5562 | 1200989.0877
116 | 2606630.0947 | 1201007.4979
117 | 2606625.408 | 1201060.95
118 | 2606682.5056 | 1200984.425
119 | 2606608.163 | 1201063.1745
120 | 2606604.5245 | 1201077.2078
121 | 2606726.8618 | 1201160.8743
122 | 2606726.8693 | 1201160.8983
123 | 2606727.3473 | 1201162.427
124 | 2606735.5295 | 1201186.5669
125 | 2606926.2975 | 1201042.4929
126 | 2606916.3521 | 1201048.1895
127 | 2606892.7728 | 1201063.2703
128 | 2606930.1839 | 1201059.6227
129 | 2606884.2343 | 1201068.7314
130 | 2606941.2714 | 1201057.7633
131 | 2606870.9397 | 1201078.2437
132 | 2606887.4031 | 1200997.7317
133 | 2606885.489 | 1200997.9703
134 | 2606907.3206 | 1200995.2485
135 | 2606862.0989 | 1201000.9871
136 | 2606907.6886 | 1200995.2026
137 | 2606854.3176 | 1201002.0055
138 | 2606841.8632 | 1201003.7372
139 | 2606859.2837 | 1201087.758
140 | 2606847.9975 | 1201096.9911
141 | 2606846.2401 | 1201098.5943
142 | 2606772.6333 | 1201167.7967
143 | 2606781.8243 | 1201159.1265
144 | 2606769.0463 | 1201171.1804
145 | 2606791.8258 | 1201149.6918
146 | 2606764.8535 | 1201175.0707
147 | 2606797.3082 | 1201144.513
148 | 2606760.5895 | 1201179.0153
149 | 2606812.91 | 1201129.5453
150 | 2606756.8821 | 1201182.4452
151 | 2606813.0287 | 1201129.4314
152 | 2606819.9291 | 1201122.8114
153 | 2606825.2407 | 1201117.7504
154 | 2606833.5931 | 1201110.1312
155 | 2606838.0369 | 1201106.0774
156 | 2606600.7803 | 1201107.3673
157 | 2606598.8503 | 1201122.9138
158 | 2606755.9818 | 1201183.2781
159 | 2606740.2199 | 1201197.8598
160 | 2606744.3233 | 1201207.8613
161 | 2606749.494 | 1201220.4643
162 | 2606761.2782 | 1201249.0701
163 | 2606754.5561 | 1201232.7624
164 | 2606750.9961 | 1201224.1255
165 | 2606694.1466 | 1201056.8992

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1