## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_359-7_1_3_node_20 | 0.4 | n |  | TRUE
1 | bus_LV_359-7_1_3_node_21 | 0.4 | n |  | TRUE
2 | bus_LV_359-7_1_3_node_22 | 0.4 | n |  | TRUE
3 | bus_LV_359-7_1_3_node_23 | 0.4 | n |  | TRUE
4 | bus_LV_359-7_1_3_node_24 | 0.4 | n |  | TRUE
5 | bus_LV_359-7_1_3_node_40 | 0.4 | n |  | TRUE
6 | bus_LV_359-7_1_3_node_30 | 0.4 | n |  | TRUE
7 | bus_LV_359-7_1_3_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_359-7_1_3_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_359-7_1_3_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_359-7_1_3_node_26 | 0.4 | n |  | TRUE
11 | bus_LV_359-7_1_3_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_359-7_1_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_359-7_1_3_node_39 | 0.4 | n |  | TRUE
14 | bus_LV_359-7_1_3_node_152 | 0.4 | n |  | TRUE
15 | bus_LV_359-7_1_3_node_151 | 0.4 | n |  | TRUE
16 | bus_LV_359-7_1_3_node_38 | 0.4 | n |  | TRUE
17 | bus_LV_359-7_1_3_node_46 | 0.4 | n |  | TRUE
18 | bus_LV_359-7_1_3_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_359-7_1_3_node_153 | 0.4 | n |  | TRUE
20 | bus_LV_359-7_1_3_node_150 | 0.4 | n |  | TRUE
21 | bus_LV_359-7_1_3_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_359-7_1_3_node_44 | 0.4 | n |  | TRUE
23 | bus_LV_359-7_1_3_node_42 | 0.4 | n |  | TRUE
24 | bus_LV_359-7_1_3_node_47 | 0.4 | n |  | TRUE
25 | bus_LV_359-7_1_3_node_142 | 0.4 | n |  | TRUE
26 | bus_LV_359-7_1_3_node_143 | 0.4 | n |  | TRUE
27 | bus_LV_359-7_1_3_node_48 | 0.4 | n |  | TRUE
28 | bus_LV_359-7_1_3_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_359-7_1_3_node_50 | 0.4 | n |  | TRUE
30 | bus_LV_359-7_1_3_node_51 | 0.4 | n |  | TRUE
31 | bus_LV_359-7_1_3_node_52 | 0.4 | n |  | TRUE
32 | bus_LV_359-7_1_3_node_56 | 0.4 | n |  | TRUE
33 | bus_LV_359-7_1_3_node_155 | 0.4 | n |  | TRUE
34 | bus_LV_359-7_1_3_node_54 | 0.4 | n |  | TRUE
35 | bus_LV_359-7_1_3_node_53 | 0.4 | n |  | TRUE
36 | bus_LV_359-7_1_3_node_55 | 0.4 | n |  | TRUE
37 | bus_LV_359-7_1_3_node_58 | 0.4 | n |  | TRUE
38 | bus_LV_359-7_1_3_node_57 | 0.4 | n |  | TRUE
39 | bus_LV_359-7_1_3_node_61 | 0.4 | n |  | TRUE
40 | bus_LV_359-7_1_3_node_62 | 0.4 | n |  | TRUE
41 | bus_LV_359-7_1_3_node_59 | 0.4 | n |  | TRUE
42 | bus_LV_359-7_1_3_node_60 | 0.4 | n |  | TRUE
43 | bus_LV_359-7_1_3_node_160 | 0.4 | n |  | TRUE
44 | bus_LV_359-7_1_3_node_66 | 0.4 | n |  | TRUE
45 | bus_LV_359-7_1_3_node_102 | 0.4 | n |  | TRUE
46 | bus_LV_359-7_1_3_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_359-7_1_3_node_120 | 0.4 | n |  | TRUE
48 | bus_LV_359-7_1_3_node_119 | 0.4 | n |  | TRUE
49 | bus_LV_359-7_1_3_node_100 | 0.4 | n |  | TRUE
50 | bus_LV_359-7_1_3_node_63 | 0.4 | n |  | TRUE
51 | bus_LV_359-7_1_3_node_65 | 0.4 | n |  | TRUE
52 | bus_LV_359-7_1_3_node_96 | 0.4 | n |  | TRUE
53 | bus_LV_359-7_1_3_node_97 | 0.4 | n |  | TRUE
54 | bus_LV_359-7_1_3_node_98 | 0.4 | n |  | TRUE
55 | bus_LV_359-7_1_3_node_99 | 0.4 | n |  | TRUE
56 | bus_LV_359-7_1_3_node_121 | 0.4 | n |  | TRUE
57 | bus_LV_359-7_1_3_node_117 | 0.4 | n |  | TRUE
58 | bus_LV_359-7_1_3_node_104 | 0.4 | n |  | TRUE
59 | bus_LV_359-7_1_3_node_105 | 0.4 | n |  | TRUE
60 | bus_LV_359-7_1_3_node_106 | 0.4 | n |  | TRUE
61 | bus_LV_359-7_1_3_node_107 | 0.4 | n |  | TRUE
62 | bus_LV_359-7_1_3_node_108 | 0.4 | n |  | TRUE
63 | bus_LV_359-7_1_3_node_109 | 0.4 | n |  | TRUE
64 | bus_LV_359-7_1_3_node_110 | 0.4 | n |  | TRUE
65 | bus_LV_359-7_1_3_node_112 | 0.4 | n |  | TRUE
66 | bus_LV_359-7_1_3_node_111 | 0.4 | n |  | TRUE
67 | bus_LV_359-7_1_3_node_113 | 0.4 | n |  | TRUE
68 | bus_LV_359-7_1_3_node_114 | 0.4 | n |  | TRUE
69 | bus_LV_359-7_1_3_node_144 | 0.4 | n |  | TRUE
70 | bus_LV_359-7_1_3_node_145 | 0.4 | n |  | TRUE
71 | bus_LV_359-7_1_3_node_115 | 0.4 | n |  | TRUE
72 | bus_LV_359-7_1_3_node_116 | 0.4 | n |  | TRUE
73 | bus_LV_359-7_1_3_node_118 | 0.4 | n |  | TRUE
74 | bus_LV_359-7_1_3_node_128 | 0.4 | n |  | TRUE
75 | bus_LV_359-7_1_3_node_131 | 0.4 | n |  | TRUE
76 | bus_LV_359-7_1_3_node_122 | 0.4 | n |  | TRUE
77 | bus_LV_359-7_1_3_node_123 | 0.4 | n |  | TRUE
78 | bus_LV_359-7_1_3_node_124 | 0.4 | n |  | TRUE
79 | bus_LV_359-7_1_3_node_125 | 0.4 | n |  | TRUE
80 | bus_LV_359-7_1_3_node_126 | 0.4 | n |  | TRUE
81 | bus_LV_359-7_1_3_node_127 | 0.4 | n |  | TRUE
82 | bus_LV_359-7_1_3_node_133 | 0.4 | n |  | TRUE
83 | bus_LV_359-7_1_3_node_129 | 0.4 | n |  | TRUE
84 | bus_LV_359-7_1_3_node_130 | 0.4 | n |  | TRUE
85 | bus_LV_359-7_1_3_node_132 | 0.4 | n |  | TRUE
86 | bus_LV_359-7_1_3_node_135 | 0.4 | n |  | TRUE
87 | bus_LV_359-7_1_3_node_146 | 0.4 | n |  | TRUE
88 | bus_LV_359-7_1_3_node_134 | 0.4 | n |  | TRUE
89 | bus_LV_359-7_1_3_node_147 | 0.4 | n |  | TRUE
90 | bus_LV_359-7_1_3_node_136 | 0.4 | n |  | TRUE
91 | bus_LV_359-7_1_3_node_137 | 0.4 | n |  | TRUE
92 | bus_LV_359-7_1_3_node_138 | 0.4 | n |  | TRUE
93 | bus_LV_359-7_1_3_node_139 | 0.4 | n |  | TRUE
94 | bus_LV_359-7_1_3_node_140 | 0.4 | n |  | TRUE
95 | bus_LV_359-7_1_3_node_141 | 0.4 | n |  | TRUE
96 | bus_LV_359-7_1_3_node_154 | 0.4 | n |  | TRUE
97 | bus_LV_359-7_1_3_node_148 | 0.4 | n |  | TRUE
98 | bus_LV_359-7_1_3_node_149 | 0.4 | n |  | TRUE
99 | bus_MV_92_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_359-7_1_3_load_20 | 0 | 0.0040323 | 0.0010106 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_359-7_1_3_load_21 | 1 | 0.003578 | 0.00089674 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_359-7_1_3_load_22 | 2 | 0.003343 | 0.00083785 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_359-7_1_3_load_23 | 3 | 0.0027489 | 0.00068893 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_359-7_1_3_load_24 | 4 | 0.0030032 | 0.00075268 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_359-7_1_3_load_40 | 5 | 0.0050645 | 0.0012693 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_359-7_1_3_load_30 | 6 | 0.004254 | 0.0010662 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_359-7_1_3_load_41 | 7 | 0.0033159 | 0.00083106 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_359-7_1_3_load_29 | 8 | 0.0034897 | 0.0008746 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_359-7_1_3_load_25 | 9 | 0.0035925 | 0.00090036 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_359-7_1_3_load_26 | 10 | 0.0039207 | 0.00098262 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_359-7_1_3_load_27 | 11 | 0.00316 | 0.00079198 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_359-7_1_3_load_152 | 14 | 0.0010367 | 0.00025981 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_359-7_1_3_load_151 | 15 | 0.0028796 | 0.00072169 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_359-7_1_3_load_38 | 16 | 0.0035569 | 0.00089143 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_359-7_1_3_load_46 | 17 | 0.0029037 | 0.00072774 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_359-7_1_3_load_45 | 18 | 0.0043258 | 0.0010842 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_359-7_1_3_load_153 | 19 | 0.00085526 | 0.00021435 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_359-7_1_3_load_150 | 20 | 0.0021848 | 0.00054757 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_359-7_1_3_load_42 | 23 | 0.0028323 | 0.00070984 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_359-7_1_3_load_47 | 24 | 0.0041911 | 0.0010504 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_359-7_1_3_load_142 | 25 | 0.0021577 | 0.00054076 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_359-7_1_3_load_143 | 26 | 0.0018883 | 0.00047325 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_359-7_1_3_load_48 | 27 | 0.0035459 | 0.00088868 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_359-7_1_3_load_49 | 28 | 0.0061176 | 0.0015332 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_359-7_1_3_load_51 | 30 | 0.0024516 | 0.00061442 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_359-7_1_3_load_52 | 31 | 0.0023931 | 0.00059977 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_359-7_1_3_load_56 | 32 | 0.0036007 | 0.00090242 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_359-7_1_3_load_155 | 33 | 0.0042322 | 0.0010607 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_359-7_1_3_load_54 | 34 | 0.0028396 | 0.00071168 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_359-7_1_3_load_53 | 35 | 0.0029845 | 0.00074798 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_359-7_1_3_load_55 | 36 | 0.0027486 | 0.00068888 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_359-7_1_3_load_58 | 37 | 0.0041574 | 0.0010419 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_359-7_1_3_load_57 | 38 | 0.0023571 | 0.00059075 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_359-7_1_3_load_59 | 41 | 0.0035337 | 0.00088563 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_359-7_1_3_load_66 | 44 | 0.0032455 | 0.00081339 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_359-7_1_3_load_101 | 46 | 0.0017456 | 0.0004375 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_359-7_1_3_load_120 | 47 | 0.0031249 | 0.00078317 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_359-7_1_3_load_119 | 48 | 0.001928 | 0.00048321 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_359-7_1_3_load_100 | 49 | 0.0021477 | 0.00053827 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_359-7_1_3_load_63 | 50 | 0.0037243 | 0.0009334 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_359-7_1_3_load_96 | 52 | 0.0013067 | 0.00032748 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_359-7_1_3_load_97 | 53 | 0.0019437 | 0.00048714 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_359-7_1_3_load_98 | 54 | 0.0020146 | 0.00050492 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_359-7_1_3_load_99 | 55 | 0.0020714 | 0.00051913 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_359-7_1_3_load_121 | 56 | 0.0062286 | 0.001561 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_359-7_1_3_load_117 | 57 | 0.001971 | 0.00049399 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_359-7_1_3_load_104 | 58 | 0.0058368 | 0.0014628 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_359-7_1_3_load_105 | 59 | 0.0023686 | 0.00059363 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_359-7_1_3_load_106 | 60 | 0.0017306 | 0.00043373 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_359-7_1_3_load_107 | 61 | 0.0031931 | 0.00080028 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_359-7_1_3_load_108 | 62 | 0.0013911 | 0.00034864 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_359-7_1_3_load_109 | 63 | 0.0013908 | 0.00034857 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_359-7_1_3_load_110 | 64 | 0.0019631 | 0.00049199 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_359-7_1_3_load_112 | 65 | 0.001376 | 0.00034487 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_359-7_1_3_load_111 | 66 | 0.0014298 | 0.00035834 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_359-7_1_3_load_113 | 67 | 0.0018333 | 0.00045947 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_359-7_1_3_load_114 | 68 | 0.0030376 | 0.00076129 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_359-7_1_3_load_144 | 69 | 0.0023845 | 0.00059761 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_359-7_1_3_load_145 | 70 | 0.0060646 | 0.0015199 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_359-7_1_3_load_115 | 71 | 0.0014177 | 0.00035532 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_359-7_1_3_load_116 | 72 | 0.0038863 | 0.00097401 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_359-7_1_3_load_118 | 73 | 0.0014269 | 0.00035761 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_359-7_1_3_load_122 | 76 | 0.0063595 | 0.0015939 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_359-7_1_3_load_123 | 77 | 0.0043236 | 0.0010836 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_359-7_1_3_load_124 | 78 | 0.0046892 | 0.0011752 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_359-7_1_3_load_125 | 79 | 0.0015939 | 0.00039946 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_359-7_1_3_load_126 | 80 | 0.0011608 | 0.00029093 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_359-7_1_3_load_127 | 81 | 0.0015836 | 0.00039689 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_359-7_1_3_load_133 | 82 | 0.0033637 | 0.00084302 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_359-7_1_3_load_129 | 83 | 0.0031842 | 0.00079804 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_359-7_1_3_load_130 | 84 | 0.0024943 | 0.00062513 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_359-7_1_3_load_132 | 85 | 0.0026332 | 0.00065994 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_359-7_1_3_load_135 | 86 | 0.0027012 | 0.00067698 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_359-7_1_3_load_146 | 87 | 0.0040242 | 0.0010086 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_359-7_1_3_load_134 | 88 | 0.002728 | 0.0006837 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_359-7_1_3_load_147 | 89 | 0.0042252 | 0.0010589 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_359-7_1_3_load_136 | 90 | 0.0027603 | 0.00069181 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_359-7_1_3_load_137 | 91 | 0.0010822 | 0.00027123 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_359-7_1_3_load_138 | 92 | 0.0026164 | 0.00065573 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_359-7_1_3_load_139 | 93 | 0.0011019 | 0.00027616 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_359-7_1_3_load_140 | 94 | 0.0010643 | 0.00026673 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_359-7_1_3_load_141 | 95 | 0.001046 | 0.00026215 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_359-7_1_3_load_154 | 96 | 0.0023903 | 0.00059906 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_359-7_1_3_load_148 | 97 | 0.0035522 | 0.00089026 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_359-7_1_3_load_149 | 98 | 0.0023033 | 0.00057727 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 75 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_359-7_1_3_line_0 |  | 0 | 1 | 0.017427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_359-7_1_3_line_1 |  | 0 | 2 | 0.014881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_359-7_1_3_line_2 |  | 1 | 3 | 0.0080319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_359-7_1_3_line_3 |  | 2 | 4 | 0.013775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_359-7_1_3_line_4 |  | 3 | 5 | 0.01943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_359-7_1_3_line_5 |  | 4 | 6 | 0.011651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_359-7_1_3_line_6 |  | 5 | 7 | 0.010867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_359-7_1_3_line_7 |  | 6 | 8 | 0.001933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_359-7_1_3_line_8 |  | 7 | 21 | 0.023848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_359-7_1_3_line_9 |  | 8 | 11 | 0.018052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_359-7_1_3_line_10 |  | 9 | 10 | 0.019747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_359-7_1_3_line_11 |  | 9 | 11 | 0.011194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_359-7_1_3_line_12 |  | 10 | 12 | 0.034435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_359-7_1_3_line_13 |  | 12 | 13 | 0.042626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_359-7_1_3_line_14 |  | 13 | 14 | 0.018036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_359-7_1_3_line_15 |  | 13 | 15 | 0.0066041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_359-7_1_3_line_16 |  | 14 | 19 | 0.00031177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_359-7_1_3_line_17 |  | 15 | 20 | 0.0032482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_359-7_1_3_line_18 |  | 16 | 17 | 0.021355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_359-7_1_3_line_19 |  | 17 | 18 | 0.0052521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_359-7_1_3_line_20 |  | 18 | 22 | 0.024235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_359-7_1_3_line_21 |  | 19 | 96 | 0.0038958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_359-7_1_3_line_22 |  | 21 | 22 | 0.012265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_359-7_1_3_line_23 |  | 21 | 23 | 0.0078743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_359-7_1_3_line_24 |  | 22 | 24 | 0.016797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_359-7_1_3_line_25 |  | 24 | 25 | 0.00014884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_359-7_1_3_line_26 |  | 25 | 26 | 0.0083378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_359-7_1_3_line_27 |  | 27 | 28 | 0.004523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_359-7_1_3_line_28 |  | 27 | 29 | 0.020578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_359-7_1_3_line_29 |  | 28 | 30 | 0.017012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_359-7_1_3_line_30 |  | 29 | 31 | 0.01709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_359-7_1_3_line_31 |  | 30 | 32 | 0.0086641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_359-7_1_3_line_32 |  | 31 | 33 | 0.00084634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_359-7_1_3_line_33 |  | 32 | 34 | 0.0084561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_359-7_1_3_line_34 |  | 34 | 35 | 0.016506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_359-7_1_3_line_35 |  | 35 | 36 | 0.0053623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_359-7_1_3_line_36 |  | 35 | 37 | 0.050702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_359-7_1_3_line_37 |  | 36 | 38 | 0.0087606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_359-7_1_3_line_38 |  | 37 | 41 | 0.028061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_359-7_1_3_line_39 |  | 38 | 39 | 0.012961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_359-7_1_3_line_40 |  | 39 | 40 | 0.018546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_359-7_1_3_line_41 |  | 40 | 45 | 0.022183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_359-7_1_3_line_42 |  | 40 | 46 | 0.014421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_359-7_1_3_line_43 |  | 41 | 42 | 0.016117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_359-7_1_3_line_44 |  | 42 | 43 | 0.003649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_359-7_1_3_line_45 |  | 43 | 44 | 0.037748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_359-7_1_3_line_46 |  | 44 | 51 | 0.0033692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_359-7_1_3_line_47 |  | 45 | 47 | 0.021665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_359-7_1_3_line_48 |  | 45 | 48 | 0.017653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_359-7_1_3_line_49 |  | 46 | 49 | 0.020085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_359-7_1_3_line_50 |  | 47 | 56 | 0.026967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_359-7_1_3_line_51 |  | 48 | 57 | 0.0036799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_359-7_1_3_line_52 |  | 49 | 55 | 0.018453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_359-7_1_3_line_53 |  | 50 | 51 | 0.023987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_359-7_1_3_line_54 |  | 52 | 53 | 0.017621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_359-7_1_3_line_55 |  | 53 | 54 | 0.0093216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_359-7_1_3_line_56 |  | 54 | 55 | 0.022015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_359-7_1_3_line_57 |  | 56 | 76 | 0.026177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_359-7_1_3_line_58 |  | 57 | 71 | 0.016145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_359-7_1_3_line_59 |  | 58 | 59 | 0.0054085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_359-7_1_3_line_60 |  | 59 | 60 | 0.026279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_359-7_1_3_line_61 |  | 60 | 61 | 0.00014667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_359-7_1_3_line_62 |  | 61 | 62 | 0.016374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_359-7_1_3_line_63 |  | 62 | 63 | 0.0048748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_359-7_1_3_line_64 |  | 63 | 64 | 0.0039755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_359-7_1_3_line_65 |  | 64 | 65 | 0.0043414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_359-7_1_3_line_66 |  | 65 | 66 | 0.014241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_359-7_1_3_line_67 |  | 66 | 67 | 0.008463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_359-7_1_3_line_68 |  | 67 | 68 | 0.01059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_359-7_1_3_line_69 |  | 68 | 69 | 0.017815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_359-7_1_3_line_70 |  | 69 | 70 | 0.007449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_359-7_1_3_line_71 |  | 70 | 74 | 0.0092785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_359-7_1_3_line_72 |  | 71 | 72 | 0.018731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_359-7_1_3_line_73 |  | 72 | 73 | 0.00325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_359-7_1_3_line_74 |  | 73 | 74 | 0.017036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_359-7_1_3_line_75 |  | 74 | 75 | 0.019889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_359-7_1_3_line_76 |  | 75 | 82 | 0.0093825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_359-7_1_3_line_77 |  | 75 | 83 | 0.013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_359-7_1_3_line_78 |  | 76 | 77 | 0.0084652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_359-7_1_3_line_79 |  | 77 | 78 | 0.027389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_359-7_1_3_line_80 |  | 78 | 79 | 0.0008737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_359-7_1_3_line_81 |  | 79 | 80 | 0.0199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_359-7_1_3_line_82 |  | 80 | 81 | 0.0012106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_359-7_1_3_line_83 |  | 82 | 87 | 0.0050711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_359-7_1_3_line_84 |  | 83 | 84 | 0.024687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_359-7_1_3_line_85 |  | 84 | 85 | 0.0083338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_359-7_1_3_line_86 |  | 85 | 86 | 0.018859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_359-7_1_3_line_87 |  | 86 | 88 | 0.0063504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_359-7_1_3_line_88 |  | 87 | 89 | 0.0029396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_359-7_1_3_line_89 |  | 88 | 90 | 0.0025608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_359-7_1_3_line_90 |  | 89 | 97 | 0.010822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_359-7_1_3_line_91 |  | 90 | 91 | 0.013917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_359-7_1_3_line_92 |  | 91 | 92 | 0.0045839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_359-7_1_3_line_93 |  | 92 | 93 | 0.0092468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_359-7_1_3_line_94 |  | 93 | 94 | 0.0028137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_359-7_1_3_line_95 |  | 94 | 95 | 0.015281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_359-7_1_3_line_96 |  | 94 | 96 | 0.040758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_359-7_1_3_line_97 |  | 97 | 98 | 0.014891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_359-7_1_3_trafo_131 | 0.63 MVA 20/0.4 kV | 99 | 75 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2607790.4534 | 1200742.1944 | 2607785.7302 | 1200745.2862 | 2607775.2927 | 1200750.7505
1 | 2607790.4534 | 1200742.1944 | 2607802.1548 | 1200734.535 | 2607802.934 | 1200734.0934
2 | 2607768.086 | 1200754.284 | 2607770.5423 | 1200753.2375 | 2607775.2927 | 1200750.7505
3 | 2607814.9731 | 1200727.4053 | 2607813.0171 | 1200728.3791 | 2607802.934 | 1200734.0934
4 | 2607768.086 | 1200754.284 | 2607755.2192 | 1200759.7658 | 2607750.0532 | 1200761.4843
5 | 2607825.4034 | 1200722.2132 | 2607814.9731 | 1200727.4053
6 | 2607739.8389 | 1200765.169 | 2607742.7689 | 1200763.9075 | 2607750.0532 | 1200761.4843
7 | 2607825.4034 | 1200722.2132 | 2607827.1339 | 1200721.3517
8 | 2607718.1385 | 1200775.0486 | 2607729.9742 | 1200769.4163 | 2607739.8389 | 1200765.169
9 | 2607843.6309 | 1200714.058 | 2607834.2446 | 1200717.812 | 2607827.1339 | 1200721.3517
10 | 2607854.0108 | 1200709.8685 | 2607860.6558 | 1200707.1407 | 2607872.6 | 1200703.2431
11 | 2607843.6309 | 1200714.058 | 2607850.3974 | 1200711.3518 | 2607854.0108 | 1200709.8685
12 | 2607905.4617 | 1200692.9583 | 2607881.8635 | 1200700.2202 | 2607872.6 | 1200703.2431
13 | 2607905.4617 | 1200692.9583 | 2607898.8852 | 1200704.5559 | 2607893.3372 | 1200709.6403 | 2607878.732 | 1200725.841
14 | 2607878.732 | 1200725.841 | 2607892.1505 | 1200726.5812 | 2607893.4959 | 1200730.9769
15 | 2607878.732 | 1200725.841 | 2607874.3106 | 1200730.7467
16 | 2607893.5871 | 1200731.275 | 2607893.4959 | 1200730.9769
17 | 2607872.136 | 1200733.1596 | 2607874.3106 | 1200730.7467
18 | 2607666.2784 | 1200810.972 | 2607670.7146 | 1200807.7168 | 2607683.4352 | 1200798.2562
19 | 2607687.6495 | 1200795.1219 | 2607683.4352 | 1200798.2562
20 | 2607707.7023 | 1200781.5387 | 2607702.827 | 1200784.5786 | 2607694.8739 | 1200789.749 | 2607687.6495 | 1200795.1219
21 | 2607894.7274 | 1200735.0002 | 2607893.5871 | 1200731.275
22 | 2607718.1385 | 1200775.0486 | 2607707.7023 | 1200781.5387
23 | 2607718.1385 | 1200775.0486 | 2607715.2179 | 1200773.344 | 2607714.0235 | 1200772.8644 | 2607712.6916 | 1200772.7182 | 2607710.8304 | 1200772.8465
24 | 2607707.7023 | 1200781.5387 | 2607718.0567 | 1200794.7648
25 | 2607718.0567 | 1200794.7648 | 2607718.1485 | 1200794.882
26 | 2607723.2882 | 1200801.4472 | 2607718.1485 | 1200794.882
27 | 2607892.4822 | 1200905.3987 | 2607893.4081 | 1200905.3347 | 2607896.9635 | 1200904.8025
28 | 2607916.6921 | 1200899.1285 | 2607911.7649 | 1200901.0676 | 2607908.8714 | 1200901.9198 | 2607906.016 | 1200902.7721 | 2607899.4451 | 1200904.431 | 2607896.9635 | 1200904.8025
29 | 2607892.4822 | 1200905.3987 | 2607875.5104 | 1200906.5715
30 | 2607916.6921 | 1200899.1285 | 2607931.6283 | 1200890.8243
31 | 2607866.8674 | 1200907.1763 | 2607868.4631 | 1200907.0585 | 2607875.5104 | 1200906.5715
32 | 2607932.368 | 1200890.4131 | 2607931.6283 | 1200890.8243
33 | 2607858.4342 | 1200907.7988 | 2607866.8674 | 1200907.1763
34 | 2607858.4342 | 1200907.7988 | 2607841.9727 | 1200909.014
35 | 2607836.6163 | 1200909.265 | 2607841.9727 | 1200909.014 | 2607841.9727 | 1200909.014
36 | 2607841.9727 | 1200909.014 | 2607842.1029 | 1200959.7157
37 | 2607827.8656 | 1200909.6815 | 2607833.8964 | 1200909.3925 | 2607836.6163 | 1200909.265
38 | 2607855.6281 | 1200984.3021 | 2607842.1029 | 1200959.7157
39 | 2607814.9199 | 1200910.3017 | 2607827.8656 | 1200909.6815
40 | 2607796.3765 | 1200911.7452 | 2607814.9199 | 1200910.3017
41 | 2607796.3765 | 1200911.7452 | 2607796.6052 | 1200905.6199 | 2607797.2882 | 1200901.3185 | 2607798.7321 | 1200897.1626 | 2607802.0402 | 1200893.5093 | 2607803.9222 | 1200892.0554
42 | 2607796.3765 | 1200911.7452 | 2607781.9987 | 1200912.8588
43 | 2607863.3963 | 1200998.4234 | 2607855.6281 | 1200984.3021
44 | 2607866.3827 | 1200996.315 | 2607863.3963 | 1200998.4234
45 | 2607866.3827 | 1200996.315 | 2607898.2799 | 1200976.1282
46 | 2607901.1269 | 1200974.3264 | 2607898.2799 | 1200976.1282
47 | 2607803.9222 | 1200892.0554 | 2607823.0821 | 1200881.9428
48 | 2607803.9222 | 1200892.0554 | 2607800.321 | 1200886.9035 | 2607799.479 | 1200884.679 | 2607798.8061 | 1200881.1652 | 2607797.9715 | 1200875.8189
49 | 2607761.9737 | 1200914.4123 | 2607776.189 | 1200913.3088 | 2607781.9987 | 1200912.8588
50 | 2607823.0821 | 1200881.9428 | 2607826.5514 | 1200880.1117 | 2607847.0449 | 1200869.5742
51 | 2607797.4039 | 1200872.1831 | 2607797.9715 | 1200875.8189
52 | 2607743.5764 | 1200915.8404 | 2607761.9737 | 1200914.4123
53 | 2607901.1269 | 1200974.3264 | 2607920.9908 | 1200960.8807
54 | 2607694.7656 | 1200919.6294 | 2607712.3339 | 1200918.2656
55 | 2607721.6276 | 1200917.5442 | 2607712.3339 | 1200918.2656
56 | 2607721.6276 | 1200917.5442 | 2607743.5764 | 1200915.8404
57 | 2607847.0449 | 1200869.5742 | 2607870.3248 | 1200857.6039
58 | 2607797.4039 | 1200872.1831 | 2607796.3376 | 1200865.3534 | 2607796.3492 | 1200862.3185 | 2607797.1904 | 1200859.2735 | 2607798.564 | 1200856.5627 | 2607798.564 | 1200856.5627
59 | 2607680.9648 | 1200867.8575 | 2607680.0684 | 1200868.1168 | 2607675.668 | 1200868.9327
60 | 2607680.9648 | 1200867.8575 | 2607698.9747 | 1200862.6491 | 2607706.1548 | 1200860.3753
61 | 2607706.2946 | 1200860.331 | 2607706.1548 | 1200860.3753
62 | 2607721.6158 | 1200854.6053 | 2607713.4501 | 1200858.0651 | 2607706.2946 | 1200860.331
63 | 2607721.6158 | 1200854.6053 | 2607726.1043 | 1200852.7035
64 | 2607729.7648 | 1200851.1525 | 2607726.1043 | 1200852.7035
65 | 2607733.7622 | 1200849.4588 | 2607729.7648 | 1200851.1525
66 | 2607733.7622 | 1200849.4588 | 2607746.8744 | 1200843.9032
67 | 2607754.6792 | 1200840.6311 | 2607750.8049 | 1200842.2378 | 2607746.8744 | 1200843.9032
68 | 2607754.6792 | 1200840.6311 | 2607764.4617 | 1200836.5743
69 | 2607764.4617 | 1200836.5743 | 2607780.9177 | 1200829.7498
70 | 2607780.9177 | 1200829.7498 | 2607787.7985 | 1200826.8963
71 | 2607796.3692 | 1200823.342 | 2607787.7985 | 1200826.8963
72 | 2607798.564 | 1200856.5627 | 2607800.271 | 1200854.9529 | 2607806.3883 | 1200850.9254 | 2607803.2938 | 1200842.4094
73 | 2607802.1838 | 1200839.3548 | 2607803.2938 | 1200842.4094
74 | 2607796.3692 | 1200823.342 | 2607799.9339 | 1200833.163 | 2607802.1838 | 1200839.3548
75 | 2607814.7687 | 1200815.6617 | 2607796.3692 | 1200823.342
76 | 2607814.7687 | 1200815.6617 | 2607813.0052 | 1200806.4464
77 | 2607814.7687 | 1200815.6617 | 2607827.3813 | 1200810.5953
78 | 2607877.8532 | 1200853.7329 | 2607870.3248 | 1200857.6039
79 | 2607877.8532 | 1200853.7329 | 2607892.9531 | 1200845.9688 | 2607902.0432 | 1200840.8949
80 | 2607902.8061 | 1200840.4691 | 2607902.0432 | 1200840.8949
81 | 2607902.8061 | 1200840.4691 | 2607920.1824 | 1200830.7701
82 | 2607921.2396 | 1200830.1801 | 2607920.1824 | 1200830.7701
83 | 2607813.105 | 1200801.4185 | 2607813.105 | 1200801.4185 | 2607812.7521 | 1200803.5525 | 2607812.9088 | 1200805.9429 | 2607813.0052 | 1200806.4464
84 | 2607827.3813 | 1200810.5953 | 2607837.4173 | 1200806.564 | 2607850.131 | 1200801.0154
85 | 2607857.7691 | 1200797.682 | 2607850.131 | 1200801.0154
86 | 2607857.7691 | 1200797.682 | 2607867.0052 | 1200793.6511 | 2607874.9083 | 1200789.822
87 | 2607880.6233 | 1200787.0531 | 2607874.9083 | 1200789.822
88 | 2607813.105 | 1200801.4185 | 2607813.9992 | 1200798.6182 | 2607813.9992 | 1200798.6182
89 | 2607882.9278 | 1200785.9365 | 2607880.6233 | 1200787.0531
90 | 2607813.9992 | 1200798.6182 | 2607820.5554 | 1200790.0084
91 | 2607882.9278 | 1200785.9365 | 2607895.4519 | 1200779.8685
92 | 2607895.4519 | 1200779.8685 | 2607899.5771 | 1200777.8698
93 | 2607907.8986 | 1200773.838 | 2607899.5771 | 1200777.8698
94 | 2607907.8986 | 1200773.838 | 2607910.4308 | 1200772.6111
95 | 2607924.1825 | 1200765.9484 | 2607910.4308 | 1200772.6111
96 | 2607910.4308 | 1200772.6111 | 2607894.7274 | 1200735.0002
97 | 2607820.5554 | 1200790.0084 | 2607820.8918 | 1200789.5667 | 2607830.3222 | 1200778.7688

## bus_geodata
| x | y | coords
0 | 2607790.4534 | 1200742.1944
1 | 2607775.2927 | 1200750.7505
2 | 2607802.934 | 1200734.0934
3 | 2607768.086 | 1200754.284
4 | 2607814.9731 | 1200727.4053
5 | 2607750.0532 | 1200761.4843
6 | 2607825.4034 | 1200722.2132
7 | 2607739.8389 | 1200765.169
8 | 2607827.1339 | 1200721.3517
9 | 2607854.0108 | 1200709.8685
10 | 2607872.6 | 1200703.2431
11 | 2607843.6309 | 1200714.058
12 | 2607905.4617 | 1200692.9583
13 | 2607878.732 | 1200725.841
14 | 2607893.4959 | 1200730.9769
15 | 2607874.3106 | 1200730.7467
16 | 2607666.2784 | 1200810.972
17 | 2607683.4352 | 1200798.2562
18 | 2607687.6495 | 1200795.1219
19 | 2607893.5871 | 1200731.275
20 | 2607872.136 | 1200733.1596
21 | 2607718.1385 | 1200775.0486
22 | 2607707.7023 | 1200781.5387
23 | 2607710.8304 | 1200772.8465
24 | 2607718.0567 | 1200794.7648
25 | 2607718.1485 | 1200794.882
26 | 2607723.2882 | 1200801.4472
27 | 2607896.9635 | 1200904.8025
28 | 2607892.4822 | 1200905.3987
29 | 2607916.6921 | 1200899.1285
30 | 2607875.5104 | 1200906.5715
31 | 2607931.6283 | 1200890.8243
32 | 2607866.8674 | 1200907.1763
33 | 2607932.368 | 1200890.4131
34 | 2607858.4342 | 1200907.7988
35 | 2607841.9727 | 1200909.014
36 | 2607836.6163 | 1200909.265
37 | 2607842.1029 | 1200959.7157
38 | 2607827.8656 | 1200909.6815
39 | 2607814.9199 | 1200910.3017
40 | 2607796.3765 | 1200911.7452
41 | 2607855.6281 | 1200984.3021
42 | 2607863.3963 | 1200998.4234
43 | 2607866.3827 | 1200996.315
44 | 2607898.2799 | 1200976.1282
45 | 2607803.9222 | 1200892.0554
46 | 2607781.9987 | 1200912.8588
47 | 2607823.0821 | 1200881.9428
48 | 2607797.9715 | 1200875.8189
49 | 2607761.9737 | 1200914.4123
50 | 2607920.9908 | 1200960.8807
51 | 2607901.1269 | 1200974.3264
52 | 2607694.7656 | 1200919.6294
53 | 2607712.3339 | 1200918.2656
54 | 2607721.6276 | 1200917.5442
55 | 2607743.5764 | 1200915.8404
56 | 2607847.0449 | 1200869.5742
57 | 2607797.4039 | 1200872.1831
58 | 2607675.668 | 1200868.9327
59 | 2607680.9648 | 1200867.8575
60 | 2607706.1548 | 1200860.3753
61 | 2607706.2946 | 1200860.331
62 | 2607721.6158 | 1200854.6053
63 | 2607726.1043 | 1200852.7035
64 | 2607729.7648 | 1200851.1525
65 | 2607733.7622 | 1200849.4588
66 | 2607746.8744 | 1200843.9032
67 | 2607754.6792 | 1200840.6311
68 | 2607764.4617 | 1200836.5743
69 | 2607780.9177 | 1200829.7498
70 | 2607787.7985 | 1200826.8963
71 | 2607798.564 | 1200856.5627
72 | 2607803.2938 | 1200842.4094
73 | 2607802.1838 | 1200839.3548
74 | 2607796.3692 | 1200823.342
75 | 2607814.7687 | 1200815.6617
76 | 2607870.3248 | 1200857.6039
77 | 2607877.8532 | 1200853.7329
78 | 2607902.0432 | 1200840.8949
79 | 2607902.8061 | 1200840.4691
80 | 2607920.1824 | 1200830.7701
81 | 2607921.2396 | 1200830.1801
82 | 2607813.0052 | 1200806.4464
83 | 2607827.3813 | 1200810.5953
84 | 2607850.131 | 1200801.0154
85 | 2607857.7691 | 1200797.682
86 | 2607874.9083 | 1200789.822
87 | 2607813.105 | 1200801.4185
88 | 2607880.6233 | 1200787.0531
89 | 2607813.9992 | 1200798.6182
90 | 2607882.9278 | 1200785.9365
91 | 2607895.4519 | 1200779.8685
92 | 2607899.5771 | 1200777.8698
93 | 2607907.8986 | 1200773.838
94 | 2607910.4308 | 1200772.6111
95 | 2607924.1825 | 1200765.9484
96 | 2607894.7274 | 1200735.0002
97 | 2607820.5554 | 1200790.0084
98 | 2607830.3222 | 1200778.7688
99 | 2607796.3692 | 1200823.342

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1