## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_363-28_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_363-28_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_363-28_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_363-28_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_363-28_0_4_node_66 | 0.4 | n |  | TRUE
5 | bus_LV_363-28_0_4_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_363-28_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_363-28_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_363-28_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_363-28_0_4_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_363-28_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_363-28_0_4_node_64 | 0.4 | n |  | TRUE
12 | bus_LV_363-28_0_4_node_65 | 0.4 | n |  | TRUE
13 | bus_LV_363-28_0_4_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_363-28_0_4_node_123 | 0.4 | n |  | TRUE
15 | bus_LV_363-28_0_4_node_117 | 0.4 | n |  | TRUE
16 | bus_LV_363-28_0_4_node_37 | 0.4 | n |  | TRUE
17 | bus_LV_363-28_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_363-28_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_363-28_0_4_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_363-28_0_4_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_363-28_0_4_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_363-28_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_363-28_0_4_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_363-28_0_4_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_363-28_0_4_node_31 | 0.4 | n |  | TRUE
26 | bus_LV_363-28_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_363-28_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_363-28_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_363-28_0_4_node_127 | 0.4 | n |  | TRUE
30 | bus_LV_363-28_0_4_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_363-28_0_4_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_363-28_0_4_node_67 | 0.4 | n |  | TRUE
33 | bus_LV_363-28_0_4_node_75 | 0.4 | n |  | TRUE
34 | bus_LV_363-28_0_4_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_363-28_0_4_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_363-28_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_363-28_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_363-28_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_363-28_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_363-28_0_4_node_56 | 0.4 | n |  | TRUE
41 | bus_LV_363-28_0_4_node_57 | 0.4 | n |  | TRUE
42 | bus_LV_363-28_0_4_node_50 | 0.4 | n |  | TRUE
43 | bus_LV_363-28_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_363-28_0_4_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_363-28_0_4_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_363-28_0_4_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_363-28_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_363-28_0_4_node_68 | 0.4 | n |  | TRUE
49 | bus_LV_363-28_0_4_node_78 | 0.4 | n |  | TRUE
50 | bus_LV_363-28_0_4_node_129 | 0.4 | n |  | TRUE
51 | bus_LV_363-28_0_4_node_118 | 0.4 | n |  | TRUE
52 | bus_LV_363-28_0_4_node_73 | 0.4 | n |  | TRUE
53 | bus_LV_363-28_0_4_node_70 | 0.4 | n |  | TRUE
54 | bus_LV_363-28_0_4_node_72 | 0.4 | n |  | TRUE
55 | bus_LV_363-28_0_4_node_122 | 0.4 | n |  | TRUE
56 | bus_LV_363-28_0_4_node_71 | 0.4 | n |  | TRUE
57 | bus_LV_363-28_0_4_node_48 | 0.4 | n |  | TRUE
58 | bus_LV_363-28_0_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_363-28_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_363-28_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_363-28_0_4_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_363-28_0_4_node_84 | 0.4 | n |  | TRUE
63 | bus_LV_363-28_0_4_node_81 | 0.4 | n |  | TRUE
64 | bus_LV_363-28_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_363-28_0_4_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_363-28_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_363-28_0_4_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_363-28_0_4_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_363-28_0_4_node_103 | 0.4 | n |  | TRUE
70 | bus_LV_363-28_0_4_node_124 | 0.4 | n |  | TRUE
71 | bus_LV_363-28_0_4_node_104 | 0.4 | n |  | TRUE
72 | bus_LV_363-28_0_4_node_125 | 0.4 | n |  | TRUE
73 | bus_LV_363-28_0_4_node_58 | 0.4 | n |  | TRUE
74 | bus_LV_363-28_0_4_node_59 | 0.4 | n |  | TRUE
75 | bus_LV_363-28_0_4_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_363-28_0_4_node_61 | 0.4 | n |  | TRUE
77 | bus_LV_363-28_0_4_node_62 | 0.4 | n |  | TRUE
78 | bus_LV_363-28_0_4_node_126 | 0.4 | n |  | TRUE
79 | bus_LV_363-28_0_4_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_363-28_0_4_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_363-28_0_4_node_76 | 0.4 | n |  | TRUE
82 | bus_LV_363-28_0_4_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_363-28_0_4_node_90 | 0.4 | n |  | TRUE
84 | bus_LV_363-28_0_4_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_363-28_0_4_node_88 | 0.4 | n |  | TRUE
86 | bus_LV_363-28_0_4_node_92 | 0.4 | n |  | TRUE
87 | bus_LV_363-28_0_4_node_79 | 0.4 | n |  | TRUE
88 | bus_LV_363-28_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_363-28_0_4_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_363-28_0_4_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_363-28_0_4_node_85 | 0.4 | n |  | TRUE
92 | bus_LV_363-28_0_4_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_363-28_0_4_node_100 | 0.4 | n |  | TRUE
94 | bus_LV_363-28_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_363-28_0_4_node_87 | 0.4 | n |  | TRUE
96 | bus_LV_363-28_0_4_node_89 | 0.4 | n |  | TRUE
97 | bus_LV_363-28_0_4_node_96 | 0.4 | n |  | TRUE
98 | bus_LV_363-28_0_4_node_97 | 0.4 | n |  | TRUE
99 | bus_LV_363-28_0_4_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_363-28_0_4_node_94 | 0.4 | n |  | TRUE
101 | bus_LV_363-28_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_363-28_0_4_node_98 | 0.4 | n |  | TRUE
103 | bus_LV_363-28_0_4_node_119 | 0.4 | n |  | TRUE
104 | bus_LV_363-28_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_363-28_0_4_node_109 | 0.4 | n |  | TRUE
106 | bus_LV_363-28_0_4_node_106 | 0.4 | n |  | TRUE
107 | bus_LV_363-28_0_4_node_130 | 0.4 | n |  | TRUE
108 | bus_LV_363-28_0_4_node_120 | 0.4 | n |  | TRUE
109 | bus_LV_363-28_0_4_node_115 | 0.4 | n |  | TRUE
110 | bus_LV_363-28_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_363-28_0_4_node_105 | 0.4 | n |  | TRUE
112 | bus_LV_363-28_0_4_node_110 | 0.4 | n |  | TRUE
113 | bus_LV_363-28_0_4_node_111 | 0.4 | n |  | TRUE
114 | bus_LV_363-28_0_4_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_363-28_0_4_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_363-28_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_363-28_0_4_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_363-28_0_4_node_113 | 0.4 | n |  | TRUE
119 | bus_LV_363-28_0_4_node_114 | 0.4 | n |  | TRUE
120 | bus_MV_599_0_node_149 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_363-28_0_4_load_0 | 0 | 0.024473 | 0.0061336 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_363-28_0_4_load_4 | 3 | 0.0055055 | 0.0013798 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_363-28_0_4_load_66 | 4 | 0.030407 | 0.0076207 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_363-28_0_4_load_7 | 6 | 0.006447 | 0.0016158 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_363-28_0_4_load_12 | 9 | 0.0062922 | 0.001577 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_363-28_0_4_load_64 | 11 | 0.0060797 | 0.0015237 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_363-28_0_4_load_63 | 13 | 0.0068532 | 0.0017176 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_363-28_0_4_load_123 | 14 | 0.0045575 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_363-28_0_4_load_117 | 15 | 0.013912 | 0.0034867 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_363-28_0_4_load_13 | 17 | 0.0069649 | 0.0017456 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_363-28_0_4_load_16 | 19 | 0.010928 | 0.0027388 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_363-28_0_4_load_17 | 20 | 0.013669 | 0.0034258 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_363-28_0_4_load_30 | 21 | 0.0062819 | 0.0015744 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_363-28_0_4_load_36 | 23 | 0.0038857 | 0.00097385 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_363-28_0_4_load_34 | 24 | 0.0044333 | 0.0011111 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_363-28_0_4_load_31 | 25 | 0.0043797 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_363-28_0_4_load_21 | 26 | 0.011474 | 0.0028755 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_363-28_0_4_load_127 | 29 | 0.0052303 | 0.0013108 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_363-28_0_4_load_29 | 30 | 0.0035208 | 0.0008824 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_363-28_0_4_load_67 | 32 | 0.0048981 | 0.0012276 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_363-28_0_4_load_33 | 34 | 0.0044184 | 0.0011073 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_363-28_0_4_load_24 | 35 | 0.010587 | 0.0026532 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_363-28_0_4_load_25 | 36 | 0.013707 | 0.0034354 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_363-28_0_4_load_26 | 38 | 0.011944 | 0.0029935 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_363-28_0_4_load_28 | 39 | 0.0028926 | 0.00072496 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_363-28_0_4_load_57 | 41 | 0.0066504 | 0.0016668 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_363-28_0_4_load_50 | 42 | 0.0038031 | 0.00095313 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_363-28_0_4_load_42 | 44 | 0.010724 | 0.0026876 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_363-28_0_4_load_39 | 45 | 0.010739 | 0.0026916 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_363-28_0_4_load_49 | 46 | 0.011896 | 0.0029814 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_363-28_0_4_load_40 | 47 | 0.010757 | 0.0026959 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_363-28_0_4_load_129 | 50 | 0.018311 | 0.0045891 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_363-28_0_4_load_118 | 51 | 0.014712 | 0.0036873 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_363-28_0_4_load_73 | 52 | 0.0075069 | 0.0018814 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_363-28_0_4_load_70 | 53 | 0.0048831 | 0.0012238 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_363-28_0_4_load_122 | 55 | 0.0010066 | 0.00025227 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_363-28_0_4_load_71 | 56 | 0.00077887 | 0.0001952 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_363-28_0_4_load_43 | 58 | 0.010739 | 0.0026916 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_363-28_0_4_load_44 | 59 | 0.00027838 | 6.977e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_363-28_0_4_load_47 | 61 | 0.0058457 | 0.0014651 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_363-28_0_4_load_51 | 64 | 0.00021495 | 5.3871e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_363-28_0_4_load_52 | 65 | 0.00020699 | 5.1877e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_363-28_0_4_load_53 | 66 | 0.00020711 | 5.1908e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_363-28_0_4_load_54 | 67 | 0.0002074 | 5.198e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_363-28_0_4_load_55 | 68 | 0.0027108 | 0.00067939 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_363-28_0_4_load_103 | 69 | 0.00021471 | 5.3811e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_363-28_0_4_load_124 | 70 | 0.0026121 | 0.00065464 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_363-28_0_4_load_104 | 71 | 0.00020774 | 5.2065e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_363-28_0_4_load_125 | 72 | 0.0026079 | 0.0006536 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_363-28_0_4_load_58 | 73 | 0.0027138 | 0.00068014 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_363-28_0_4_load_59 | 74 | 0.0022137 | 0.0005548 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_363-28_0_4_load_60 | 75 | 0.0026119 | 0.00065462 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_363-28_0_4_load_61 | 76 | 0.0022178 | 0.00055584 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_363-28_0_4_load_62 | 77 | 0.0026145 | 0.00065525 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_363-28_0_4_load_126 | 78 | 0.0026913 | 0.00067451 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_363-28_0_4_load_69 | 79 | 0.0056301 | 0.001411 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_363-28_0_4_load_74 | 80 | 0.0046165 | 0.001157 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_363-28_0_4_load_76 | 81 | 0.00087482 | 0.00021925 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_363-28_0_4_load_91 | 84 | 0.0072258 | 0.0018109 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_363-28_0_4_load_92 | 86 | 0.007225 | 0.0018108 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_363-28_0_4_load_79 | 87 | 0.0010437 | 0.00026158 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_363-28_0_4_load_82 | 89 | 0.0010405 | 0.00026077 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_363-28_0_4_load_83 | 90 | 0.0011101 | 0.00027821 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_363-28_0_4_load_85 | 91 | 0.00069485 | 0.00017415 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_363-28_0_4_load_101 | 92 | 0.00028017 | 7.0217e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_363-28_0_4_load_86 | 94 | 0.0072465 | 0.0018161 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_363-28_0_4_load_87 | 95 | 0.0072115 | 0.0018074 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_363-28_0_4_load_96 | 97 | 0.00096824 | 0.00024266 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_363-28_0_4_load_94 | 100 | 0.00096751 | 0.00024248 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_363-28_0_4_load_119 | 103 | 0.0002806 | 7.0325e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_363-28_0_4_load_109 | 105 | 0.00020725 | 5.1942e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_363-28_0_4_load_106 | 106 | 0.00021575 | 5.4072e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_363-28_0_4_load_130 | 107 | 0.00069458 | 0.00017408 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_363-28_0_4_load_120 | 108 | 0.00020779 | 5.2077e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_363-28_0_4_load_115 | 109 | 0.00021561 | 5.4036e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_363-28_0_4_load_107 | 110 | 0.00020764 | 5.2039e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_363-28_0_4_load_105 | 111 | 0.00021547 | 5.4002e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_363-28_0_4_load_110 | 112 | 0.00020725 | 5.1943e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_363-28_0_4_load_111 | 113 | 0.00020796 | 5.2119e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_363-28_0_4_load_108 | 114 | 0.00020725 | 5.1941e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_363-28_0_4_load_121 | 115 | 0.00020765 | 5.2043e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_363-28_0_4_load_116 | 116 | 0.00020777 | 5.2072e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_363-28_0_4_load_112 | 117 | 0.00021615 | 5.4171e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_363-28_0_4_load_113 | 118 | 0.00020719 | 5.1926e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_363-28_0_4_load_114 | 119 | 0.00020718 | 5.1925e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_363-28_0_4_line_0 |  | 0 | 1 | 0.046577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_363-28_0_4_line_1 |  | 1 | 2 | 0.033638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_363-28_0_4_line_2 |  | 1 | 3 | 0.07549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_363-28_0_4_line_3 |  | 2 | 4 | 0.056382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_363-28_0_4_line_4 |  | 4 | 5 | 0.012756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_363-28_0_4_line_5 |  | 5 | 22 | 0.047689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_363-28_0_4_line_6 |  | 6 | 7 | 0.0023804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_363-28_0_4_line_7 |  | 7 | 8 | 0.024735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_363-28_0_4_line_8 |  | 7 | 9 | 0.026326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_363-28_0_4_line_9 |  | 8 | 12 | 0.025295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_363-28_0_4_line_10 |  | 8 | 13 | 0.0046547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_363-28_0_4_line_11 |  | 9 | 14 | 0.026868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_363-28_0_4_line_12 |  | 10 | 11 | 0.010324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_363-28_0_4_line_13 |  | 10 | 12 | 0.024647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_363-28_0_4_line_14 |  | 12 | 15 | 0.014862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_363-28_0_4_line_15 |  | 14 | 16 | 0.022427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_363-28_0_4_line_16 |  | 15 | 51 | 0.00059631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_363-28_0_4_line_17 |  | 16 | 33 | 0.015486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_363-28_0_4_line_18 |  | 17 | 18 | 0.01581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_363-28_0_4_line_19 |  | 18 | 19 | 0.004546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_363-28_0_4_line_20 |  | 18 | 20 | 0.022816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_363-28_0_4_line_21 |  | 20 | 21 | 0.0051635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_363-28_0_4_line_22 |  | 21 | 25 | 0.017699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_363-28_0_4_line_23 |  | 22 | 23 | 0.030876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_363-28_0_4_line_24 |  | 22 | 24 | 0.020123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_363-28_0_4_line_25 |  | 23 | 31 | 0.030415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_363-28_0_4_line_26 |  | 23 | 32 | 0.022294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_363-28_0_4_line_27 |  | 24 | 34 | 0.0018118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_363-28_0_4_line_28 |  | 25 | 34 | 0.020344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_363-28_0_4_line_29 |  | 26 | 27 | 0.0048884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_363-28_0_4_line_30 |  | 27 | 35 | 0.015044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_363-28_0_4_line_31 |  | 27 | 36 | 0.022479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_363-28_0_4_line_32 |  | 28 | 29 | 0.009462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_363-28_0_4_line_33 |  | 28 | 30 | 0.014752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_363-28_0_4_line_34 |  | 30 | 37 | 0.019646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_363-28_0_4_line_35 |  | 31 | 47 | 0.01961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_363-28_0_4_line_36 |  | 32 | 48 | 0.010031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_363-28_0_4_line_37 |  | 33 | 52 | 0.024981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_363-28_0_4_line_38 |  | 35 | 38 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_363-28_0_4_line_39 |  | 37 | 39 | 0.010564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_363-28_0_4_line_40 |  | 37 | 38 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_363-28_0_4_line_41 |  | 39 | 40 | 0.014259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_363-28_0_4_line_42 |  | 40 | 41 | 0.009709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_363-28_0_4_line_43 |  | 40 | 42 | 0.014977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_363-28_0_4_line_44 |  | 42 | 57 | 0.005552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_363-28_0_4_line_45 |  | 43 | 44 | 0.01103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_363-28_0_4_line_46 |  | 43 | 45 | 0.023856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_363-28_0_4_line_47 |  | 44 | 46 | 0.020089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_363-28_0_4_line_48 |  | 45 | 47 | 0.00086558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_363-28_0_4_line_49 |  | 46 | 57 | 0.018189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_363-28_0_4_line_50 |  | 48 | 79 | 0.017244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_363-28_0_4_line_51 |  | 48 | 53 | 0.010024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_363-28_0_4_line_52 |  | 49 | 50 | 0.022432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_363-28_0_4_line_53 |  | 49 | 51 | 0.014583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_363-28_0_4_line_54 |  | 50 | 83 | 0.016734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_363-28_0_4_line_55 |  | 52 | 80 | 0.022123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_363-28_0_4_line_56 |  | 54 | 55 | 0.020961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_363-28_0_4_line_57 |  | 54 | 56 | 0.00056981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_363-28_0_4_line_58 |  | 55 | 62 | 0.019744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_363-28_0_4_line_59 |  | 56 | 79 | 0.021565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_363-28_0_4_line_60 |  | 57 | 60 | 0.009076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_363-28_0_4_line_61 |  | 58 | 59 | 0.0014925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_363-28_0_4_line_62 |  | 58 | 60 | 0.013413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_363-28_0_4_line_63 |  | 60 | 61 | 0.009948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_363-28_0_4_line_64 |  | 62 | 63 | 0.010766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_363-28_0_4_line_65 |  | 63 | 91 | 0.010336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_363-28_0_4_line_66 |  | 63 | 87 | 0.011975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_363-28_0_4_line_67 |  | 64 | 65 | 2.7908e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_363-28_0_4_line_68 |  | 64 | 66 | 6.663e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_363-28_0_4_line_69 |  | 65 | 67 | 0.04766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_363-28_0_4_line_70 |  | 66 | 68 | 0.029361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_363-28_0_4_line_71 |  | 67 | 69 | 6.3938e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_363-28_0_4_line_72 |  | 68 | 70 | 7.081e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_363-28_0_4_line_73 |  | 69 | 71 | 7.2641e-07 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_363-28_0_4_line_74 |  | 70 | 72 | 4.1285e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_363-28_0_4_line_75 |  | 71 | 111 | 0.029346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_363-28_0_4_line_76 |  | 72 | 78 | 0.029337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_363-28_0_4_line_77 |  | 73 | 74 | 0.030147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_363-28_0_4_line_78 |  | 73 | 75 | 2.6274e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_363-28_0_4_line_79 |  | 74 | 76 | 2.2208e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_363-28_0_4_line_80 |  | 75 | 77 | 3.3721e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_363-28_0_4_line_81 |  | 76 | 78 | 6.8698e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_363-28_0_4_line_82 |  | 80 | 81 | 0.020502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_363-28_0_4_line_83 |  | 82 | 83 | 0.012791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_363-28_0_4_line_84 |  | 82 | 84 | 0.024843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_363-28_0_4_line_85 |  | 83 | 85 | 0.0247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_363-28_0_4_line_86 |  | 84 | 86 | 0.033999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_363-28_0_4_line_87 |  | 85 | 94 | 0.02624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_363-28_0_4_line_88 |  | 86 | 99 | 0.021111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_363-28_0_4_line_89 |  | 87 | 88 | 0.017516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_363-28_0_4_line_90 |  | 88 | 89 | 0.0069031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_363-28_0_4_line_91 |  | 88 | 90 | 0.010201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_363-28_0_4_line_92 |  | 89 | 92 | 0.0081406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
93 | LV_363-28_0_4_line_93 |  | 92 | 93 | 0.041632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_363-28_0_4_line_94 |  | 93 | 101 | 0.003026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_363-28_0_4_line_95 |  | 93 | 100 | 0.019507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_363-28_0_4_line_96 |  | 95 | 96 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_363-28_0_4_line_97 |  | 96 | 97 | 0.017567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_363-28_0_4_line_98 |  | 97 | 98 | 0.026952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_363-28_0_4_line_99 |  | 98 | 102 | 0.007986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_363-28_0_4_line_100 |  | 99 | 100 | 0.021401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_363-28_0_4_line_101 |  | 101 | 107 | 0.01127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_363-28_0_4_line_102 |  | 101 | 102 | 0.027994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_363-28_0_4_line_103 |  | 102 | 103 | 0.0086769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_363-28_0_4_line_104 |  | 103 | 108 | 0.015728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_363-28_0_4_line_105 |  | 104 | 105 | 0.039814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_363-28_0_4_line_106 |  | 104 | 106 | 0.014654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_363-28_0_4_line_107 |  | 105 | 109 | 7.5202e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_363-28_0_4_line_108 |  | 106 | 110 | 0.006209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_363-28_0_4_line_109 |  | 108 | 115 | 0.0060912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_363-28_0_4_line_110 |  | 109 | 116 | 2.1944e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_363-28_0_4_line_111 |  | 110 | 114 | 0.0060876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_363-28_0_4_line_112 |  | 111 | 112 | 4.7629e-08 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_363-28_0_4_line_113 |  | 112 | 113 | 2.4579e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_363-28_0_4_line_114 |  | 113 | 117 | 0.029354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_363-28_0_4_line_115 |  | 114 | 115 | 0.0060892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_363-28_0_4_line_116 |  | 116 | 119 | 0.030138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_363-28_0_4_line_117 |  | 117 | 118 | 5.199e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_363-28_0_4_line_118 |  | 118 | 119 | 6.4495e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_363-28_0_4_trafo_36 | 0.63 MVA 20/0.4 kV | 120 | 23 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2604471.4288 | 1200626.8498 | 2604440.5448 | 1200610.1181 | 2604436.5324 | 1200611.3158 | 2604430.1974 | 1200607.7605
1 | 2604471.4288 | 1200626.8498 | 2604501.1944 | 1200642.6803
2 | 2604471.4288 | 1200626.8498 | 2604475.2812 | 1200636.0576 | 2604475.7139 | 1200637.6476 | 2604475.9184 | 1200639.0041 | 2604475.8566 | 1200640.2269 | 2604475.6195 | 1200641.7942 | 2604474.8111 | 1200643.8614 | 2604446.618 | 1200693.9291
3 | 2604501.1944 | 1200642.6803 | 2604528.7177 | 1200593.4724
4 | 2604534.9445 | 1200582.3396 | 2604528.7177 | 1200593.4724
5 | 2604534.9445 | 1200582.3396 | 2604538.207 | 1200576.2388 | 2604553.9008 | 1200548.2244 | 2604558.1311 | 1200540.6679
6 | 2604583.9654 | 1200652.1251 | 2604582.8084 | 1200654.2054
7 | 2604583.9654 | 1200652.1251 | 2604606.0996 | 1200663.2923
8 | 2604583.9654 | 1200652.1251 | 2604596.7555 | 1200629.1147
9 | 2604631.4624 | 1200662.7336 | 2604606.0996 | 1200663.2923
10 | 2604606.0996 | 1200663.2923 | 2604610.0894 | 1200665.6898
11 | 2604596.7555 | 1200629.1147 | 2604609.8087 | 1200605.631
12 | 2604642.1475 | 1200684.9537 | 2604633.2979 | 1200679.6359
13 | 2604642.1475 | 1200684.9537 | 2604631.4624 | 1200662.7336
14 | 2604631.4624 | 1200662.7336 | 2604639.1203 | 1200649.9962
15 | 2604620.7045 | 1200586.0285 | 2604609.8087 | 1200605.631
16 | 2604639.4275 | 1200649.4852 | 2604639.1203 | 1200649.9962
17 | 2604620.7045 | 1200586.0285 | 2604624.661 | 1200588.2772 | 2604634.164 | 1200593.6874
18 | 2604481.3967 | 1200497.6766 | 2604473.7061 | 1200511.4894
19 | 2604481.3967 | 1200497.6766 | 2604483.6056 | 1200493.7032
20 | 2604481.3967 | 1200497.6766 | 2604501.3382 | 1200508.7638
21 | 2604501.3382 | 1200508.7638 | 2604505.8511 | 1200511.273
22 | 2604521.3202 | 1200519.8737 | 2604505.8511 | 1200511.273
23 | 2604558.1311 | 1200540.6679 | 2604573.2154 | 1200513.7092
24 | 2604558.1311 | 1200540.6679 | 2604540.6106 | 1200530.7707
25 | 2604573.2154 | 1200513.7092 | 2604588.0103 | 1200487.1172
26 | 2604573.2154 | 1200513.7092 | 2604592.7258 | 1200524.4963
27 | 2604539.0331 | 1200529.8796 | 2604540.6106 | 1200530.7707
28 | 2604521.3202 | 1200519.8737 | 2604539.0331 | 1200529.8796
29 | 2604509.4463 | 1200447.248 | 2604507.0695 | 1200451.5197
30 | 2604509.4463 | 1200447.248 | 2604516.7625 | 1200434.1025
31 | 2604509.4463 | 1200447.248 | 2604529.318 | 1200457.7562
32 | 2604509.9791 | 1200375.5766 | 2604505.3677 | 1200383.8442
33 | 2604505.3677 | 1200383.8442 | 2604518.2407 | 1200391.0481
34 | 2604535.3849 | 1200400.6423 | 2604518.2407 | 1200391.0481
35 | 2604588.0103 | 1200487.1172 | 2604570.567 | 1200478.1564
36 | 2604601.5048 | 1200529.3501 | 2604592.7258 | 1200524.4963
37 | 2604634.164 | 1200593.6874 | 2604646.2706 | 1200571.8363
38 | 2604516.7625 | 1200434.1025 | 2604526.4878 | 1200416.6283
39 | 2604535.3849 | 1200400.6423 | 2604544.6295 | 1200405.7539
40 | 2604535.3849 | 1200400.6423 | 2604526.4878 | 1200416.6283
41 | 2604557.1084 | 1200412.6539 | 2604544.6295 | 1200405.7539
42 | 2604561.7886 | 1200404.1417 | 2604557.1084 | 1200412.6539
43 | 2604557.1084 | 1200412.6539 | 2604570.1534 | 1200420.0119
44 | 2604574.9891 | 1200422.7395 | 2604570.1534 | 1200420.0119
45 | 2604551.1462 | 1200465.9003 | 2604556.4799 | 1200456.2452
46 | 2604551.1462 | 1200465.9003 | 2604564.3555 | 1200472.7139 | 2604563.5853 | 1200474.5698 | 2604569.7971 | 1200477.7609
47 | 2604566.1939 | 1200438.6608 | 2604556.4799 | 1200456.2452
48 | 2604570.567 | 1200478.1564 | 2604569.7971 | 1200477.7609
49 | 2604574.9891 | 1200422.7395 | 2604566.1939 | 1200438.6608
50 | 2604601.5048 | 1200529.3501 | 2604609.8328 | 1200514.2506
51 | 2604601.5048 | 1200529.3501 | 2604610.2403 | 1200534.2662
52 | 2604646.9416 | 1200636.9871 | 2604659.295 | 1200637.7192 | 2604662.1962 | 1200636.2762 | 2604666.3342 | 1200630.8588
53 | 2604646.9416 | 1200636.9871 | 2604639.4275 | 1200649.4852
54 | 2604675.6991 | 1200617.0429 | 2604672.6349 | 1200622.6102 | 2604666.3342 | 1200630.8588
55 | 2604646.2706 | 1200571.8363 | 2604656.9922 | 1200552.4848
56 | 2604620.5228 | 1200494.8683 | 2604630.7244 | 1200476.5568
57 | 2604620.2476 | 1200495.3672 | 2604620.5228 | 1200494.8683
58 | 2604640.3335 | 1200459.3087 | 2604630.7244 | 1200476.5568
59 | 2604609.8328 | 1200514.2506 | 2604620.2476 | 1200495.3672
60 | 2604574.9891 | 1200422.7395 | 2604582.9633 | 1200427.1145
61 | 2604594.7246 | 1200433.5636 | 2604596.0333 | 1200434.2811
62 | 2604582.9633 | 1200427.1145 | 2604594.7246 | 1200433.5636
63 | 2604587.8568 | 1200418.4469 | 2604582.9633 | 1200427.1145
64 | 2604640.3335 | 1200459.3087 | 2604649.7761 | 1200464.5299
65 | 2604654.7689 | 1200455.4733 | 2604649.7761 | 1200464.5299
66 | 2604649.7761 | 1200464.5299 | 2604660.2531 | 1200470.3298
67 | 2604625.9021 | 1200380.443 | 2604625.8997 | 1200380.4416
68 | 2604625.8997 | 1200380.4416 | 2604625.8991 | 1200380.4413
69 | 2604667.5434 | 1200403.6269 | 2604625.9021 | 1200380.443
70 | 2604625.8991 | 1200380.4413 | 2604600.2459 | 1200366.1588
71 | 2604667.544 | 1200403.6272 | 2604667.5434 | 1200403.6269
72 | 2604600.2459 | 1200366.1588 | 2604600.2453 | 1200366.1585
73 | 2604667.5446 | 1200403.6275 | 2604667.544 | 1200403.6272
74 | 2604600.2453 | 1200366.1585 | 2604600.2417 | 1200366.1565
75 | 2604693.1849 | 1200417.9028 | 2604667.5446 | 1200403.6275
76 | 2604600.2417 | 1200366.1565 | 2604574.6099 | 1200351.8859
77 | 2604548.2624 | 1200337.2169 | 2604574.602 | 1200351.8815
78 | 2604548.2624 | 1200337.2169 | 2604548.2601 | 1200337.2156
79 | 2604574.6039 | 1200351.8826 | 2604574.602 | 1200351.8815
80 | 2604548.2601 | 1200337.2156 | 2604548.2571 | 1200337.2139
81 | 2604574.6099 | 1200351.8859 | 2604574.6039 | 1200351.8826
82 | 2604656.9922 | 1200552.4848 | 2604666.928 | 1200534.5517
83 | 2604664.5679 | 1200610.6865 | 2604675.6991 | 1200617.0429
84 | 2604664.5679 | 1200610.6865 | 2604676.6873 | 1200588.9999
85 | 2604697.3302 | 1200629.0772 | 2604675.6991 | 1200617.0429
86 | 2604676.6873 | 1200588.9999 | 2604693.2733 | 1200559.3209
87 | 2604697.3302 | 1200629.0772 | 2604710.0062 | 1200606.1019
88 | 2604705.0322 | 1200542.3032 | 2604701.6356 | 1200544.3572 | 2604693.2733 | 1200559.3209
89 | 2604675.5774 | 1200478.813 | 2604660.2531 | 1200470.3298
90 | 2604675.5774 | 1200478.813 | 2604681.5947 | 1200482.196
91 | 2604680.3038 | 1200469.7673 | 2604675.5774 | 1200478.813
92 | 2604681.5947 | 1200482.196 | 2604688.6907 | 1200486.1856
93 | 2604724.9804 | 1200506.5884 | 2604688.6907 | 1200486.1856
94 | 2604727.6206 | 1200508.0801 | 2604724.9804 | 1200506.5884
95 | 2604724.9804 | 1200506.5884 | 2604715.4682 | 1200523.6187
96 | 2604735.7709 | 1200559.403 | 2604727.167 | 1200574.9977
97 | 2604735.7709 | 1200559.403 | 2604744.3974 | 1200544.0998
98 | 2604757.6323 | 1200520.6215 | 2604744.3974 | 1200544.0998
99 | 2604757.6323 | 1200520.6215 | 2604750.6857 | 1200516.6472
100 | 2604705.0322 | 1200542.3032 | 2604715.4682 | 1200523.6187
101 | 2604727.6206 | 1200508.0801 | 2604733.0556 | 1200498.2013
102 | 2604727.6206 | 1200508.0801 | 2604748.841 | 1200519.9142 | 2604750.6857 | 1200516.6472
103 | 2604750.6857 | 1200516.6472 | 2604754.8097 | 1200509.013
104 | 2604754.8097 | 1200509.013 | 2604754.8097 | 1200509.013 | 2604757.6478 | 1200510.5605 | 2604758.471 | 1200509.0937 | 2604756.6982 | 1200508.1029 | 2604760.9641 | 1200500.4257
105 | 2604779.9705 | 1200466.2209 | 2604745.1849 | 1200446.8539
106 | 2604779.9705 | 1200466.2209 | 2604772.853 | 1200479.0299
107 | 2604745.1849 | 1200446.8539 | 2604745.1783 | 1200446.8503
108 | 2604772.853 | 1200479.0299 | 2604769.8372 | 1200484.4573
109 | 2604760.9641 | 1200500.4257 | 2604763.9227 | 1200495.1013
110 | 2604745.1783 | 1200446.8503 | 2604745.1764 | 1200446.8492
111 | 2604766.8804 | 1200489.7786 | 2604769.8372 | 1200484.4573
112 | 2604693.185 | 1200417.9028 | 2604693.1849 | 1200417.9028
113 | 2604693.1871 | 1200417.904 | 2604693.185 | 1200417.9028
114 | 2604718.834 | 1200432.183 | 2604693.1871 | 1200417.904
115 | 2604763.9227 | 1200495.1013 | 2604766.8804 | 1200489.7786
116 | 2604745.1764 | 1200446.8492 | 2604718.8442 | 1200432.1887
117 | 2604718.8385 | 1200432.1855 | 2604718.834 | 1200432.183
118 | 2604718.8442 | 1200432.1887 | 2604718.8385 | 1200432.1855

## bus_geodata
| x | y | coords
0 | 2604430.1974 | 1200607.7605
1 | 2604471.4288 | 1200626.8498
2 | 2604501.1944 | 1200642.6803
3 | 2604446.618 | 1200693.9291
4 | 2604528.7177 | 1200593.4724
5 | 2604534.9445 | 1200582.3396
6 | 2604582.8084 | 1200654.2054
7 | 2604583.9654 | 1200652.1251
8 | 2604606.0996 | 1200663.2923
9 | 2604596.7555 | 1200629.1147
10 | 2604642.1475 | 1200684.9537
11 | 2604633.2979 | 1200679.6359
12 | 2604631.4624 | 1200662.7336
13 | 2604610.0894 | 1200665.6898
14 | 2604609.8087 | 1200605.631
15 | 2604639.1203 | 1200649.9962
16 | 2604620.7045 | 1200586.0285
17 | 2604473.7061 | 1200511.4894
18 | 2604481.3967 | 1200497.6766
19 | 2604483.6056 | 1200493.7032
20 | 2604501.3382 | 1200508.7638
21 | 2604505.8511 | 1200511.273
22 | 2604558.1311 | 1200540.6679
23 | 2604573.2154 | 1200513.7092
24 | 2604540.6106 | 1200530.7707
25 | 2604521.3202 | 1200519.8737
26 | 2604507.0695 | 1200451.5197
27 | 2604509.4463 | 1200447.248
28 | 2604505.3677 | 1200383.8442
29 | 2604509.9791 | 1200375.5766
30 | 2604518.2407 | 1200391.0481
31 | 2604588.0103 | 1200487.1172
32 | 2604592.7258 | 1200524.4963
33 | 2604634.164 | 1200593.6874
34 | 2604539.0331 | 1200529.8796
35 | 2604516.7625 | 1200434.1025
36 | 2604529.318 | 1200457.7562
37 | 2604535.3849 | 1200400.6423
38 | 2604526.4878 | 1200416.6283
39 | 2604544.6295 | 1200405.7539
40 | 2604557.1084 | 1200412.6539
41 | 2604561.7886 | 1200404.1417
42 | 2604570.1534 | 1200420.0119
43 | 2604551.1462 | 1200465.9003
44 | 2604556.4799 | 1200456.2452
45 | 2604569.7971 | 1200477.7609
46 | 2604566.1939 | 1200438.6608
47 | 2604570.567 | 1200478.1564
48 | 2604601.5048 | 1200529.3501
49 | 2604646.9416 | 1200636.9871
50 | 2604666.3342 | 1200630.8588
51 | 2604639.4275 | 1200649.4852
52 | 2604646.2706 | 1200571.8363
53 | 2604610.2403 | 1200534.2662
54 | 2604620.5228 | 1200494.8683
55 | 2604630.7244 | 1200476.5568
56 | 2604620.2476 | 1200495.3672
57 | 2604574.9891 | 1200422.7395
58 | 2604594.7246 | 1200433.5636
59 | 2604596.0333 | 1200434.2811
60 | 2604582.9633 | 1200427.1145
61 | 2604587.8568 | 1200418.4469
62 | 2604640.3335 | 1200459.3087
63 | 2604649.7761 | 1200464.5299
64 | 2604625.8997 | 1200380.4416
65 | 2604625.9021 | 1200380.443
66 | 2604625.8991 | 1200380.4413
67 | 2604667.5434 | 1200403.6269
68 | 2604600.2459 | 1200366.1588
69 | 2604667.544 | 1200403.6272
70 | 2604600.2453 | 1200366.1585
71 | 2604667.5446 | 1200403.6275
72 | 2604600.2417 | 1200366.1565
73 | 2604548.2624 | 1200337.2169
74 | 2604574.602 | 1200351.8815
75 | 2604548.2601 | 1200337.2156
76 | 2604574.6039 | 1200351.8826
77 | 2604548.2572 | 1200337.2139
78 | 2604574.6099 | 1200351.8859
79 | 2604609.8328 | 1200514.2506
80 | 2604656.9922 | 1200552.4848
81 | 2604666.928 | 1200534.5517
82 | 2604664.5679 | 1200610.6865
83 | 2604675.6991 | 1200617.0429
84 | 2604676.6873 | 1200588.9999
85 | 2604697.3302 | 1200629.0772
86 | 2604693.2733 | 1200559.3209
87 | 2604660.2531 | 1200470.3298
88 | 2604675.5774 | 1200478.813
89 | 2604681.5947 | 1200482.196
90 | 2604680.3038 | 1200469.7673
91 | 2604654.7689 | 1200455.4733
92 | 2604688.6907 | 1200486.1856
93 | 2604724.9804 | 1200506.5884
94 | 2604710.0062 | 1200606.1019
95 | 2604727.167 | 1200574.9977
96 | 2604735.7709 | 1200559.403
97 | 2604744.3974 | 1200544.0998
98 | 2604757.6323 | 1200520.6215
99 | 2604705.0322 | 1200542.3032
100 | 2604715.4682 | 1200523.6187
101 | 2604727.6206 | 1200508.0801
102 | 2604750.6857 | 1200516.6472
103 | 2604754.8097 | 1200509.013
104 | 2604779.9705 | 1200466.2209
105 | 2604745.1849 | 1200446.8539
106 | 2604772.853 | 1200479.0299
107 | 2604733.0556 | 1200498.2013
108 | 2604760.9641 | 1200500.4257
109 | 2604745.1783 | 1200446.8503
110 | 2604769.8372 | 1200484.4573
111 | 2604693.1849 | 1200417.9028
112 | 2604693.185 | 1200417.9028
113 | 2604693.1871 | 1200417.904
114 | 2604766.8804 | 1200489.7786
115 | 2604763.9227 | 1200495.1013
116 | 2604745.1764 | 1200446.8492
117 | 2604718.834 | 1200432.183
118 | 2604718.8385 | 1200432.1855
119 | 2604718.8442 | 1200432.1887
120 | 2604588.0103 | 1200487.1172

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1