## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4005-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4005-6_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4005-6_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4005-6_0_5_node_94 | 0.4 | n |  | TRUE
4 | bus_LV_4005-6_0_5_node_95 | 0.4 | n |  | TRUE
5 | bus_LV_4005-6_0_5_node_92 | 0.4 | n |  | TRUE
6 | bus_LV_4005-6_0_5_node_99 | 0.4 | n |  | TRUE
7 | bus_LV_4005-6_0_5_node_90 | 0.4 | n |  | TRUE
8 | bus_LV_4005-6_0_5_node_100 | 0.4 | n |  | TRUE
9 | bus_LV_4005-6_0_5_node_91 | 0.4 | n |  | TRUE
10 | bus_LV_4005-6_0_5_node_3 | 0.4 | n |  | TRUE
11 | bus_LV_4005-6_0_5_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_4005-6_0_5_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_4005-6_0_5_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_4005-6_0_5_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_4005-6_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_4005-6_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_4005-6_0_5_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_4005-6_0_5_node_62 | 0.4 | n |  | TRUE
19 | bus_LV_4005-6_0_5_node_78 | 0.4 | n |  | TRUE
20 | bus_LV_4005-6_0_5_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_4005-6_0_5_node_76 | 0.4 | n |  | TRUE
22 | bus_LV_4005-6_0_5_node_130 | 0.4 | n |  | TRUE
23 | bus_LV_4005-6_0_5_node_136 | 0.4 | n |  | TRUE
24 | bus_LV_4005-6_0_5_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_4005-6_0_5_node_63 | 0.4 | n |  | TRUE
26 | bus_LV_4005-6_0_5_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_4005-6_0_5_node_77 | 0.4 | n |  | TRUE
28 | bus_LV_4005-6_0_5_node_128 | 0.4 | n |  | TRUE
29 | bus_LV_4005-6_0_5_node_137 | 0.4 | n |  | TRUE
30 | bus_LV_4005-6_0_5_node_135 | 0.4 | n |  | TRUE
31 | bus_LV_4005-6_0_5_node_79 | 0.4 | n |  | TRUE
32 | bus_LV_4005-6_0_5_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_4005-6_0_5_node_109 | 0.4 | n |  | TRUE
34 | bus_LV_4005-6_0_5_node_179 | 0.4 | n |  | TRUE
35 | bus_LV_4005-6_0_5_node_80 | 0.4 | n |  | TRUE
36 | bus_LV_4005-6_0_5_node_178 | 0.4 | n |  | TRUE
37 | bus_LV_4005-6_0_5_node_107 | 0.4 | n |  | TRUE
38 | bus_LV_4005-6_0_5_node_61 | 0.4 | n |  | TRUE
39 | bus_LV_4005-6_0_5_node_15 | 0.4 | n |  | TRUE
40 | bus_LV_4005-6_0_5_node_16 | 0.4 | n |  | TRUE
41 | bus_LV_4005-6_0_5_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_4005-6_0_5_node_17 | 0.4 | n |  | TRUE
43 | bus_LV_4005-6_0_5_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_4005-6_0_5_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_4005-6_0_5_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_4005-6_0_5_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_4005-6_0_5_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_4005-6_0_5_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_4005-6_0_5_node_27 | 0.4 | n |  | TRUE
50 | bus_LV_4005-6_0_5_node_25 | 0.4 | n |  | TRUE
51 | bus_LV_4005-6_0_5_node_26 | 0.4 | n |  | TRUE
52 | bus_LV_4005-6_0_5_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_4005-6_0_5_node_30 | 0.4 | n |  | TRUE
54 | bus_LV_4005-6_0_5_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_4005-6_0_5_node_67 | 0.4 | n |  | TRUE
56 | bus_LV_4005-6_0_5_node_65 | 0.4 | n |  | TRUE
57 | bus_LV_4005-6_0_5_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_4005-6_0_5_node_64 | 0.4 | n |  | TRUE
59 | bus_LV_4005-6_0_5_node_68 | 0.4 | n |  | TRUE
60 | bus_LV_4005-6_0_5_node_41 | 0.4 | n |  | TRUE
61 | bus_LV_4005-6_0_5_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_4005-6_0_5_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_4005-6_0_5_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_4005-6_0_5_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_4005-6_0_5_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_4005-6_0_5_node_148 | 0.4 | n |  | TRUE
67 | bus_LV_4005-6_0_5_node_146 | 0.4 | n |  | TRUE
68 | bus_LV_4005-6_0_5_node_34 | 0.4 | n |  | TRUE
69 | bus_LV_4005-6_0_5_node_35 | 0.4 | n |  | TRUE
70 | bus_LV_4005-6_0_5_node_151 | 0.4 | n |  | TRUE
71 | bus_LV_4005-6_0_5_node_147 | 0.4 | n |  | TRUE
72 | bus_LV_4005-6_0_5_node_38 | 0.4 | n |  | TRUE
73 | bus_LV_4005-6_0_5_node_39 | 0.4 | n |  | TRUE
74 | bus_LV_4005-6_0_5_node_40 | 0.4 | n |  | TRUE
75 | bus_LV_4005-6_0_5_node_42 | 0.4 | n |  | TRUE
76 | bus_LV_4005-6_0_5_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_4005-6_0_5_node_43 | 0.4 | n |  | TRUE
78 | bus_LV_4005-6_0_5_node_44 | 0.4 | n |  | TRUE
79 | bus_LV_4005-6_0_5_node_45 | 0.4 | n |  | TRUE
80 | bus_LV_4005-6_0_5_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_4005-6_0_5_node_108 | 0.4 | n |  | TRUE
82 | bus_LV_4005-6_0_5_node_49 | 0.4 | n |  | TRUE
83 | bus_LV_4005-6_0_5_node_47 | 0.4 | n |  | TRUE
84 | bus_LV_4005-6_0_5_node_48 | 0.4 | n |  | TRUE
85 | bus_LV_4005-6_0_5_node_50 | 0.4 | n |  | TRUE
86 | bus_LV_4005-6_0_5_node_51 | 0.4 | n |  | TRUE
87 | bus_LV_4005-6_0_5_node_53 | 0.4 | n |  | TRUE
88 | bus_LV_4005-6_0_5_node_54 | 0.4 | n |  | TRUE
89 | bus_LV_4005-6_0_5_node_55 | 0.4 | n |  | TRUE
90 | bus_LV_4005-6_0_5_node_59 | 0.4 | n |  | TRUE
91 | bus_LV_4005-6_0_5_node_57 | 0.4 | n |  | TRUE
92 | bus_LV_4005-6_0_5_node_106 | 0.4 | n |  | TRUE
93 | bus_LV_4005-6_0_5_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_4005-6_0_5_node_93 | 0.4 | n |  | TRUE
95 | bus_LV_4005-6_0_5_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_4005-6_0_5_node_96 | 0.4 | n |  | TRUE
97 | bus_LV_4005-6_0_5_node_60 | 0.4 | n |  | TRUE
98 | bus_LV_4005-6_0_5_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_4005-6_0_5_node_114 | 0.4 | n |  | TRUE
100 | bus_LV_4005-6_0_5_node_120 | 0.4 | n |  | TRUE
101 | bus_LV_4005-6_0_5_node_112 | 0.4 | n |  | TRUE
102 | bus_LV_4005-6_0_5_node_115 | 0.4 | n |  | TRUE
103 | bus_LV_4005-6_0_5_node_116 | 0.4 | n |  | TRUE
104 | bus_LV_4005-6_0_5_node_117 | 0.4 | n |  | TRUE
105 | bus_LV_4005-6_0_5_node_119 | 0.4 | n |  | TRUE
106 | bus_LV_4005-6_0_5_node_121 | 0.4 | n |  | TRUE
107 | bus_LV_4005-6_0_5_node_97 | 0.4 | n |  | TRUE
108 | bus_LV_4005-6_0_5_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_4005-6_0_5_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_4005-6_0_5_node_66 | 0.4 | n |  | TRUE
111 | bus_LV_4005-6_0_5_node_165 | 0.4 | n |  | TRUE
112 | bus_LV_4005-6_0_5_node_166 | 0.4 | n |  | TRUE
113 | bus_LV_4005-6_0_5_node_164 | 0.4 | n |  | TRUE
114 | bus_LV_4005-6_0_5_node_69 | 0.4 | n |  | TRUE
115 | bus_LV_4005-6_0_5_node_70 | 0.4 | n |  | TRUE
116 | bus_LV_4005-6_0_5_node_71 | 0.4 | n |  | TRUE
117 | bus_LV_4005-6_0_5_node_73 | 0.4 | n |  | TRUE
118 | bus_LV_4005-6_0_5_node_74 | 0.4 | n |  | TRUE
119 | bus_LV_4005-6_0_5_node_72 | 0.4 | n |  | TRUE
120 | bus_LV_4005-6_0_5_node_132 | 0.4 | n |  | TRUE
121 | bus_LV_4005-6_0_5_node_131 | 0.4 | n |  | TRUE
122 | bus_LV_4005-6_0_5_node_75 | 0.4 | n |  | TRUE
123 | bus_LV_4005-6_0_5_node_133 | 0.4 | n |  | TRUE
124 | bus_LV_4005-6_0_5_node_173 | 0.4 | n |  | TRUE
125 | bus_LV_4005-6_0_5_node_171 | 0.4 | n |  | TRUE
126 | bus_LV_4005-6_0_5_node_81 | 0.4 | n |  | TRUE
127 | bus_LV_4005-6_0_5_node_82 | 0.4 | n |  | TRUE
128 | bus_LV_4005-6_0_5_node_83 | 0.4 | n |  | TRUE
129 | bus_LV_4005-6_0_5_node_87 | 0.4 | n |  | TRUE
130 | bus_LV_4005-6_0_5_node_85 | 0.4 | n |  | TRUE
131 | bus_LV_4005-6_0_5_node_86 | 0.4 | n |  | TRUE
132 | bus_LV_4005-6_0_5_node_88 | 0.4 | n |  | TRUE
133 | bus_LV_4005-6_0_5_node_101 | 0.4 | n |  | TRUE
134 | bus_LV_4005-6_0_5_node_104 | 0.4 | n |  | TRUE
135 | bus_LV_4005-6_0_5_node_102 | 0.4 | n |  | TRUE
136 | bus_LV_4005-6_0_5_node_122 | 0.4 | n |  | TRUE
137 | bus_LV_4005-6_0_5_node_111 | 0.4 | n |  | TRUE
138 | bus_LV_4005-6_0_5_node_113 | 0.4 | n |  | TRUE
139 | bus_LV_4005-6_0_5_node_103 | 0.4 | n |  | TRUE
140 | bus_LV_4005-6_0_5_node_123 | 0.4 | n |  | TRUE
141 | bus_LV_4005-6_0_5_node_118 | 0.4 | n |  | TRUE
142 | bus_LV_4005-6_0_5_node_124 | 0.4 | n |  | TRUE
143 | bus_LV_4005-6_0_5_node_125 | 0.4 | n |  | TRUE
144 | bus_LV_4005-6_0_5_node_126 | 0.4 | n |  | TRUE
145 | bus_LV_4005-6_0_5_node_127 | 0.4 | n |  | TRUE
146 | bus_LV_4005-6_0_5_node_138 | 0.4 | n |  | TRUE
147 | bus_LV_4005-6_0_5_node_129 | 0.4 | n |  | TRUE
148 | bus_LV_4005-6_0_5_node_142 | 0.4 | n |  | TRUE
149 | bus_LV_4005-6_0_5_node_176 | 0.4 | n |  | TRUE
150 | bus_LV_4005-6_0_5_node_170 | 0.4 | n |  | TRUE
151 | bus_LV_4005-6_0_5_node_134 | 0.4 | n |  | TRUE
152 | bus_LV_4005-6_0_5_node_141 | 0.4 | n |  | TRUE
153 | bus_LV_4005-6_0_5_node_140 | 0.4 | n |  | TRUE
154 | bus_LV_4005-6_0_5_node_143 | 0.4 | n |  | TRUE
155 | bus_LV_4005-6_0_5_node_180 | 0.4 | n |  | TRUE
156 | bus_LV_4005-6_0_5_node_139 | 0.4 | n |  | TRUE
157 | bus_LV_4005-6_0_5_node_152 | 0.4 | n |  | TRUE
158 | bus_LV_4005-6_0_5_node_149 | 0.4 | n |  | TRUE
159 | bus_LV_4005-6_0_5_node_150 | 0.4 | n |  | TRUE
160 | bus_LV_4005-6_0_5_node_157 | 0.4 | n |  | TRUE
161 | bus_LV_4005-6_0_5_node_156 | 0.4 | n |  | TRUE
162 | bus_LV_4005-6_0_5_node_153 | 0.4 | n |  | TRUE
163 | bus_LV_4005-6_0_5_node_154 | 0.4 | n |  | TRUE
164 | bus_LV_4005-6_0_5_node_155 | 0.4 | n |  | TRUE
165 | bus_LV_4005-6_0_5_node_158 | 0.4 | n |  | TRUE
166 | bus_LV_4005-6_0_5_node_163 | 0.4 | n |  | TRUE
167 | bus_LV_4005-6_0_5_node_159 | 0.4 | n |  | TRUE
168 | bus_LV_4005-6_0_5_node_160 | 0.4 | n |  | TRUE
169 | bus_LV_4005-6_0_5_node_161 | 0.4 | n |  | TRUE
170 | bus_LV_4005-6_0_5_node_162 | 0.4 | n |  | TRUE
171 | bus_LV_4005-6_0_5_node_167 | 0.4 | n |  | TRUE
172 | bus_LV_4005-6_0_5_node_168 | 0.4 | n |  | TRUE
173 | bus_LV_4005-6_0_5_node_169 | 0.4 | n |  | TRUE
174 | bus_LV_4005-6_0_5_node_172 | 0.4 | n |  | TRUE
175 | bus_LV_4005-6_0_5_node_174 | 0.4 | n |  | TRUE
176 | bus_LV_4005-6_0_5_node_175 | 0.4 | n |  | TRUE
177 | bus_LV_4005-6_0_5_node_177 | 0.4 | n |  | TRUE
178 | bus_MV_390_0_node_64 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4005-6_0_5_load_0 | 0 | 0.0011487 | 0.00028788 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4005-6_0_5_load_1 | 1 | 0.00051703 | 0.00012958 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4005-6_0_5_load_2 | 2 | 0.0018775 | 0.00047056 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4005-6_0_5_load_94 | 3 | 0.002752 | 0.00068972 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4005-6_0_5_load_95 | 4 | 0.0055952 | 0.0014023 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4005-6_0_5_load_92 | 5 | 0.00078973 | 0.00019793 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4005-6_0_5_load_99 | 6 | 0.0010965 | 0.00027481 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4005-6_0_5_load_90 | 7 | 0.0034755 | 0.00087104 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4005-6_0_5_load_91 | 9 | 0.00080439 | 0.0002016 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4005-6_0_5_load_3 | 10 | 0.0023128 | 0.00057965 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4005-6_0_5_load_9 | 16 | 0.0044686 | 0.0011199 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4005-6_0_5_load_62 | 18 | 0.0042486 | 0.0010648 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4005-6_0_5_load_78 | 19 | 0.001312 | 0.00032881 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4005-6_0_5_load_76 | 21 | 0.011348 | 0.0028441 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4005-6_0_5_load_130 | 22 | 0.001424 | 0.00035688 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4005-6_0_5_load_10 | 24 | 0.0035238 | 0.00088314 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4005-6_0_5_load_63 | 25 | 0.00030421 | 7.6243e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4005-6_0_5_load_77 | 27 | 0.0012426 | 0.00031142 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4005-6_0_5_load_128 | 28 | 0.0013428 | 0.00033653 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4005-6_0_5_load_135 | 30 | 0.00089736 | 0.0002249 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4005-6_0_5_load_79 | 31 | 0.0099118 | 0.0024841 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4005-6_0_5_load_179 | 34 | 0.0026184 | 0.00065624 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4005-6_0_5_load_178 | 36 | 0.0020441 | 0.00051229 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4005-6_0_5_load_15 | 39 | 0.010274 | 0.002575 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4005-6_0_5_load_16 | 40 | 0.0070526 | 0.0017675 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4005-6_0_5_load_19 | 43 | 0.0087968 | 0.0022047 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4005-6_0_5_load_29 | 48 | 0.0014235 | 0.00035676 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4005-6_0_5_load_27 | 49 | 0.0021247 | 0.0005325 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4005-6_0_5_load_25 | 50 | 0.0063456 | 0.0015904 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4005-6_0_5_load_26 | 51 | 0.0073038 | 0.0018305 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4005-6_0_5_load_30 | 53 | 0.0036666 | 0.00091893 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4005-6_0_5_load_28 | 54 | 0.0013034 | 0.00032666 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4005-6_0_5_load_36 | 57 | 0.0020998 | 0.00052627 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4005-6_0_5_load_64 | 58 | 0.016432 | 0.0041184 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4005-6_0_5_load_68 | 59 | 0.0038034 | 0.00095323 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4005-6_0_5_load_33 | 63 | 0.003542 | 0.0008877 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4005-6_0_5_load_56 | 65 | 0.0022878 | 0.00057337 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4005-6_0_5_load_148 | 66 | 0.0027532 | 0.00069001 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4005-6_0_5_load_146 | 67 | 0.0010005 | 0.00025075 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4005-6_0_5_load_34 | 68 | 0.0043073 | 0.0010795 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4005-6_0_5_load_35 | 69 | 0.0020109 | 0.00050397 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4005-6_0_5_load_147 | 71 | 0.0090002 | 0.0022557 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4005-6_0_5_load_38 | 72 | 0.0015366 | 0.00038511 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4005-6_0_5_load_40 | 74 | 0.0034991 | 0.00087695 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4005-6_0_5_load_46 | 76 | 0.0034671 | 0.00086893 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4005-6_0_5_load_43 | 77 | 0.0027085 | 0.00067881 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4005-6_0_5_load_44 | 78 | 0.0035975 | 0.00090163 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4005-6_0_5_load_45 | 79 | 0.001503 | 0.00037669 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4005-6_0_5_load_108 | 81 | 0.00051185 | 0.00012828 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4005-6_0_5_load_47 | 83 | 0.0010434 | 0.00026149 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4005-6_0_5_load_48 | 84 | 0.0018302 | 0.0004587 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4005-6_0_5_load_50 | 85 | 0.0020761 | 0.00052032 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4005-6_0_5_load_51 | 86 | 0.0040781 | 0.0010221 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4005-6_0_5_load_54 | 88 | 0.0038981 | 0.00097697 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4005-6_0_5_load_55 | 89 | 0.0055573 | 0.0013928 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4005-6_0_5_load_57 | 91 | 0.0097311 | 0.0024388 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4005-6_0_5_load_106 | 92 | 0.0013838 | 0.0003468 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4005-6_0_5_load_89 | 93 | 0.0033932 | 0.00085042 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4005-6_0_5_load_96 | 96 | 0.0019599 | 0.0004912 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4005-6_0_5_load_60 | 97 | 0.0039 | 0.00097743 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4005-6_0_5_load_98 | 98 | 0.0022966 | 0.00057559 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4005-6_0_5_load_114 | 99 | 0.0020853 | 0.00052262 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4005-6_0_5_load_115 | 102 | 0.0010202 | 0.00025569 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4005-6_0_5_load_116 | 103 | 0.0019921 | 0.00049926 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4005-6_0_5_load_119 | 105 | 0.001154 | 0.00028921 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4005-6_0_5_load_121 | 106 | 0.0023755 | 0.00059536 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4005-6_0_5_load_97 | 107 | 0.007508 | 0.0018817 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4005-6_0_5_load_110 | 108 | 0.0031323 | 0.00078502 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4005-6_0_5_load_105 | 109 | 0.0016546 | 0.00041467 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4005-6_0_5_load_66 | 110 | 0.0019902 | 0.00049879 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4005-6_0_5_load_166 | 112 | 0.002749 | 0.00068897 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4005-6_0_5_load_69 | 114 | 0.017753 | 0.0044493 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4005-6_0_5_load_74 | 118 | 0.0096387 | 0.0024157 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4005-6_0_5_load_132 | 120 | 0.0043337 | 0.0010861 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4005-6_0_5_load_131 | 121 | 0.0031873 | 0.00079881 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4005-6_0_5_load_173 | 124 | 0.0016843 | 0.00042213 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4005-6_0_5_load_171 | 125 | 0.00073778 | 0.0001849 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4005-6_0_5_load_81 | 126 | 0.0014314 | 0.00035874 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4005-6_0_5_load_82 | 127 | 0.00097751 | 0.00024499 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4005-6_0_5_load_83 | 128 | 0.0027401 | 0.00068672 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4005-6_0_5_load_87 | 129 | 0.0027023 | 0.00067727 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4005-6_0_5_load_85 | 130 | 0.0014182 | 0.00035542 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4005-6_0_5_load_86 | 131 | 0.0040447 | 0.0010137 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4005-6_0_5_load_88 | 132 | 0.00099328 | 0.00024894 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4005-6_0_5_load_101 | 133 | 0.00062584 | 0.00015685 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4005-6_0_5_load_104 | 134 | 0.00071128 | 0.00017826 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4005-6_0_5_load_102 | 135 | 0.0017796 | 0.00044601 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4005-6_0_5_load_122 | 136 | 0.0017875 | 0.000448 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4005-6_0_5_load_111 | 137 | 0.0040459 | 0.001014 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4005-6_0_5_load_113 | 138 | 0.0026553 | 0.00066548 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4005-6_0_5_load_103 | 139 | 0.0007844 | 0.00019659 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4005-6_0_5_load_123 | 140 | 0.0039078 | 0.00097939 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4005-6_0_5_load_118 | 141 | 0.0030331 | 0.00076017 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4005-6_0_5_load_124 | 142 | 0.027491 | 0.00689 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4005-6_0_5_load_125 | 143 | 0.01209 | 0.0030302 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4005-6_0_5_load_126 | 144 | 0.0055575 | 0.0013928 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4005-6_0_5_load_138 | 146 | 0.0009099 | 0.00022804 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4005-6_0_5_load_129 | 147 | 0.0022015 | 0.00055175 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4005-6_0_5_load_142 | 148 | 0.008962 | 0.0022461 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4005-6_0_5_load_176 | 149 | 0.0023077 | 0.00057838 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4005-6_0_5_load_134 | 151 | 0.00078159 | 0.00019589 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4005-6_0_5_load_141 | 152 | 0.00090607 | 0.00022708 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4005-6_0_5_load_143 | 154 | 0.026305 | 0.0065926 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4005-6_0_5_load_180 | 155 | 0.0033855 | 0.0008485 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4005-6_0_5_load_139 | 156 | 0.0020636 | 0.00051718 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4005-6_0_5_load_152 | 157 | 0.0067261 | 0.0016857 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4005-6_0_5_load_149 | 158 | 0.0028285 | 0.00070888 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4005-6_0_5_load_150 | 159 | 0.0029811 | 0.00074712 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4005-6_0_5_load_157 | 160 | 0.0020271 | 0.00050804 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4005-6_0_5_load_153 | 162 | 0.0016157 | 0.00040493 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4005-6_0_5_load_154 | 163 | 0.0018879 | 0.00047316 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4005-6_0_5_load_155 | 164 | 0.001287 | 0.00032254 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4005-6_0_5_load_158 | 165 | 0.0012799 | 0.00032077 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4005-6_0_5_load_163 | 166 | 0.001158 | 0.00029023 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4005-6_0_5_load_159 | 167 | 0.001158 | 0.00029023 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4005-6_0_5_load_160 | 168 | 0.00090493 | 0.0002268 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4005-6_0_5_load_161 | 169 | 0.00090505 | 0.00022683 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4005-6_0_5_load_162 | 170 | 0.0055869 | 0.0014002 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4005-6_0_5_load_167 | 171 | 0.0024016 | 0.00060189 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4005-6_0_5_load_168 | 172 | 0.0036481 | 0.0009143 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4005-6_0_5_load_169 | 173 | 0.001899 | 0.00047593 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4005-6_0_5_load_172 | 174 | 0.0023662 | 0.00059301 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4005-6_0_5_load_174 | 175 | 0.0014839 | 0.00037189 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4005-6_0_5_load_175 | 176 | 0.0020758 | 0.00052023 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4005-6_0_5_load_177 | 177 | 0.0023079 | 0.00057842 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 76 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4005-6_0_5_line_0 |  | 0 | 1 | 0.023277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4005-6_0_5_line_1 |  | 1 | 2 | 0.018067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4005-6_0_5_line_2 |  | 2 | 6 | 0.037728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4005-6_0_5_line_3 |  | 3 | 4 | 0.023022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4005-6_0_5_line_4 |  | 3 | 5 | 8.2801e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4005-6_0_5_line_5 |  | 5 | 7 | 0.018606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4005-6_0_5_line_6 |  | 6 | 8 | 0.014746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4005-6_0_5_line_7 |  | 7 | 9 | 0.0017929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4005-6_0_5_line_8 |  | 8 | 135 | 0.014861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4005-6_0_5_line_9 |  | 8 | 133 | 0.0072007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4005-6_0_5_line_10 |  | 9 | 94 | 0.038245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4005-6_0_5_line_11 |  | 10 | 11 | 0.020804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4005-6_0_5_line_12 |  | 11 | 12 | 0.027683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4005-6_0_5_line_13 |  | 11 | 13 | 0.024624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4005-6_0_5_line_14 |  | 12 | 17 | 0.013285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4005-6_0_5_line_15 |  | 12 | 18 | 0.028341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4005-6_0_5_line_16 |  | 13 | 19 | 0.019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4005-6_0_5_line_17 |  | 13 | 20 | 0.011953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_4005-6_0_5_line_18 |  | 13 | 21 | 0.026445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4005-6_0_5_line_19 |  | 14 | 15 | 0.023905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4005-6_0_5_line_20 |  | 14 | 16 | 0.0077143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4005-6_0_5_line_21 |  | 15 | 19 | 0.039281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4005-6_0_5_line_22 |  | 15 | 22 | 0.0075323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4005-6_0_5_line_23 |  | 16 | 23 | 0.034634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4005-6_0_5_line_24 |  | 17 | 24 | 0.020308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4005-6_0_5_line_25 |  | 18 | 25 | 0.02244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4005-6_0_5_line_26 |  | 20 | 26 | 0.005548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_4005-6_0_5_line_27 |  | 21 | 27 | 0.0097768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4005-6_0_5_line_28 |  | 22 | 28 | 0.018908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4005-6_0_5_line_29 |  | 23 | 29 | 0.008362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4005-6_0_5_line_30 |  | 23 | 30 | 0.011454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4005-6_0_5_line_31 |  | 26 | 31 | 0.027103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_4005-6_0_5_line_32 |  | 27 | 117 | 0.023495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4005-6_0_5_line_33 |  | 28 | 147 | 0.024743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4005-6_0_5_line_34 |  | 29 | 152 | 0.0031733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4005-6_0_5_line_35 |  | 30 | 151 | 0.015265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4005-6_0_5_line_36 |  | 31 | 35 | 0.021464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_4005-6_0_5_line_37 |  | 32 | 33 | 0.021161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4005-6_0_5_line_38 |  | 32 | 34 | 0.034473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4005-6_0_5_line_39 |  | 33 | 36 | 0.0016074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_4005-6_0_5_line_40 |  | 33 | 37 | 0.008565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4005-6_0_5_line_41 |  | 34 | 38 | 0.017683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4005-6_0_5_line_42 |  | 35 | 36 | 0.019144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_4005-6_0_5_line_43 |  | 37 | 109 | 0.0065966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_4005-6_0_5_line_44 |  | 38 | 90 | 0.005883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4005-6_0_5_line_45 |  | 39 | 40 | 0.014249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4005-6_0_5_line_46 |  | 40 | 41 | 0.0042383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4005-6_0_5_line_47 |  | 41 | 45 | 0.024446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4005-6_0_5_line_48 |  | 41 | 46 | 0.011272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4005-6_0_5_line_49 |  | 42 | 43 | 0.02971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4005-6_0_5_line_50 |  | 42 | 44 | 0.03339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4005-6_0_5_line_51 |  | 43 | 47 | 0.023392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4005-6_0_5_line_52 |  | 44 | 48 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4005-6_0_5_line_53 |  | 44 | 49 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4005-6_0_5_line_54 |  | 45 | 47 | 0.013686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4005-6_0_5_line_55 |  | 45 | 50 | 0.0019628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4005-6_0_5_line_56 |  | 46 | 51 | 0.006878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4005-6_0_5_line_57 |  | 47 | 52 | 0.033204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_4005-6_0_5_line_58 |  | 48 | 53 | 0.015054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4005-6_0_5_line_59 |  | 49 | 54 | 0.014146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4005-6_0_5_line_60 |  | 52 | 55 | 0.0071694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4005-6_0_5_line_61 |  | 52 | 56 | 0.019171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
62 | LV_4005-6_0_5_line_62 |  | 53 | 61 | 0.0028228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4005-6_0_5_line_63 |  | 55 | 57 | 0.014115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4005-6_0_5_line_64 |  | 56 | 58 | 0.028642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_4005-6_0_5_line_65 |  | 57 | 69 | 0.018392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4005-6_0_5_line_66 |  | 58 | 76 | 0.028965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_4005-6_0_5_line_67 |  | 59 | 60 | 0.021601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4005-6_0_5_line_68 |  | 60 | 73 | 0.001843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4005-6_0_5_line_69 |  | 61 | 62 | 0.022689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4005-6_0_5_line_70 |  | 61 | 63 | 0.014626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4005-6_0_5_line_71 |  | 62 | 64 | 0.029027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4005-6_0_5_line_72 |  | 63 | 65 | 0.0010664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4005-6_0_5_line_73 |  | 64 | 66 | 0.030721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4005-6_0_5_line_74 |  | 64 | 67 | 0.027494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4005-6_0_5_line_75 |  | 66 | 70 | 0.013541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4005-6_0_5_line_76 |  | 67 | 71 | 0.016061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4005-6_0_5_line_77 |  | 68 | 69 | 0.011215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4005-6_0_5_line_78 |  | 70 | 157 | 0.016191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4005-6_0_5_line_79 |  | 70 | 158 | 0.014053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4005-6_0_5_line_80 |  | 72 | 73 | 0.016768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4005-6_0_5_line_81 |  | 72 | 74 | 0.0094677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4005-6_0_5_line_82 |  | 73 | 75 | 0.006191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4005-6_0_5_line_83 |  | 75 | 76 | 0.033067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_4005-6_0_5_line_84 |  | 75 | 77 | 0.010755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_4005-6_0_5_line_85 |  | 77 | 78 | 0.0062043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_4005-6_0_5_line_86 |  | 78 | 79 | 0.033917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_4005-6_0_5_line_87 |  | 79 | 80 | 0.0072809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_4005-6_0_5_line_88 |  | 80 | 81 | 0.032661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_4005-6_0_5_line_89 |  | 80 | 82 | 0.001826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4005-6_0_5_line_90 |  | 81 | 92 | 0.003022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_4005-6_0_5_line_91 |  | 82 | 86 | 0.022884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4005-6_0_5_line_92 |  | 82 | 83 | 0.024122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4005-6_0_5_line_93 |  | 83 | 84 | 0.020355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4005-6_0_5_line_94 |  | 84 | 85 | 0.027334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4005-6_0_5_line_95 |  | 85 | 87 | 0.029616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4005-6_0_5_line_96 |  | 87 | 88 | 0.045283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4005-6_0_5_line_97 |  | 87 | 89 | 0.040623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4005-6_0_5_line_98 |  | 88 | 93 | 0.0093803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4005-6_0_5_line_99 |  | 89 | 94 | 0.010394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4005-6_0_5_line_100 |  | 90 | 91 | 0.018652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4005-6_0_5_line_101 |  | 92 | 109 | 0.0014968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_4005-6_0_5_line_102 |  | 93 | 95 | 0.02225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4005-6_0_5_line_103 |  | 94 | 96 | 0.016406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4005-6_0_5_line_104 |  | 95 | 129 | 0.014595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4005-6_0_5_line_105 |  | 95 | 128 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4005-6_0_5_line_106 |  | 96 | 107 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4005-6_0_5_line_107 |  | 97 | 98 | 0.037099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4005-6_0_5_line_108 |  | 98 | 107 | 0.013722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4005-6_0_5_line_109 |  | 99 | 100 | 0.019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4005-6_0_5_line_110 |  | 99 | 101 | 0.01572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4005-6_0_5_line_111 |  | 100 | 106 | 0.040718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4005-6_0_5_line_112 |  | 100 | 105 | 0.034716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4005-6_0_5_line_113 |  | 101 | 108 | 0.049008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4005-6_0_5_line_114 |  | 102 | 103 | 0.046635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4005-6_0_5_line_115 |  | 102 | 104 | 0.013519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4005-6_0_5_line_116 |  | 103 | 141 | 0.023549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4005-6_0_5_line_117 |  | 104 | 105 | 0.018224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4005-6_0_5_line_118 |  | 106 | 136 | 0.026905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4005-6_0_5_line_119 |  | 107 | 140 | 0.043587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4005-6_0_5_line_120 |  | 108 | 137 | 0.010888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4005-6_0_5_line_121 |  | 110 | 111 | 0.019896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4005-6_0_5_line_122 |  | 111 | 112 | 0.015952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4005-6_0_5_line_123 |  | 111 | 113 | 0.002573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4005-6_0_5_line_124 |  | 112 | 173 | 0.029861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4005-6_0_5_line_125 |  | 113 | 166 | 0.013393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4005-6_0_5_line_126 |  | 113 | 165 | 0.029908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4005-6_0_5_line_127 |  | 114 | 115 | 0.024353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4005-6_0_5_line_128 |  | 114 | 116 | 0.015434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4005-6_0_5_line_129 |  | 115 | 117 | 0.002158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4005-6_0_5_line_130 |  | 116 | 118 | 0.019797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4005-6_0_5_line_131 |  | 119 | 120 | 0.0033398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4005-6_0_5_line_132 |  | 119 | 121 | 0.027295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4005-6_0_5_line_133 |  | 121 | 122 | 0.025495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4005-6_0_5_line_134 |  | 122 | 123 | 0.010163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4005-6_0_5_line_135 |  | 123 | 124 | 0.02309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4005-6_0_5_line_136 |  | 123 | 125 | 0.037308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4005-6_0_5_line_137 |  | 124 | 149 | 0.048874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4005-6_0_5_line_138 |  | 125 | 150 | 0.02814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4005-6_0_5_line_139 |  | 126 | 127 | 0.018853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4005-6_0_5_line_140 |  | 127 | 128 | 0.037731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4005-6_0_5_line_141 |  | 129 | 130 | 0.0052284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4005-6_0_5_line_142 |  | 130 | 131 | 0.007201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4005-6_0_5_line_143 |  | 131 | 132 | 0.016797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4005-6_0_5_line_144 |  | 133 | 134 | 0.020108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4005-6_0_5_line_145 |  | 134 | 139 | 0.0017639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4005-6_0_5_line_146 |  | 135 | 136 | 0.028912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4005-6_0_5_line_147 |  | 137 | 138 | 0.032855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4005-6_0_5_line_148 |  | 140 | 141 | 0.00097177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4005-6_0_5_line_149 |  | 142 | 143 | 0.012317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4005-6_0_5_line_150 |  | 142 | 144 | 0.028899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4005-6_0_5_line_151 |  | 144 | 145 | 0.0094589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4005-6_0_5_line_152 |  | 145 | 146 | 0.010948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4005-6_0_5_line_153 |  | 145 | 147 | 0.0099881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4005-6_0_5_line_154 |  | 146 | 148 | 0.0127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4005-6_0_5_line_155 |  | 148 | 154 | 0.054644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4005-6_0_5_line_156 |  | 148 | 155 | 0.055997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4005-6_0_5_line_157 |  | 149 | 177 | 0.014269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4005-6_0_5_line_158 |  | 150 | 174 | 0.02341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4005-6_0_5_line_159 |  | 150 | 173 | 0.015908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4005-6_0_5_line_160 |  | 152 | 153 | 0.020919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4005-6_0_5_line_161 |  | 153 | 156 | 0.026262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4005-6_0_5_line_162 |  | 157 | 160 | 0.0029342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4005-6_0_5_line_163 |  | 158 | 159 | 0.018296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4005-6_0_5_line_164 |  | 160 | 161 | 0.013066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4005-6_0_5_line_165 |  | 161 | 165 | 0.010378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4005-6_0_5_line_166 |  | 161 | 163 | 0.014811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4005-6_0_5_line_167 |  | 162 | 163 | 0.020339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4005-6_0_5_line_168 |  | 162 | 164 | 0.017267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4005-6_0_5_line_169 |  | 166 | 169 | 0.00067929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4005-6_0_5_line_170 |  | 167 | 168 | 0.0094689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4005-6_0_5_line_171 |  | 167 | 169 | 0.0143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4005-6_0_5_line_172 |  | 168 | 170 | 0.0033383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4005-6_0_5_line_173 |  | 170 | 171 | 0.0074054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4005-6_0_5_line_174 |  | 171 | 172 | 0.019603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4005-6_0_5_line_175 |  | 174 | 175 | 0.0015317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4005-6_0_5_line_176 |  | 175 | 176 | 0.029148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4005-6_0_5_trafo_46 | 0.63 MVA 20/0.4 kV | 178 | 76 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2643427.6494 | 1250556.5969 | 2643407.1168 | 1250567.562
1 | 2643390.7791 | 1250575.2705 | 2643405.6541 | 1250568.3431 | 2643407.1168 | 1250567.562
2 | 2643390.7791 | 1250575.2705 | 2643380.621 | 1250580.0012 | 2643355.113 | 1250587.2677
3 | 2643278.8074 | 1250549.9595 | 2643281.3303 | 1250572.8424
4 | 2643281.3394 | 1250572.9247 | 2643281.3303 | 1250572.8424
5 | 2643283.3785 | 1250591.4189 | 2643281.3394 | 1250572.9247
6 | 2643340.9314 | 1250591.3076 | 2643355.113 | 1250587.2677
7 | 2643283.3785 | 1250591.4189 | 2643283.5749 | 1250593.201
8 | 2643340.9314 | 1250591.3076 | 2643341.2587 | 1250594.034 | 2643343.8629 | 1250605.8659
9 | 2643340.9314 | 1250591.3076 | 2643340.0823 | 1250584.1571
10 | 2643257.8729 | 1250610.2807 | 2643279.1622 | 1250606.8115 | 2643283.0118 | 1250604.7604 | 2643284.6693 | 1250603.1269 | 2643283.5749 | 1250593.201
11 | 2643102.0862 | 1250715.3842 | 2643094.8842 | 1250734.9015
12 | 2643128.1182 | 1250725.0132 | 2643102.0862 | 1250715.3842
13 | 2643078.9299 | 1250706.8213 | 2643102.0862 | 1250715.3842
14 | 2643132.6626 | 1250712.5267 | 2643128.1182 | 1250725.0132
15 | 2643128.1182 | 1250725.0132 | 2643154.5978 | 1250735.116
16 | 2643078.9299 | 1250706.8213 | 2643072.2485 | 1250725.6607
17 | 2643078.9299 | 1250706.8213 | 2643083.6294 | 1250695.8258
18 | 2643078.9299 | 1250706.8213 | 2643054.2597 | 1250697.2955
19 | 2643059.1174 | 1250762.6818 | 2643081.1808 | 1250772.0372
20 | 2643081.1808 | 1250772.0372 | 2643088.2927 | 1250775.0257
21 | 2643059.1174 | 1250762.6818 | 2643062.639 | 1250752.7562 | 2643072.2485 | 1250725.6607
22 | 2643059.1174 | 1250762.6818 | 2643052.0438 | 1250760.0932
23 | 2643120.2218 | 1250788.443 | 2643088.2927 | 1250775.0257
24 | 2643132.6626 | 1250712.5267 | 2643113.439 | 1250705.9791
25 | 2643175.5633 | 1250743.115 | 2643154.5978 | 1250735.116
26 | 2643083.6294 | 1250695.8258 | 2643087.3805 | 1250691.7281
27 | 2643054.2597 | 1250697.2955 | 2643045.1392 | 1250693.7738
28 | 2643052.0438 | 1250760.0932 | 2643034.2878 | 1250753.5953
29 | 2643120.2218 | 1250788.443 | 2643116.8298 | 1250796.0902
30 | 2643120.2218 | 1250788.443 | 2643130.7844 | 1250792.8718
31 | 2643093.2869 | 1250665.2754 | 2643087.3805 | 1250691.7281
32 | 2643023.2208 | 1250685.3136 | 2643029.6266 | 1250687.7839 | 2643045.1392 | 1250693.7738
33 | 2643034.2878 | 1250753.5953 | 2643032.7384 | 1250753.0283 | 2643012.6896 | 1250741.5672
34 | 2643116.8298 | 1250796.0902 | 2643115.4821 | 1250798.963
35 | 2643144.8625 | 1250798.7745 | 2643130.7844 | 1250792.8718
36 | 2643114.1654 | 1250670.5084 | 2643093.2869 | 1250665.2754
37 | 2643143.6379 | 1250678.2946 | 2643132.2945 | 1250660.4112
38 | 2643143.6379 | 1250678.2946 | 2643176.1227 | 1250689.8319
39 | 2643132.2945 | 1250660.4112 | 2643130.8903 | 1250661.1933
40 | 2643139.7978 | 1250656.2407 | 2643132.2945 | 1250660.4112
41 | 2643187.9276 | 1250685.077 | 2643184.8359 | 1250692.9265 | 2643176.1227 | 1250689.8319
42 | 2643114.1654 | 1250670.5084 | 2643130.8903 | 1250661.1933
43 | 2643139.7978 | 1250656.2407 | 2643145.5597 | 1250653.0289
44 | 2643190.1638 | 1250679.6341 | 2643187.9276 | 1250685.077
45 | 2643201.7836 | 1250493.838 | 2643207.7108 | 1250506.7955
46 | 2643209.4739 | 1250510.6498 | 2643207.7108 | 1250506.7955
47 | 2643185.6463 | 1250516.4134 | 2643209.4739 | 1250510.6498
48 | 2643214.1698 | 1250520.902 | 2643209.4739 | 1250510.6498
49 | 2643195.4266 | 1250462.9153 | 2643188.3813 | 1250471.5365 | 2643173.1164 | 1250482.1214
50 | 2643175.7336 | 1250438.878 | 2643174.2107 | 1250442.7695 | 2643195.4266 | 1250462.9153
51 | 2643178.1132 | 1250504.9731 | 2643173.1164 | 1250482.1214
52 | 2643175.7336 | 1250438.878 | 2643163.2413 | 1250433.0828
53 | 2643175.7336 | 1250438.878 | 2643180.6155 | 1250427.8414
54 | 2643178.1132 | 1250504.9731 | 2643185.6463 | 1250516.4134
55 | 2643185.6463 | 1250516.4134 | 2643186.7214 | 1250518.0557
56 | 2643217.0304 | 1250527.1604 | 2643214.1698 | 1250520.902
57 | 2643145.5143 | 1250511.7627 | 2643178.1132 | 1250504.9731
58 | 2643149.5856 | 1250426.748 | 2643163.2413 | 1250433.0828
59 | 2643185.7543 | 1250414.6942 | 2643184.5676 | 1250418.9066 | 2643180.6155 | 1250427.8414
60 | 2643141.9814 | 1250505.5551 | 2643144.1312 | 1250509.9181 | 2643145.5143 | 1250511.7627
61 | 2643129.2704 | 1250517.8932 | 2643144.1312 | 1250509.9181 | 2643145.5143 | 1250511.7627
62 | 2643147.0249 | 1250425.5601 | 2643149.5856 | 1250426.748
63 | 2643141.9814 | 1250505.5551 | 2643135.7361 | 1250492.8972
64 | 2643129.2704 | 1250517.8932 | 2643131.2066 | 1250523.6 | 2643127.5712 | 1250545.9214
65 | 2643135.7361 | 1250492.8972 | 2643134.1855 | 1250489.7544 | 2643129.4659 | 1250475.6346
66 | 2643127.5712 | 1250545.9214 | 2643126.7265 | 1250551.1081 | 2643129.0016 | 1250554.8383 | 2643127.4496 | 1250564.8004 | 2643136.5677 | 1250566.4088
67 | 2643168.0348 | 1250564.1952 | 2643167.0385 | 1250556.9275 | 2643163.9911 | 1250542.991
68 | 2643168.0348 | 1250564.1952 | 2643168.2857 | 1250566.0205
69 | 2643124.6541 | 1250423.0068 | 2643139.5542 | 1250423.1375 | 2643147.0249 | 1250425.5601
70 | 2643147.0249 | 1250425.5601 | 2643153.1212 | 1250412.2657
71 | 2643116.8505 | 1250402.0026 | 2643123.5849 | 1250400.8397 | 2643124.6541 | 1250423.0068
72 | 2643153.1212 | 1250412.2657 | 2643153.5658 | 1250411.2964
73 | 2643116.8505 | 1250402.0026 | 2643106.7001 | 1250405.7981 | 2643098.7629 | 1250410.4324 | 2643093.1858 | 1250419.5557
74 | 2643116.8505 | 1250402.0026 | 2643090.3231 | 1250394.7771
75 | 2643087.6021 | 1250431.7323 | 2643088.9308 | 1250426.5163 | 2643093.1858 | 1250419.5557
76 | 2643074.827 | 1250390.5563 | 2643090.3231 | 1250394.7771
77 | 2643126.983 | 1250464.7924 | 2643127.2114 | 1250468.8896 | 2643129.4659 | 1250475.6346
78 | 2643087.6021 | 1250431.7323 | 2643083.6077 | 1250447.4234
79 | 2643087.6021 | 1250431.7323 | 2643073.8464 | 1250428.855
80 | 2643168.2857 | 1250566.0205 | 2643185.0283 | 1250565.105
81 | 2643194.4819 | 1250564.588 | 2643185.0283 | 1250565.105
82 | 2643169.1318 | 1250572.153 | 2643168.2857 | 1250566.0205
83 | 2643169.1318 | 1250572.153 | 2643136.5677 | 1250566.4088
84 | 2643169.1318 | 1250572.153 | 2643169.9044 | 1250582.8798
85 | 2643169.9044 | 1250582.8798 | 2643170.3502 | 1250589.068
86 | 2643172.8257 | 1250622.8938 | 2643172.7377 | 1250622.213 | 2643170.3502 | 1250589.068
87 | 2643173.7596 | 1250630.1146 | 2643172.8257 | 1250622.8938
88 | 2643173.7596 | 1250630.1146 | 2643169.1871 | 1250638.1534 | 2643150.8633 | 1250650.0726 | 2643149.5066 | 1250650.8288
89 | 2643173.7596 | 1250630.1146 | 2643175.5534 | 1250630.4835
90 | 2643149.5066 | 1250650.8288 | 2643146.8671 | 1250652.3002
91 | 2643175.5534 | 1250630.4835 | 2643186.655 | 1250650.4942
92 | 2643175.5534 | 1250630.4835 | 2643181.6501 | 1250628.7378 | 2643195.1854 | 1250617.2086
93 | 2643195.1854 | 1250617.2086 | 2643201.6721 | 1250611.6832 | 2643210.7617 | 1250604.1047
94 | 2643210.7617 | 1250604.1047 | 2643221.251 | 1250595.3593 | 2643229.6541 | 1250584.5675
95 | 2643247.7693 | 1250561.1406 | 2643241.7778 | 1250569.1468 | 2643237.0393 | 1250575.0829 | 2643229.6541 | 1250584.5675
96 | 2643247.7693 | 1250561.1406 | 2643250.9974 | 1250544.9533 | 2643258.7042 | 1250525.3296 | 2643261.8951 | 1250518.3287
97 | 2643247.7693 | 1250561.1406 | 2643252.2671 | 1250567.4999 | 2643255.0696 | 1250579.6396 | 2643256.6917 | 1250598.3752 | 2643256.8467 | 1250599.9372
98 | 2643265.7855 | 1250509.7932 | 2643261.8951 | 1250518.3287
99 | 2643257.8729 | 1250610.2807 | 2643256.8467 | 1250599.9372
100 | 2643190.1638 | 1250679.6341 | 2643201.0278 | 1250683.5158 | 2643207.5868 | 1250686.2749
101 | 2643146.8671 | 1250652.3002 | 2643145.5597 | 1250653.0289
102 | 2643275.0137 | 1250489.5466 | 2643265.7855 | 1250509.7932
103 | 2643257.8729 | 1250610.2807 | 2643259.4927 | 1250626.6062
104 | 2643275.0137 | 1250489.5466 | 2643280.9905 | 1250476.2317
105 | 2643275.0137 | 1250489.5466 | 2643261.9476 | 1250483.5847
106 | 2643261.1316 | 1250643.1239 | 2643259.4927 | 1250626.6062
107 | 2643262.4882 | 1250656.7788 | 2643265.0451 | 1250682.5151 | 2643266.2673 | 1250693.6841
108 | 2643261.1316 | 1250643.1239 | 2643261.1495 | 1250643.3047 | 2643262.4882 | 1250656.7788
109 | 2643375.5911 | 1250696.921 | 2643394.0276 | 1250690.4445
110 | 2643408.8592 | 1250685.2343 | 2643394.0276 | 1250690.4445
111 | 2643375.5911 | 1250696.921 | 2643365.834 | 1250670.7209 | 2643361.0166 | 1250658.9048
112 | 2643375.5911 | 1250696.921 | 2643347.4109 | 1250712.7145 | 2643345.2793 | 1250713.8424
113 | 2643408.8592 | 1250685.2343 | 2643402.5794 | 1250663.5181 | 2643410.2417 | 1250651.0658 | 2643413.4909 | 1250642.3504 | 2643412.4026 | 1250640.1224
114 | 2643323.81 | 1250709.9548 | 2643318.6238 | 1250697.9498 | 2643310.1709 | 1250669.8803 | 2643309.363 | 1250665.7152
115 | 2643329.1715 | 1250722.3656 | 2643323.81 | 1250709.9548
116 | 2643309.363 | 1250665.7152 | 2643304.8784 | 1250642.5975
117 | 2643329.1715 | 1250722.3656 | 2643345.2793 | 1250713.8424
118 | 2643361.0166 | 1250658.9048 | 2643355.7269 | 1250645.9303 | 2643351.8866 | 1250633.6215
119 | 2643261.1316 | 1250643.1239 | 2643304.6933 | 1250641.6435
120 | 2643412.4026 | 1250640.1224 | 2643407.624 | 1250630.3395
121 | 2643068.6256 | 1250504.3434 | 2643088.0427 | 1250508.6817
122 | 2643068.6256 | 1250504.3434 | 2643064.9404 | 1250518.0592 | 2643064.2915 | 1250519.6839
123 | 2643069.2928 | 1250501.8577 | 2643068.6256 | 1250504.3434
124 | 2643053.2162 | 1250547.4156 | 2643064.2915 | 1250519.6839
125 | 2643069.2928 | 1250501.8577 | 2643056.0084 | 1250500.152
126 | 2643069.2928 | 1250501.8577 | 2643077.0418 | 1250472.9709
127 | 2643021.2036 | 1250684.5318 | 2643033.199 | 1250663.3382
128 | 2643040.8014 | 1250649.9062 | 2643033.199 | 1250663.3382
129 | 2643023.2208 | 1250685.3136 | 2643021.2036 | 1250684.5318
130 | 2643040.8014 | 1250649.9062 | 2643043.0083 | 1250652.6462 | 2643058.7961 | 1250656.6119
131 | 2642970.4922 | 1250664.9621 | 2642967.4626 | 1250666.3679
132 | 2642970.4922 | 1250664.9621 | 2642987.8296 | 1250643.8801
133 | 2643004.0235 | 1250624.1888 | 2642987.8296 | 1250643.8801
134 | 2643010.4815 | 1250616.3414 | 2643007.024 | 1250620.5414 | 2643004.0235 | 1250624.1888
135 | 2643010.4815 | 1250616.3414 | 2643032.9616 | 1250621.6115
136 | 2643010.4815 | 1250616.3414 | 2643015.6829 | 1250610.0193 | 2643032.0907 | 1250585.9601
137 | 2643032.9616 | 1250621.6115 | 2643073.9614 | 1250631.2232 | 2643075.4535 | 1250624.6271
138 | 2643046.2201 | 1250561.6972 | 2643039.5486 | 1250575.0244 | 2643032.0907 | 1250585.9601
139 | 2643235.5106 | 1250436.2821 | 2643239.5131 | 1250454.705
140 | 2643239.5131 | 1250454.705 | 2643240.5108 | 1250459.2969 | 2643249.2822 | 1250473.7928 | 2643259.6356 | 1250482.5297 | 2643261.9476 | 1250483.5847
141 | 2643282.5801 | 1250471.2748 | 2643281.8737 | 1250474.2642 | 2643280.9905 | 1250476.2317
142 | 2643282.5801 | 1250471.2748 | 2643284.236 | 1250464.2667
143 | 2643287.1999 | 1250447.7625 | 2643286.2981 | 1250455.5394 | 2643284.236 | 1250464.2667
144 | 2643340.0823 | 1250584.1571 | 2643339.7937 | 1250581.7261 | 2643336.974 | 1250564.2924
145 | 2643336.6923 | 1250562.5511 | 2643336.974 | 1250564.2924
146 | 2643343.8629 | 1250605.8659 | 2643345.3864 | 1250612.7879 | 2643351.8866 | 1250633.6215
147 | 2643413.1724 | 1250604.4114 | 2643400.7366 | 1250616.2394 | 2643407.624 | 1250630.3395
148 | 2643304.6933 | 1250641.6435 | 2643304.8784 | 1250642.5975
149 | 2642971.7703 | 1250715.838 | 2642961.4062 | 1250709.1825
150 | 2642971.7703 | 1250715.838 | 2642996.087 | 1250731.4535
151 | 2643004.0461 | 1250736.5646 | 2642996.087 | 1250731.4535
152 | 2643004.0461 | 1250736.5646 | 2642999.5692 | 1250746.5555
153 | 2643004.0461 | 1250736.5646 | 2643004.9026 | 1250737.1157 | 2643012.6896 | 1250741.5672
154 | 2642992.6425 | 1250757.1292 | 2642998.1613 | 1250749.6975 | 2642999.5692 | 1250746.5555
155 | 2642992.6425 | 1250757.1292 | 2642949.0765 | 1250790.1136
156 | 2642992.6425 | 1250757.1292 | 2643016.5653 | 1250807.759
157 | 2643078.6018 | 1250610.7097 | 2643075.4535 | 1250624.6271
158 | 2643046.2201 | 1250561.6972 | 2643069.3342 | 1250565.4064
159 | 2643046.2201 | 1250561.6972 | 2643052.6005 | 1250548.9571 | 2643053.2162 | 1250547.4156
160 | 2643107.1286 | 1250818.1345 | 2643111.6162 | 1250807.2042 | 2643115.4821 | 1250798.963
161 | 2643107.1286 | 1250818.1345 | 2643099.2385 | 1250825.7045 | 2643086.9922 | 1250834.9224
162 | 2643082.8839 | 1250450.2669 | 2643083.6077 | 1250447.4234
163 | 2643055.9382 | 1250425.1091 | 2643073.8464 | 1250428.855
164 | 2643079.6606 | 1250462.929 | 2643082.8839 | 1250450.2669
165 | 2643079.6606 | 1250462.929 | 2643078.2619 | 1250468.4225 | 2643077.0418 | 1250472.9709
166 | 2643079.6606 | 1250462.929 | 2643065.1241 | 1250460.0933
167 | 2643045.1613 | 1250456.1992 | 2643065.1241 | 1250460.0933
168 | 2643028.214 | 1250452.8933 | 2643045.1613 | 1250456.1992
169 | 2643056.0084 | 1250500.152 | 2643055.3347 | 1250500.0655
170 | 2643041.1507 | 1250498.2443 | 2643031.7589 | 1250497.0384
171 | 2643041.1507 | 1250498.2443 | 2643055.3347 | 1250500.0655
172 | 2643031.7589 | 1250497.0384 | 2643028.4478 | 1250496.6133
173 | 2643023.2925 | 1250491.6612 | 2643023.7547 | 1250493.1881 | 2643028.4478 | 1250496.6133 | 2643028.4478 | 1250496.6133
174 | 2643025.1132 | 1250472.4284 | 2643022.3615 | 1250488.586 | 2643023.2925 | 1250491.6612
175 | 2643070.8465 | 1250565.6491 | 2643069.3342 | 1250565.4064
176 | 2643070.8465 | 1250565.6491 | 2643099.6262 | 1250570.2675

## bus_geodata
| x | y | coords
0 | 2643427.6494 | 1250556.5969
1 | 2643407.1168 | 1250567.562
2 | 2643390.7791 | 1250575.2705
3 | 2643281.3303 | 1250572.8424
4 | 2643278.8074 | 1250549.9595
5 | 2643281.3394 | 1250572.9247
6 | 2643355.113 | 1250587.2677
7 | 2643283.3785 | 1250591.4189
8 | 2643340.9314 | 1250591.3076
9 | 2643283.5749 | 1250593.201
10 | 2643094.8842 | 1250734.9015
11 | 2643102.0862 | 1250715.3842
12 | 2643128.1182 | 1250725.0132
13 | 2643078.9299 | 1250706.8213
14 | 2643081.1808 | 1250772.0372
15 | 2643059.1174 | 1250762.6818
16 | 2643088.2927 | 1250775.0257
17 | 2643132.6626 | 1250712.5267
18 | 2643154.5978 | 1250735.116
19 | 2643072.2485 | 1250725.6607
20 | 2643083.6294 | 1250695.8258
21 | 2643054.2597 | 1250697.2955
22 | 2643052.0438 | 1250760.0932
23 | 2643120.2218 | 1250788.443
24 | 2643113.439 | 1250705.9791
25 | 2643175.5633 | 1250743.115
26 | 2643087.3805 | 1250691.7281
27 | 2643045.1392 | 1250693.7738
28 | 2643034.2878 | 1250753.5953
29 | 2643116.8298 | 1250796.0902
30 | 2643130.7844 | 1250792.8718
31 | 2643093.2869 | 1250665.2754
32 | 2643143.6379 | 1250678.2946
33 | 2643132.2945 | 1250660.4112
34 | 2643176.1227 | 1250689.8319
35 | 2643114.1654 | 1250670.5084
36 | 2643130.8903 | 1250661.1933
37 | 2643139.7978 | 1250656.2407
38 | 2643187.9276 | 1250685.077
39 | 2643201.7836 | 1250493.838
40 | 2643207.7108 | 1250506.7955
41 | 2643209.4739 | 1250510.6498
42 | 2643195.4266 | 1250462.9153
43 | 2643173.1164 | 1250482.1214
44 | 2643175.7336 | 1250438.878
45 | 2643185.6463 | 1250516.4134
46 | 2643214.1698 | 1250520.902
47 | 2643178.1132 | 1250504.9731
48 | 2643163.2413 | 1250433.0828
49 | 2643180.6155 | 1250427.8414
50 | 2643186.7214 | 1250518.0557
51 | 2643217.0304 | 1250527.1604
52 | 2643145.5143 | 1250511.7627
53 | 2643149.5856 | 1250426.748
54 | 2643185.7543 | 1250414.6942
55 | 2643141.9814 | 1250505.5551
56 | 2643129.2704 | 1250517.8932
57 | 2643135.7361 | 1250492.8972
58 | 2643127.5712 | 1250545.9214
59 | 2643163.9911 | 1250542.991
60 | 2643168.0348 | 1250564.1952
61 | 2643147.0249 | 1250425.5601
62 | 2643124.6541 | 1250423.0068
63 | 2643153.1212 | 1250412.2657
64 | 2643116.8505 | 1250402.0026
65 | 2643153.5658 | 1250411.2964
66 | 2643093.1858 | 1250419.5557
67 | 2643090.3231 | 1250394.7771
68 | 2643126.983 | 1250464.7924
69 | 2643129.4659 | 1250475.6346
70 | 2643087.6021 | 1250431.7323
71 | 2643074.827 | 1250390.5563
72 | 2643185.0283 | 1250565.105
73 | 2643168.2857 | 1250566.0205
74 | 2643194.4819 | 1250564.588
75 | 2643169.1318 | 1250572.153
76 | 2643136.5677 | 1250566.4088
77 | 2643169.9044 | 1250582.8798
78 | 2643170.3502 | 1250589.068
79 | 2643172.8257 | 1250622.8938
80 | 2643173.7595 | 1250630.1146
81 | 2643149.5066 | 1250650.8288
82 | 2643175.5534 | 1250630.4835
83 | 2643195.1854 | 1250617.2086
84 | 2643210.7617 | 1250604.1047
85 | 2643229.6541 | 1250584.5675
86 | 2643186.655 | 1250650.4942
87 | 2643247.7693 | 1250561.1406
88 | 2643261.8951 | 1250518.3287
89 | 2643256.8467 | 1250599.9372
90 | 2643190.1638 | 1250679.6341
91 | 2643207.5868 | 1250686.2749
92 | 2643146.8671 | 1250652.3002
93 | 2643265.7855 | 1250509.7932
94 | 2643257.8729 | 1250610.2807
95 | 2643275.0137 | 1250489.5466
96 | 2643259.4927 | 1250626.6062
97 | 2643266.2673 | 1250693.6841
98 | 2643262.4882 | 1250656.7788
99 | 2643394.0276 | 1250690.4445
100 | 2643375.5911 | 1250696.921
101 | 2643408.8592 | 1250685.2343
102 | 2643323.81 | 1250709.9548
103 | 2643309.363 | 1250665.7152
104 | 2643329.1715 | 1250722.3656
105 | 2643345.2793 | 1250713.8424
106 | 2643361.0166 | 1250658.9048
107 | 2643261.1316 | 1250643.1239
108 | 2643412.4026 | 1250640.1224
109 | 2643145.5597 | 1250653.0289
110 | 2643088.0427 | 1250508.6817
111 | 2643068.6256 | 1250504.3434
112 | 2643064.2915 | 1250519.6839
113 | 2643069.2928 | 1250501.8577
114 | 2643033.199 | 1250663.3382
115 | 2643021.2036 | 1250684.5318
116 | 2643040.8014 | 1250649.9062
117 | 2643023.2208 | 1250685.3136
118 | 2643058.7961 | 1250656.6119
119 | 2642970.4922 | 1250664.9621
120 | 2642967.4626 | 1250666.3679
121 | 2642987.8296 | 1250643.8801
122 | 2643004.0235 | 1250624.1888
123 | 2643010.4815 | 1250616.3414
124 | 2643032.9616 | 1250621.6115
125 | 2643032.0907 | 1250585.9601
126 | 2643235.5106 | 1250436.2821
127 | 2643239.5131 | 1250454.705
128 | 2643261.9476 | 1250483.5847
129 | 2643280.9905 | 1250476.2317
130 | 2643282.5801 | 1250471.2748
131 | 2643284.236 | 1250464.2667
132 | 2643287.1999 | 1250447.7625
133 | 2643340.0823 | 1250584.1571
134 | 2643336.974 | 1250564.2924
135 | 2643343.8629 | 1250605.8659
136 | 2643351.8866 | 1250633.6215
137 | 2643407.624 | 1250630.3395
138 | 2643413.1724 | 1250604.4114
139 | 2643336.6923 | 1250562.5511
140 | 2643304.6933 | 1250641.6435
141 | 2643304.8784 | 1250642.5975
142 | 2642971.7703 | 1250715.838
143 | 2642961.4062 | 1250709.1825
144 | 2642996.087 | 1250731.4535
145 | 2643004.0461 | 1250736.5646
146 | 2642999.5692 | 1250746.5555
147 | 2643012.6896 | 1250741.5672
148 | 2642992.6424 | 1250757.1292
149 | 2643075.4535 | 1250624.6271
150 | 2643046.2201 | 1250561.6972
151 | 2643144.8625 | 1250798.7745
152 | 2643115.4821 | 1250798.963
153 | 2643107.1286 | 1250818.1345
154 | 2642949.0765 | 1250790.1136
155 | 2643016.5653 | 1250807.759
156 | 2643086.9922 | 1250834.9224
157 | 2643083.6077 | 1250447.4234
158 | 2643073.8464 | 1250428.855
159 | 2643055.9382 | 1250425.1091
160 | 2643082.8839 | 1250450.2669
161 | 2643079.6606 | 1250462.929
162 | 2643045.1613 | 1250456.1992
163 | 2643065.1241 | 1250460.0934
164 | 2643028.214 | 1250452.8933
165 | 2643077.0418 | 1250472.9709
166 | 2643056.0084 | 1250500.152
167 | 2643041.1507 | 1250498.2443
168 | 2643031.7589 | 1250497.0384
169 | 2643055.3347 | 1250500.0655
170 | 2643028.4478 | 1250496.6133
171 | 2643023.2925 | 1250491.6612
172 | 2643025.1132 | 1250472.4284
173 | 2643053.2162 | 1250547.4156
174 | 2643069.3342 | 1250565.4064
175 | 2643070.8465 | 1250565.6491
176 | 2643099.6262 | 1250570.2675
177 | 2643078.6018 | 1250610.7097
178 | 2643169.1318 | 1250572.153

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1