## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4010-10_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4010-10_0_7_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_4010-10_0_7_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_4010-10_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4010-10_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4010-10_0_7_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4010-10_0_7_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_4010-10_0_7_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_4010-10_0_7_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_4010-10_0_7_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_4010-10_0_7_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_4010-10_0_7_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_4010-10_0_7_node_167 | 0.4 | n |  | TRUE
13 | bus_LV_4010-10_0_7_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_4010-10_0_7_node_185 | 0.4 | n |  | TRUE
15 | bus_LV_4010-10_0_7_node_133 | 0.4 | n |  | TRUE
16 | bus_LV_4010-10_0_7_node_132 | 0.4 | n |  | TRUE
17 | bus_LV_4010-10_0_7_node_179 | 0.4 | n |  | TRUE
18 | bus_LV_4010-10_0_7_node_149 | 0.4 | n |  | TRUE
19 | bus_LV_4010-10_0_7_node_143 | 0.4 | n |  | TRUE
20 | bus_LV_4010-10_0_7_node_131 | 0.4 | n |  | TRUE
21 | bus_LV_4010-10_0_7_node_178 | 0.4 | n |  | TRUE
22 | bus_LV_4010-10_0_7_node_181 | 0.4 | n |  | TRUE
23 | bus_LV_4010-10_0_7_node_176 | 0.4 | n |  | TRUE
24 | bus_LV_4010-10_0_7_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_4010-10_0_7_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_4010-10_0_7_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_4010-10_0_7_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_4010-10_0_7_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_4010-10_0_7_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_4010-10_0_7_node_28 | 0.4 | n |  | TRUE
31 | bus_LV_4010-10_0_7_node_29 | 0.4 | n |  | TRUE
32 | bus_LV_4010-10_0_7_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_4010-10_0_7_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_4010-10_0_7_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_4010-10_0_7_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_4010-10_0_7_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_4010-10_0_7_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_4010-10_0_7_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_4010-10_0_7_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_4010-10_0_7_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_4010-10_0_7_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_4010-10_0_7_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_4010-10_0_7_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_4010-10_0_7_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_4010-10_0_7_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_4010-10_0_7_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_4010-10_0_7_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_4010-10_0_7_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_4010-10_0_7_node_150 | 0.4 | n |  | TRUE
50 | bus_LV_4010-10_0_7_node_148 | 0.4 | n |  | TRUE
51 | bus_LV_4010-10_0_7_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_4010-10_0_7_node_145 | 0.4 | n |  | TRUE
53 | bus_LV_4010-10_0_7_node_152 | 0.4 | n |  | TRUE
54 | bus_LV_4010-10_0_7_node_88 | 0.4 | n |  | TRUE
55 | bus_LV_4010-10_0_7_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_4010-10_0_7_node_87 | 0.4 | n |  | TRUE
57 | bus_LV_4010-10_0_7_node_155 | 0.4 | n |  | TRUE
58 | bus_LV_4010-10_0_7_node_50 | 0.4 | n |  | TRUE
59 | bus_LV_4010-10_0_7_node_45 | 0.4 | n |  | TRUE
60 | bus_LV_4010-10_0_7_node_146 | 0.4 | n |  | TRUE
61 | bus_LV_4010-10_0_7_node_153 | 0.4 | n |  | TRUE
62 | bus_LV_4010-10_0_7_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_4010-10_0_7_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_4010-10_0_7_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_4010-10_0_7_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_4010-10_0_7_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_4010-10_0_7_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_4010-10_0_7_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_4010-10_0_7_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_4010-10_0_7_node_54 | 0.4 | n |  | TRUE
71 | bus_LV_4010-10_0_7_node_56 | 0.4 | n |  | TRUE
72 | bus_LV_4010-10_0_7_node_57 | 0.4 | n |  | TRUE
73 | bus_LV_4010-10_0_7_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_4010-10_0_7_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_4010-10_0_7_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_4010-10_0_7_node_186 | 0.4 | n |  | TRUE
77 | bus_LV_4010-10_0_7_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_4010-10_0_7_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_4010-10_0_7_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_4010-10_0_7_node_184 | 0.4 | n |  | TRUE
81 | bus_LV_4010-10_0_7_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_4010-10_0_7_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_4010-10_0_7_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_4010-10_0_7_node_66 | 0.4 | n |  | TRUE
85 | bus_LV_4010-10_0_7_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_4010-10_0_7_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_4010-10_0_7_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_4010-10_0_7_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_4010-10_0_7_node_78 | 0.4 | n |  | TRUE
90 | bus_LV_4010-10_0_7_node_100 | 0.4 | n |  | TRUE
91 | bus_LV_4010-10_0_7_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_4010-10_0_7_node_77 | 0.4 | n |  | TRUE
93 | bus_LV_4010-10_0_7_node_101 | 0.4 | n |  | TRUE
94 | bus_LV_4010-10_0_7_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_4010-10_0_7_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_4010-10_0_7_node_74 | 0.4 | n |  | TRUE
97 | bus_LV_4010-10_0_7_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_4010-10_0_7_node_112 | 0.4 | n |  | TRUE
99 | bus_LV_4010-10_0_7_node_138 | 0.4 | n |  | TRUE
100 | bus_LV_4010-10_0_7_node_137 | 0.4 | n |  | TRUE
101 | bus_LV_4010-10_0_7_node_124 | 0.4 | n |  | TRUE
102 | bus_LV_4010-10_0_7_node_128 | 0.4 | n |  | TRUE
103 | bus_LV_4010-10_0_7_node_122 | 0.4 | n |  | TRUE
104 | bus_LV_4010-10_0_7_node_130 | 0.4 | n |  | TRUE
105 | bus_LV_4010-10_0_7_node_129 | 0.4 | n |  | TRUE
106 | bus_LV_4010-10_0_7_node_111 | 0.4 | n |  | TRUE
107 | bus_LV_4010-10_0_7_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_4010-10_0_7_node_79 | 0.4 | n |  | TRUE
109 | bus_LV_4010-10_0_7_node_105 | 0.4 | n |  | TRUE
110 | bus_LV_4010-10_0_7_node_103 | 0.4 | n |  | TRUE
111 | bus_LV_4010-10_0_7_node_82 | 0.4 | n |  | TRUE
112 | bus_LV_4010-10_0_7_node_83 | 0.4 | n |  | TRUE
113 | bus_LV_4010-10_0_7_node_84 | 0.4 | n |  | TRUE
114 | bus_LV_4010-10_0_7_node_85 | 0.4 | n |  | TRUE
115 | bus_LV_4010-10_0_7_node_90 | 0.4 | n |  | TRUE
116 | bus_LV_4010-10_0_7_node_86 | 0.4 | n |  | TRUE
117 | bus_LV_4010-10_0_7_node_91 | 0.4 | n |  | TRUE
118 | bus_LV_4010-10_0_7_node_89 | 0.4 | n |  | TRUE
119 | bus_LV_4010-10_0_7_node_94 | 0.4 | n |  | TRUE
120 | bus_LV_4010-10_0_7_node_151 | 0.4 | n |  | TRUE
121 | bus_LV_4010-10_0_7_node_97 | 0.4 | n |  | TRUE
122 | bus_LV_4010-10_0_7_node_92 | 0.4 | n |  | TRUE
123 | bus_LV_4010-10_0_7_node_102 | 0.4 | n |  | TRUE
124 | bus_LV_4010-10_0_7_node_99 | 0.4 | n |  | TRUE
125 | bus_LV_4010-10_0_7_node_104 | 0.4 | n |  | TRUE
126 | bus_LV_4010-10_0_7_node_98 | 0.4 | n |  | TRUE
127 | bus_LV_4010-10_0_7_node_93 | 0.4 | n |  | TRUE
128 | bus_LV_4010-10_0_7_node_95 | 0.4 | n |  | TRUE
129 | bus_LV_4010-10_0_7_node_96 | 0.4 | n |  | TRUE
130 | bus_LV_4010-10_0_7_node_113 | 0.4 | n |  | TRUE
131 | bus_LV_4010-10_0_7_node_166 | 0.4 | n |  | TRUE
132 | bus_LV_4010-10_0_7_node_157 | 0.4 | n |  | TRUE
133 | bus_LV_4010-10_0_7_node_110 | 0.4 | n |  | TRUE
134 | bus_LV_4010-10_0_7_node_156 | 0.4 | n |  | TRUE
135 | bus_LV_4010-10_0_7_node_106 | 0.4 | n |  | TRUE
136 | bus_LV_4010-10_0_7_node_107 | 0.4 | n |  | TRUE
137 | bus_LV_4010-10_0_7_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_4010-10_0_7_node_114 | 0.4 | n |  | TRUE
139 | bus_LV_4010-10_0_7_node_116 | 0.4 | n |  | TRUE
140 | bus_LV_4010-10_0_7_node_115 | 0.4 | n |  | TRUE
141 | bus_LV_4010-10_0_7_node_117 | 0.4 | n |  | TRUE
142 | bus_LV_4010-10_0_7_node_118 | 0.4 | n |  | TRUE
143 | bus_LV_4010-10_0_7_node_127 | 0.4 | n |  | TRUE
144 | bus_LV_4010-10_0_7_node_120 | 0.4 | n |  | TRUE
145 | bus_LV_4010-10_0_7_node_119 | 0.4 | n |  | TRUE
146 | bus_LV_4010-10_0_7_node_123 | 0.4 | n |  | TRUE
147 | bus_LV_4010-10_0_7_node_121 | 0.4 | n |  | TRUE
148 | bus_LV_4010-10_0_7_node_169 | 0.4 | n |  | TRUE
149 | bus_LV_4010-10_0_7_node_126 | 0.4 | n |  | TRUE
150 | bus_LV_4010-10_0_7_node_135 | 0.4 | n |  | TRUE
151 | bus_LV_4010-10_0_7_node_170 | 0.4 | n |  | TRUE
152 | bus_LV_4010-10_0_7_node_134 | 0.4 | n |  | TRUE
153 | bus_LV_4010-10_0_7_node_174 | 0.4 | n |  | TRUE
154 | bus_LV_4010-10_0_7_node_182 | 0.4 | n |  | TRUE
155 | bus_LV_4010-10_0_7_node_173 | 0.4 | n |  | TRUE
156 | bus_LV_4010-10_0_7_node_139 | 0.4 | n |  | TRUE
157 | bus_LV_4010-10_0_7_node_140 | 0.4 | n |  | TRUE
158 | bus_LV_4010-10_0_7_node_141 | 0.4 | n |  | TRUE
159 | bus_LV_4010-10_0_7_node_142 | 0.4 | n |  | TRUE
160 | bus_LV_4010-10_0_7_node_144 | 0.4 | n |  | TRUE
161 | bus_LV_4010-10_0_7_node_147 | 0.4 | n |  | TRUE
162 | bus_LV_4010-10_0_7_node_159 | 0.4 | n |  | TRUE
163 | bus_LV_4010-10_0_7_node_154 | 0.4 | n |  | TRUE
164 | bus_LV_4010-10_0_7_node_158 | 0.4 | n |  | TRUE
165 | bus_LV_4010-10_0_7_node_160 | 0.4 | n |  | TRUE
166 | bus_LV_4010-10_0_7_node_161 | 0.4 | n |  | TRUE
167 | bus_LV_4010-10_0_7_node_162 | 0.4 | n |  | TRUE
168 | bus_LV_4010-10_0_7_node_163 | 0.4 | n |  | TRUE
169 | bus_LV_4010-10_0_7_node_165 | 0.4 | n |  | TRUE
170 | bus_LV_4010-10_0_7_node_164 | 0.4 | n |  | TRUE
171 | bus_LV_4010-10_0_7_node_168 | 0.4 | n |  | TRUE
172 | bus_LV_4010-10_0_7_node_177 | 0.4 | n |  | TRUE
173 | bus_LV_4010-10_0_7_node_180 | 0.4 | n |  | TRUE
174 | bus_LV_4010-10_0_7_node_171 | 0.4 | n |  | TRUE
175 | bus_LV_4010-10_0_7_node_172 | 0.4 | n |  | TRUE
176 | bus_LV_4010-10_0_7_node_175 | 0.4 | n |  | TRUE
177 | bus_MV_419_0_node_112 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4010-10_0_7_load_0 | 0 | 0.0091357 | 0.0022896 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4010-10_0_7_load_1 | 2 | 0.0065394 | 0.0016389 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4010-10_0_7_load_5 | 5 | 0.00091439 | 0.00022917 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4010-10_0_7_load_8 | 7 | 0.002531 | 0.00063433 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4010-10_0_7_load_6 | 8 | 0.014259 | 0.0035736 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4010-10_0_7_load_12 | 9 | 0.012237 | 0.0030668 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4010-10_0_7_load_13 | 13 | 0.003823 | 0.00095813 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4010-10_0_7_load_185 | 14 | 0.0029305 | 0.00073445 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4010-10_0_7_load_133 | 15 | 0.0032483 | 0.0008141 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4010-10_0_7_load_132 | 16 | 0.0051067 | 0.0012799 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4010-10_0_7_load_179 | 17 | 0.0031044 | 0.00077804 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4010-10_0_7_load_143 | 19 | 0.0051209 | 0.0012834 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4010-10_0_7_load_131 | 20 | 0.0029676 | 0.00074376 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4010-10_0_7_load_181 | 22 | 0.0068756 | 0.0017232 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4010-10_0_7_load_15 | 24 | 0.001695 | 0.00042481 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4010-10_0_7_load_16 | 25 | 0.0015019 | 0.00037641 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4010-10_0_7_load_18 | 26 | 0.0014628 | 0.00036661 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4010-10_0_7_load_19 | 28 | 0.002033 | 0.00050952 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4010-10_0_7_load_28 | 30 | 0.0016451 | 0.00041231 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4010-10_0_7_load_29 | 31 | 0.0031405 | 0.00078707 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4010-10_0_7_load_21 | 32 | 0.0014947 | 0.00037461 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4010-10_0_7_load_22 | 33 | 0.0017569 | 0.00044033 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4010-10_0_7_load_26 | 34 | 0.001246 | 0.00031228 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4010-10_0_7_load_24 | 35 | 0.0013824 | 0.00034646 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4010-10_0_7_load_31 | 36 | 0.001263 | 0.00031653 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4010-10_0_7_load_37 | 37 | 0.0080371 | 0.0020143 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4010-10_0_7_load_25 | 38 | 0.0012045 | 0.00030188 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4010-10_0_7_load_27 | 39 | 0.0018963 | 0.00047527 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4010-10_0_7_load_30 | 40 | 0.002332 | 0.00058446 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4010-10_0_7_load_32 | 42 | 0.0019731 | 0.0004945 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4010-10_0_7_load_33 | 43 | 0.0026686 | 0.00066882 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4010-10_0_7_load_34 | 44 | 0.011276 | 0.002826 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4010-10_0_7_load_41 | 48 | 0.0021081 | 0.00052833 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4010-10_0_7_load_150 | 49 | 0.014076 | 0.0035278 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4010-10_0_7_load_148 | 50 | 0.0048811 | 0.0012233 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4010-10_0_7_load_145 | 52 | 0.0013727 | 0.00034402 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4010-10_0_7_load_152 | 53 | 0.0053355 | 0.0013372 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4010-10_0_7_load_39 | 55 | 0.0084704 | 0.0021229 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4010-10_0_7_load_155 | 57 | 0.00075868 | 0.00019014 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4010-10_0_7_load_45 | 59 | 0.0011334 | 0.00028407 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4010-10_0_7_load_146 | 60 | 0.0043556 | 0.0010916 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4010-10_0_7_load_153 | 61 | 0.0047305 | 0.0011856 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4010-10_0_7_load_49 | 63 | 0.0048408 | 0.0012132 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4010-10_0_7_load_47 | 64 | 0.0043008 | 0.0010779 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4010-10_0_7_load_52 | 65 | 0.0018947 | 0.00047485 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4010-10_0_7_load_48 | 66 | 0.0017563 | 0.00044018 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4010-10_0_7_load_44 | 67 | 0.0028804 | 0.00072191 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4010-10_0_7_load_53 | 68 | 0.0042222 | 0.0010582 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4010-10_0_7_load_51 | 69 | 0.0011683 | 0.0002928 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4010-10_0_7_load_54 | 70 | 0.0081651 | 0.0020464 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4010-10_0_7_load_58 | 75 | 0.013153 | 0.0032966 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4010-10_0_7_load_186 | 76 | 0.014694 | 0.0036826 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4010-10_0_7_load_62 | 79 | 0.004885 | 0.0012243 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4010-10_0_7_load_68 | 81 | 0.0050537 | 0.0012666 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4010-10_0_7_load_64 | 82 | 0.001511 | 0.00037869 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4010-10_0_7_load_69 | 85 | 0.0035208 | 0.00088239 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4010-10_0_7_load_70 | 86 | 0.0049415 | 0.0012385 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4010-10_0_7_load_67 | 87 | 0.0099105 | 0.0024838 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4010-10_0_7_load_80 | 88 | 0.010141 | 0.0025415 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4010-10_0_7_load_100 | 90 | 0.0076574 | 0.0019191 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4010-10_0_7_load_81 | 91 | 0.010428 | 0.0026136 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4010-10_0_7_load_101 | 93 | 0.0058456 | 0.001465 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4010-10_0_7_load_71 | 94 | 0.001108 | 0.00027768 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4010-10_0_7_load_112 | 98 | 0.0031518 | 0.00078992 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4010-10_0_7_load_138 | 99 | 0.00049647 | 0.00012443 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4010-10_0_7_load_137 | 100 | 0.0071976 | 0.0018039 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4010-10_0_7_load_128 | 102 | 0.00035898 | 8.9969e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4010-10_0_7_load_130 | 104 | 0.00050804 | 0.00012733 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4010-10_0_7_load_129 | 105 | 0.00044681 | 0.00011198 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4010-10_0_7_load_111 | 106 | 0.0098205 | 0.0024612 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4010-10_0_7_load_109 | 107 | 0.0019187 | 0.00048086 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4010-10_0_7_load_79 | 108 | 0.00703 | 0.0017619 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4010-10_0_7_load_103 | 110 | 0.0031096 | 0.00077934 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4010-10_0_7_load_83 | 112 | 0.0094432 | 0.0023667 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4010-10_0_7_load_84 | 113 | 0.010288 | 0.0025784 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4010-10_0_7_load_85 | 114 | 0.0096696 | 0.0024234 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4010-10_0_7_load_90 | 115 | 0.0032471 | 0.0008138 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4010-10_0_7_load_86 | 116 | 0.010917 | 0.0027361 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4010-10_0_7_load_151 | 120 | 0.012605 | 0.003159 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4010-10_0_7_load_92 | 122 | 0.0069394 | 0.0017392 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4010-10_0_7_load_102 | 123 | 0.0033056 | 0.00082846 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4010-10_0_7_load_99 | 124 | 0.0035338 | 0.00088565 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4010-10_0_7_load_104 | 125 | 0.0037883 | 0.00094943 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4010-10_0_7_load_98 | 126 | 0.0064646 | 0.0016202 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4010-10_0_7_load_96 | 129 | 0.0032943 | 0.00082564 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4010-10_0_7_load_113 | 130 | 0.0031164 | 0.00078105 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4010-10_0_7_load_166 | 131 | 0.0049748 | 0.0012468 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4010-10_0_7_load_157 | 132 | 0.0027169 | 0.00068091 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4010-10_0_7_load_156 | 134 | 0.0010372 | 0.00025996 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4010-10_0_7_load_106 | 135 | 0.0028061 | 0.00070328 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4010-10_0_7_load_107 | 136 | 0.0058336 | 0.001462 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4010-10_0_7_load_108 | 137 | 0.0029493 | 0.00073917 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4010-10_0_7_load_114 | 138 | 0.0016693 | 0.00041836 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4010-10_0_7_load_116 | 139 | 0.0020842 | 0.00052235 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4010-10_0_7_load_115 | 140 | 0.0028497 | 0.00071421 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4010-10_0_7_load_117 | 141 | 0.0026726 | 0.0006698 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4010-10_0_7_load_127 | 143 | 0.0026687 | 0.00066883 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4010-10_0_7_load_120 | 144 | 0.0076822 | 0.0019254 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4010-10_0_7_load_119 | 145 | 0.0066109 | 0.0016568 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4010-10_0_7_load_169 | 148 | 0.0046125 | 0.001156 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4010-10_0_7_load_170 | 151 | 0.0025603 | 0.00064167 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4010-10_0_7_load_134 | 152 | 0.01163 | 0.0029148 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4010-10_0_7_load_174 | 153 | 0.0047067 | 0.0011796 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4010-10_0_7_load_182 | 154 | 0.0083302 | 0.0020877 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4010-10_0_7_load_173 | 155 | 0.0044572 | 0.0011171 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4010-10_0_7_load_139 | 156 | 0.0041301 | 0.0010351 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4010-10_0_7_load_140 | 157 | 0.0024693 | 0.00061886 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4010-10_0_7_load_142 | 159 | 0.00068066 | 0.00017059 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4010-10_0_7_load_144 | 160 | 0.0016098 | 0.00040346 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4010-10_0_7_load_159 | 162 | 0.0040721 | 0.0010206 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4010-10_0_7_load_154 | 163 | 0.004505 | 0.0011291 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4010-10_0_7_load_158 | 164 | 0.0019061 | 0.00047772 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4010-10_0_7_load_161 | 166 | 0.0072051 | 0.0018058 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4010-10_0_7_load_162 | 167 | 0.0043274 | 0.0010845 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4010-10_0_7_load_163 | 168 | 0.0047692 | 0.0011953 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4010-10_0_7_load_165 | 169 | 0.0097437 | 0.002442 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4010-10_0_7_load_164 | 170 | 0.0059363 | 0.0014878 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4010-10_0_7_load_180 | 173 | 0.0012306 | 0.00030843 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4010-10_0_7_load_172 | 175 | 0.0013699 | 0.00034333 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4010-10_0_7_load_175 | 176 | 0.0042847 | 0.0010739 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 121 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4010-10_0_7_line_0 |  | 0 | 1 | 0.021998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4010-10_0_7_line_1 |  | 1 | 4 | 0.025441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4010-10_0_7_line_2 |  | 1 | 5 | 0.02547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4010-10_0_7_line_3 |  | 2 | 3 | 0.026138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4010-10_0_7_line_4 |  | 3 | 6 | 0.020533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4010-10_0_7_line_5 |  | 4 | 7 | 0.015631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4010-10_0_7_line_6 |  | 4 | 8 | 0.031291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4010-10_0_7_line_7 |  | 5 | 9 | 0.033679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4010-10_0_7_line_8 |  | 6 | 10 | 0.034817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4010-10_0_7_line_9 |  | 6 | 11 | 0.011938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4010-10_0_7_line_10 |  | 7 | 12 | 0.019404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4010-10_0_7_line_11 |  | 9 | 13 | 0.048051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4010-10_0_7_line_12 |  | 10 | 14 | 0.022871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4010-10_0_7_line_13 |  | 11 | 15 | 0.022389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4010-10_0_7_line_14 |  | 11 | 16 | 0.013781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4010-10_0_7_line_15 |  | 12 | 17 | 0.03268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4010-10_0_7_line_16 |  | 12 | 18 | 0.016303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4010-10_0_7_line_17 |  | 14 | 19 | 0.0065477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4010-10_0_7_line_18 |  | 16 | 20 | 0.027939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4010-10_0_7_line_19 |  | 17 | 171 | 0.0067211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4010-10_0_7_line_20 |  | 18 | 162 | 0.023673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4010-10_0_7_line_21 |  | 18 | 161 | 0.0088927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4010-10_0_7_line_22 |  | 19 | 158 | 0.01326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4010-10_0_7_line_23 |  | 21 | 22 | 0.01862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4010-10_0_7_line_24 |  | 21 | 23 | 0.04632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4010-10_0_7_line_25 |  | 23 | 153 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4010-10_0_7_line_26 |  | 24 | 25 | 0.023275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4010-10_0_7_line_27 |  | 25 | 26 | 0.024058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4010-10_0_7_line_28 |  | 26 | 27 | 0.013974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4010-10_0_7_line_29 |  | 27 | 30 | 0.011341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4010-10_0_7_line_30 |  | 27 | 31 | 0.045849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4010-10_0_7_line_31 |  | 28 | 29 | 0.016681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4010-10_0_7_line_32 |  | 29 | 32 | 0.013025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4010-10_0_7_line_33 |  | 29 | 33 | 0.044406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4010-10_0_7_line_34 |  | 30 | 36 | 0.023115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4010-10_0_7_line_35 |  | 31 | 37 | 0.036186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4010-10_0_7_line_36 |  | 32 | 34 | 0.024224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4010-10_0_7_line_37 |  | 34 | 35 | 0.0012848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4010-10_0_7_line_38 |  | 35 | 38 | 0.023694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4010-10_0_7_line_39 |  | 36 | 40 | 0.0036272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4010-10_0_7_line_40 |  | 37 | 41 | 0.023092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4010-10_0_7_line_41 |  | 38 | 39 | 0.013257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4010-10_0_7_line_42 |  | 39 | 40 | 0.0089471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4010-10_0_7_line_43 |  | 41 | 55 | 0.024866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4010-10_0_7_line_44 |  | 42 | 43 | 0.022948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4010-10_0_7_line_45 |  | 42 | 44 | 0.028158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4010-10_0_7_line_46 |  | 43 | 45 | 0.023692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4010-10_0_7_line_47 |  | 44 | 46 | 0.025539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4010-10_0_7_line_48 |  | 45 | 47 | 0.03146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4010-10_0_7_line_49 |  | 45 | 48 | 0.012251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4010-10_0_7_line_50 |  | 46 | 49 | 0.021903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4010-10_0_7_line_51 |  | 47 | 50 | 0.034256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_4010-10_0_7_line_52 |  | 47 | 51 | 0.032675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4010-10_0_7_line_53 |  | 47 | 52 | 0.0196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4010-10_0_7_line_54 |  | 48 | 53 | 0.0084801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4010-10_0_7_line_55 |  | 50 | 57 | 0.010854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_4010-10_0_7_line_56 |  | 51 | 58 | 0.017151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4010-10_0_7_line_57 |  | 51 | 59 | 0.01899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4010-10_0_7_line_58 |  | 52 | 60 | 0.01634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4010-10_0_7_line_59 |  | 53 | 61 | 0.014901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4010-10_0_7_line_60 |  | 54 | 55 | 0.01548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4010-10_0_7_line_61 |  | 54 | 56 | 0.013442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4010-10_0_7_line_62 |  | 56 | 116 | 0.032896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4010-10_0_7_line_63 |  | 57 | 163 | 0.0062463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_4010-10_0_7_line_64 |  | 58 | 68 | 0.013041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4010-10_0_7_line_65 |  | 58 | 69 | 0.013701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4010-10_0_7_line_66 |  | 59 | 67 | 0.025995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4010-10_0_7_line_67 |  | 60 | 161 | 0.017086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4010-10_0_7_line_68 |  | 62 | 63 | 0.0017667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4010-10_0_7_line_69 |  | 62 | 64 | 0.013369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4010-10_0_7_line_70 |  | 63 | 65 | 0.012619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4010-10_0_7_line_71 |  | 64 | 66 | 0.02261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4010-10_0_7_line_72 |  | 65 | 69 | 0.015345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4010-10_0_7_line_73 |  | 70 | 71 | 0.055377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4010-10_0_7_line_74 |  | 71 | 72 | 0.012069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4010-10_0_7_line_75 |  | 72 | 73 | 0.041302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4010-10_0_7_line_76 |  | 73 | 74 | 0.044952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4010-10_0_7_line_77 |  | 73 | 75 | 0.045271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4010-10_0_7_line_78 |  | 74 | 80 | 0.018637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4010-10_0_7_line_79 |  | 75 | 78 | 0.035792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4010-10_0_7_line_80 |  | 76 | 77 | 0.040168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4010-10_0_7_line_81 |  | 77 | 78 | 0.043112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4010-10_0_7_line_82 |  | 78 | 79 | 0.047848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4010-10_0_7_line_83 |  | 80 | 81 | 0.013792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4010-10_0_7_line_84 |  | 81 | 83 | 0.0095289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4010-10_0_7_line_85 |  | 82 | 83 | 0.019271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4010-10_0_7_line_86 |  | 82 | 84 | 0.020316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4010-10_0_7_line_87 |  | 84 | 85 | 0.013454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4010-10_0_7_line_88 |  | 84 | 86 | 0.02108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4010-10_0_7_line_89 |  | 85 | 89 | 0.025997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4010-10_0_7_line_90 |  | 86 | 90 | 0.0045004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4010-10_0_7_line_91 |  | 87 | 88 | 0.02719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4010-10_0_7_line_92 |  | 88 | 91 | 0.0060624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4010-10_0_7_line_93 |  | 89 | 92 | 0.004524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4010-10_0_7_line_94 |  | 90 | 93 | 0.0312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4010-10_0_7_line_95 |  | 91 | 111 | 0.018229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4010-10_0_7_line_96 |  | 92 | 95 | 0.031842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4010-10_0_7_line_97 |  | 93 | 109 | 0.015994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4010-10_0_7_line_98 |  | 94 | 95 | 0.091896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4010-10_0_7_line_99 |  | 95 | 96 | 0.038101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4010-10_0_7_line_100 |  | 96 | 97 | 0.040643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4010-10_0_7_line_101 |  | 96 | 98 | 0.014922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4010-10_0_7_line_102 |  | 97 | 99 | 0.043243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4010-10_0_7_line_103 |  | 99 | 100 | 0.058967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4010-10_0_7_line_104 |  | 100 | 149 | 0.053818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4010-10_0_7_line_105 |  | 101 | 102 | 0.010195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4010-10_0_7_line_106 |  | 101 | 103 | 0.0466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4010-10_0_7_line_107 |  | 102 | 105 | 0.018459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4010-10_0_7_line_108 |  | 103 | 147 | 0.02767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4010-10_0_7_line_109 |  | 103 | 145 | 0.012525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4010-10_0_7_line_110 |  | 104 | 105 | 0.014855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4010-10_0_7_line_111 |  | 106 | 107 | 0.024248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4010-10_0_7_line_112 |  | 107 | 136 | 0.0045343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4010-10_0_7_line_113 |  | 108 | 109 | 0.0011292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4010-10_0_7_line_114 |  | 109 | 110 | 0.030182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4010-10_0_7_line_115 |  | 110 | 125 | 0.00028094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4010-10_0_7_line_116 |  | 111 | 112 | 0.012405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4010-10_0_7_line_117 |  | 111 | 113 | 0.020953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4010-10_0_7_line_118 |  | 112 | 114 | 0.031984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4010-10_0_7_line_119 |  | 113 | 115 | 0.024556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4010-10_0_7_line_120 |  | 114 | 116 | 0.020064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4010-10_0_7_line_121 |  | 115 | 117 | 0.028407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4010-10_0_7_line_122 |  | 117 | 123 | 0.0096241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4010-10_0_7_line_123 |  | 117 | 124 | 0.011349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
124 | LV_4010-10_0_7_line_124 |  | 118 | 119 | 0.009816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4010-10_0_7_line_125 |  | 118 | 120 | 0.021919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4010-10_0_7_line_126 |  | 119 | 121 | 0.030013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4010-10_0_7_line_127 |  | 119 | 122 | 0.033126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4010-10_0_7_line_128 |  | 121 | 131 | 0.020867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_4010-10_0_7_line_129 |  | 121 | 132 | 0.0086152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_4010-10_0_7_line_130 |  | 123 | 125 | 0.016368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4010-10_0_7_line_131 |  | 124 | 126 | 0.0090196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_4010-10_0_7_line_132 |  | 126 | 129 | 0.012196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
133 | LV_4010-10_0_7_line_133 |  | 127 | 128 | 0.006243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
134 | LV_4010-10_0_7_line_134 |  | 127 | 129 | 0.012711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_4010-10_0_7_line_135 |  | 128 | 130 | 0.037062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4010-10_0_7_line_136 |  | 128 | 131 | 0.016832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_4010-10_0_7_line_137 |  | 130 | 133 | 0.014129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4010-10_0_7_line_138 |  | 132 | 134 | 0.036806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_4010-10_0_7_line_139 |  | 133 | 138 | 0.010857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4010-10_0_7_line_140 |  | 133 | 137 | 0.014923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4010-10_0_7_line_141 |  | 134 | 163 | 0.0095263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_4010-10_0_7_line_142 |  | 135 | 136 | 0.021985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4010-10_0_7_line_143 |  | 135 | 137 | 0.0019051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4010-10_0_7_line_144 |  | 138 | 139 | 0.024174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4010-10_0_7_line_145 |  | 139 | 140 | 0.0031219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4010-10_0_7_line_146 |  | 140 | 141 | 0.024725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4010-10_0_7_line_147 |  | 141 | 142 | 0.018618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4010-10_0_7_line_148 |  | 142 | 143 | 0.0056582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4010-10_0_7_line_149 |  | 142 | 144 | 0.012044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4010-10_0_7_line_150 |  | 143 | 146 | 0.012586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4010-10_0_7_line_151 |  | 144 | 147 | 0.025447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4010-10_0_7_line_152 |  | 146 | 148 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4010-10_0_7_line_153 |  | 148 | 151 | 0.013942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4010-10_0_7_line_154 |  | 149 | 150 | 0.007185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4010-10_0_7_line_155 |  | 150 | 152 | 0.019926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4010-10_0_7_line_156 |  | 151 | 174 | 0.030646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4010-10_0_7_line_157 |  | 153 | 176 | 0.013375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4010-10_0_7_line_158 |  | 154 | 155 | 0.011582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4010-10_0_7_line_159 |  | 155 | 174 | 0.013329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4010-10_0_7_line_160 |  | 156 | 157 | 0.036393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4010-10_0_7_line_161 |  | 156 | 158 | 0.017364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4010-10_0_7_line_162 |  | 157 | 159 | 0.0013375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4010-10_0_7_line_163 |  | 159 | 160 | 0.010769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4010-10_0_7_line_164 |  | 160 | 161 | 0.017732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4010-10_0_7_line_165 |  | 162 | 164 | 0.0068633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4010-10_0_7_line_166 |  | 164 | 165 | 0.0081587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4010-10_0_7_line_167 |  | 165 | 166 | 0.030776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4010-10_0_7_line_168 |  | 165 | 167 | 0.030696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4010-10_0_7_line_169 |  | 166 | 168 | 0.019135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4010-10_0_7_line_170 |  | 167 | 169 | 0.024829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4010-10_0_7_line_171 |  | 168 | 170 | 0.0069018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4010-10_0_7_line_172 |  | 171 | 172 | 0.008156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4010-10_0_7_line_173 |  | 172 | 173 | 0.013784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4010-10_0_7_line_174 |  | 174 | 175 | 0.016105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4010-10_0_7_line_175 |  | 175 | 176 | 0.011859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4010-10_0_7_trafo_97 | 0.63 MVA 20/0.4 kV | 177 | 121 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2646001.7774 | 1245541.1403 | 2645980.2411 | 1245545.6216
1 | 2646001.7774 | 1245541.1403 | 2646008.356 | 1245565.7187
2 | 2646001.7774 | 1245541.1403 | 2645997.7416 | 1245515.9923
3 | 2645911.1286 | 1245571.9589 | 2645923.1003 | 1245568.427 | 2645923.6567 | 1245563.8949 | 2645932.4808 | 1245561.7105
4 | 2645911.1286 | 1245571.9589 | 2645914.0868 | 1245584.101 | 2645916.2026 | 1245591.8558
5 | 2646008.356 | 1245565.7187 | 2646023.4349 | 1245561.5993
6 | 2646008.356 | 1245565.7187 | 2645978.288 | 1245574.3802
7 | 2645997.7416 | 1245515.9923 | 2645964.5233 | 1245521.5432
8 | 2645916.2026 | 1245591.8558 | 2645923.2402 | 1245617.6941 | 2645925.6967 | 1245625.3515
9 | 2645916.2026 | 1245591.8558 | 2645911.0387 | 1245593.3391 | 2645908.832 | 1245594.4005 | 2645905.1164 | 1245596.1729
10 | 2646042.1529 | 1245556.4857 | 2646023.4349 | 1245561.5993
11 | 2645964.5233 | 1245521.5432 | 2645941.0208 | 1245525.4705 | 2645934.0461 | 1245526.6395 | 2645935.0027 | 1245533.8406 | 2645925.1752 | 1245534.9208
12 | 2645925.6967 | 1245625.3515 | 2645947.408 | 1245618.1612
13 | 2645884.9288 | 1245586.5216 | 2645890.5866 | 1245588.5889 | 2645894.4682 | 1245590.7425 | 2645899.5662 | 1245592.8945 | 2645905.1164 | 1245596.1729
14 | 2645905.1164 | 1245596.1729 | 2645908.1005 | 1245609.6271
15 | 2646042.1529 | 1245556.4857 | 2646041.981 | 1245554.294 | 2646034.9939 | 1245524.6244
16 | 2646042.1529 | 1245556.4857 | 2646043.4018 | 1245572.7395
17 | 2645953.6237 | 1245616.1027 | 2645947.408 | 1245618.1612
18 | 2645912.5354 | 1245637.128 | 2645911.8275 | 1245626.1225 | 2645908.5402 | 1245611.6096 | 2645908.1005 | 1245609.6271
19 | 2646033.5514 | 1245518.0602 | 2646034.6598 | 1245523.2055 | 2646034.9939 | 1245524.6244
20 | 2646043.4018 | 1245572.7395 | 2646066.7414 | 1245568.7782
21 | 2646044.0809 | 1245581.6062 | 2646043.6762 | 1245576.3106 | 2646043.4018 | 1245572.7395
22 | 2645966.2116 | 1245611.9339 | 2645953.6237 | 1245616.1027
23 | 2645980.9368 | 1245460.7588 | 2645979.5697 | 1245479.3286
24 | 2645980.9368 | 1245460.7588 | 2646001.4189 | 1245459.7391 | 2646027.295 | 1245457.7939
25 | 2646027.295 | 1245457.7939 | 2646041.3888 | 1245455.0308
26 | 2646038.4646 | 1245799.3842 | 2646059.1821 | 1245788.7773
27 | 2646059.1821 | 1245788.7773 | 2646080.5965 | 1245777.8136
28 | 2646093.0348 | 1245771.4454 | 2646080.5965 | 1245777.8136
29 | 2646093.0348 | 1245771.4454 | 2646087.0053 | 1245761.8406
30 | 2646093.0348 | 1245771.4454 | 2646133.5892 | 1245750.0563
31 | 2646001.2289 | 1245762.8832 | 2646009.9097 | 1245777.1268
32 | 2646001.2289 | 1245762.8832 | 2646012.6596 | 1245756.6396
33 | 2646001.2289 | 1245762.8832 | 2645975.6553 | 1245726.5805
34 | 2646087.0053 | 1245761.8406 | 2646074.7156 | 1245742.2637
35 | 2646133.5892 | 1245750.0563 | 2646165.5966 | 1245733.175
36 | 2646033.9192 | 1245745.0275 | 2646012.6596 | 1245756.6396
37 | 2646033.9192 | 1245745.0275 | 2646035.0468 | 1245744.4116
38 | 2646055.8407 | 1245733.0538 | 2646035.0468 | 1245744.4116
39 | 2646072.7871 | 1245739.1917 | 2646074.7156 | 1245742.2637
40 | 2646186.0219 | 1245722.4023 | 2646165.5966 | 1245733.175
41 | 2646068.0301 | 1245731.6141 | 2646067.8195 | 1245731.2786 | 2646064.6787 | 1245730.0534 | 2646060.2167 | 1245730.6636 | 2646055.8407 | 1245733.0538
42 | 2646072.7871 | 1245739.1917 | 2646068.0301 | 1245731.6141
43 | 2646186.0219 | 1245722.4023 | 2646178.0477 | 1245698.8497
44 | 2646081.0841 | 1245705.2198 | 2646071.5258 | 1245684.3575
45 | 2646081.0841 | 1245705.2198 | 2646081.0841 | 1245705.2198 | 2646088.593 | 1245709.1696 | 2646107.4598 | 1245703.5928
46 | 2646061.6576 | 1245662.8187 | 2646071.5258 | 1245684.3575
47 | 2646131.9512 | 1245696.3535 | 2646107.4598 | 1245703.5928
48 | 2646061.6576 | 1245662.8187 | 2646048.4924 | 1245634.2309
49 | 2646061.6576 | 1245662.8187 | 2646072.7787 | 1245657.6792
50 | 2646131.9512 | 1245696.3535 | 2646125.5387 | 1245675.4098
51 | 2646048.4924 | 1245634.2309 | 2646059.3083 | 1245626.7876 | 2646079.1869 | 1245619.6336
52 | 2646022.8082 | 1245653.4111 | 2646024.2715 | 1245652.7442 | 2646039.9271 | 1245644.6936 | 2646048.4924 | 1245634.2309
53 | 2646048.4924 | 1245634.2309 | 2646045.4845 | 1245621.7215 | 2646045.4095 | 1245614.9881
54 | 2646072.7787 | 1245657.6792 | 2646080.4765 | 1245654.1218
55 | 2646079.1869 | 1245619.6336 | 2646089.3997 | 1245615.9582
56 | 2646022.8082 | 1245653.4111 | 2646007.1375 | 1245660.4832
57 | 2646022.8082 | 1245653.4111 | 2646031.118 | 1245670.4864
58 | 2646045.4095 | 1245614.9881 | 2646045.2275 | 1245598.6489
59 | 2646094.0026 | 1245647.8709 | 2646080.4765 | 1245654.1218
60 | 2646173.0834 | 1245684.1874 | 2646178.0477 | 1245698.8497
61 | 2646173.0834 | 1245684.1874 | 2646169.2023 | 1245671.3153
62 | 2646169.2023 | 1245671.3153 | 2646199.6106 | 1245658.7668
63 | 2646095.277 | 1245613.8431 | 2646089.3997 | 1245615.9582
64 | 2646007.1375 | 1245660.4832 | 2646004.212 | 1245649.998 | 2646002.697 | 1245648.4651
65 | 2646007.1375 | 1245660.4832 | 2645996.3265 | 1245665.3693 | 2645994.6528 | 1245666.1273
66 | 2646042.4931 | 1245693.8602 | 2646031.118 | 1245670.4864
67 | 2646044.0809 | 1245581.6062 | 2646045.1995 | 1245596.1356 | 2646045.2275 | 1245598.6489
68 | 2645967.5034 | 1245678.2435 | 2645969.1245 | 1245677.5413
69 | 2645967.5034 | 1245678.2435 | 2645975.3398 | 1245689.0754
70 | 2645980.6744 | 1245672.4582 | 2645976.6072 | 1245674.3003 | 2645969.1245 | 1245677.5413
71 | 2645995.5305 | 1245696.9063 | 2645978.1324 | 1245692.9356 | 2645975.3398 | 1245689.0754
72 | 2645994.6528 | 1245666.1273 | 2645980.6744 | 1245672.4582
73 | 2646429.8154 | 1245712.4976 | 2646453.5651 | 1245694.4826 | 2646460.0499 | 1245694.122 | 2646473.0999 | 1245708.0315
74 | 2646429.8154 | 1245712.4976 | 2646423.8841 | 1245701.9776
75 | 2646403.5941 | 1245665.9728 | 2646423.8841 | 1245701.9776
76 | 2646377.354 | 1245629.5436 | 2646399.8311 | 1245659.3056 | 2646403.5941 | 1245665.9728
77 | 2646403.5941 | 1245665.9728 | 2646436.3972 | 1245634.7734
78 | 2646377.354 | 1245629.5436 | 2646367.8394 | 1245613.503
79 | 2646462.3322 | 1245610.1063 | 2646436.3972 | 1245634.7734
80 | 2646490.9871 | 1245639.1277 | 2646461.6703 | 1245666.5864
81 | 2646462.3322 | 1245610.1063 | 2646469.8103 | 1245612.1884 | 2646476.466 | 1245616.0765 | 2646485.7106 | 1245626.0443 | 2646490.9871 | 1245639.1277
82 | 2646462.3322 | 1245610.1063 | 2646462.3607 | 1245606.4708 | 2646441.4625 | 1245583.4808 | 2646438.0177 | 1245583.4539 | 2646430.8501 | 1245589.9875
83 | 2646367.8394 | 1245613.503 | 2646360.9403 | 1245601.5606
84 | 2646356.1738 | 1245593.3096 | 2646360.9403 | 1245601.5606
85 | 2646356.1738 | 1245593.3096 | 2646345.8117 | 1245577.0614
86 | 2646334.8879 | 1245559.9324 | 2646345.8117 | 1245577.0614
87 | 2646334.8879 | 1245559.9324 | 2646327.6533 | 1245548.589
88 | 2646334.8879 | 1245559.9324 | 2646315.7826 | 1245568.841
89 | 2646314.7618 | 1245526.0195 | 2646325.5733 | 1245545.3278 | 2646327.6533 | 1245548.589
90 | 2646315.7826 | 1245568.841 | 2646311.7038 | 1245570.7429
91 | 2646306.6313 | 1245614.1876 | 2646281.5753 | 1245624.7466
92 | 2646275.9887 | 1245627.1009 | 2646281.5753 | 1245624.7466
93 | 2646314.51 | 1245521.5034 | 2646314.7618 | 1245526.0195
94 | 2646289.5745 | 1245562.6006 | 2646293.2061 | 1245573.6274 | 2646302.3133 | 1245575.1216 | 2646311.7038 | 1245570.7429
95 | 2646259.19 | 1245634.1802 | 2646275.9887 | 1245627.1009
96 | 2646314.51 | 1245521.5034 | 2646315.1921 | 1245513.4923 | 2646315.6349 | 1245510.9607 | 2646317.4214 | 1245500.8346 | 2646319.5605 | 1245494.8918 | 2646321.1358 | 1245490.5345
97 | 2646284.5714 | 1245547.4093 | 2646289.5745 | 1245562.6006
98 | 2646321.1358 | 1245490.5345 | 2646365.3015 | 1245511.938 | 2646404.4351 | 1245529.3132
99 | 2646290.0575 | 1245484.3213 | 2646293.4873 | 1245477.5769 | 2646321.1358 | 1245490.5345
100 | 2646290.0575 | 1245484.3213 | 2646293.4873 | 1245477.5769 | 2646280.1861 | 1245471.3469 | 2646283.5988 | 1245458.0647 | 2646282.6978 | 1245453.4768
101 | 2646290.0575 | 1245484.3213 | 2646275.9302 | 1245489.1267
102 | 2646282.6978 | 1245453.4768 | 2646282.0436 | 1245450.1695 | 2646279.0385 | 1245445.0983 | 2646256.872 | 1245429.5708 | 2646250.0112 | 1245428.7196
103 | 2646250.0112 | 1245428.7196 | 2646248.1694 | 1245428.4911 | 2646236.6136 | 1245429.0126 | 2646226.2458 | 1245433.1679 | 2646195.2686 | 1245418.2697
104 | 2646150.3946 | 1245391.1388 | 2646159.6691 | 1245394.4686 | 2646163.081 | 1245398.7424 | 2646166.8884 | 1245404.6204 | 2646195.2686 | 1245418.2697
105 | 2646231.0988 | 1245448.3491 | 2646226.4414 | 1245456.5516 | 2646226.2733 | 1245457.2951
106 | 2646198.493 | 1245453.9101 | 2646205.9866 | 1245436.5902 | 2646231.0988 | 1245448.3491
107 | 2646226.2733 | 1245457.2951 | 2646224.3443 | 1245465.8303 | 2646227.1427 | 1245470.2884 | 2646231.1051 | 1245472.3014
108 | 2646173.258 | 1245442.395 | 2646198.493 | 1245453.9101
109 | 2646198.493 | 1245453.9101 | 2646198.2715 | 1245457.1327 | 2646201.0227 | 1245466.0114
110 | 2646231.1051 | 1245472.3014 | 2646234.8109 | 1245474.1841 | 2646241.52 | 1245472.2239 | 2646243.0839 | 1245468.8609
111 | 2646210.5936 | 1245522.9852 | 2646220.576 | 1245521.8604 | 2646234.7775 | 1245521.7355
112 | 2646210.5936 | 1245522.9852 | 2646209.3167 | 1245523.1291 | 2646206.1306 | 1245523.7666
113 | 2646284.5714 | 1245547.4093 | 2646285.6099 | 1245546.9657
114 | 2646284.5714 | 1245547.4093 | 2646279.3639 | 1245549.6257 | 2646256.0922 | 1245557.3567
115 | 2646256.0922 | 1245557.3567 | 2646255.8255 | 1245557.4453
116 | 2646259.19 | 1245634.1802 | 2646247.7227 | 1245638.9124
117 | 2646259.19 | 1245634.1802 | 2646251.1471 | 1245614.832
118 | 2646247.7227 | 1245638.9124 | 2646218.1576 | 1245651.113
119 | 2646251.1471 | 1245614.832 | 2646241.7212 | 1245592.1571
120 | 2646218.1576 | 1245651.113 | 2646199.6106 | 1245658.7668
121 | 2646231.2036 | 1245565.7723 | 2646236.4087 | 1245579.3774 | 2646241.7212 | 1245592.1571
122 | 2646231.2036 | 1245565.7723 | 2646240.3109 | 1245562.6612
123 | 2646231.2036 | 1245565.7723 | 2646220.466 | 1245569.4455
124 | 2646157.9147 | 1245633.5358 | 2646155.2155 | 1245624.0975
125 | 2646157.9147 | 1245633.5358 | 2646136.843 | 1245639.5728
126 | 2646155.2155 | 1245624.0975 | 2646152.4502 | 1245614.414 | 2646146.9786 | 1245595.2365
127 | 2646155.2155 | 1245624.0975 | 2646186.6124 | 1245613.5356
128 | 2646146.9786 | 1245595.2365 | 2646166.6085 | 1245588.158
129 | 2646146.9786 | 1245595.2365 | 2646138.8723 | 1245598.1538
130 | 2646255.8255 | 1245557.4453 | 2646246.8916 | 1245560.4132 | 2646240.3109 | 1245562.6612
131 | 2646211.9319 | 1245572.3648 | 2646220.466 | 1245569.4455
132 | 2646211.9319 | 1245572.3648 | 2646200.3927 | 1245576.3123
133 | 2646188.3663 | 1245580.4263 | 2646182.4426 | 1245582.4482
134 | 2646188.3663 | 1245580.4263 | 2646200.3927 | 1245576.3123
135 | 2646182.4426 | 1245582.4482 | 2646172.366 | 1245546.7819
136 | 2646182.4426 | 1245582.4482 | 2646166.6085 | 1245588.158
137 | 2646168.5246 | 1245533.1851 | 2646172.366 | 1245546.7819
138 | 2646104.2405 | 1245610.6172 | 2646138.8723 | 1245598.1538
139 | 2646168.5246 | 1245533.1851 | 2646165.5716 | 1245522.7376
140 | 2646168.5246 | 1245533.1851 | 2646182.8036 | 1245528.8479
141 | 2646095.277 | 1245613.8431 | 2646104.2405 | 1245610.6172
142 | 2646184.6265 | 1245528.2942 | 2646186.7979 | 1245527.6346 | 2646206.1306 | 1245523.7666
143 | 2646184.6265 | 1245528.2942 | 2646182.8036 | 1245528.8479
144 | 2646165.5716 | 1245522.7376 | 2646158.9965 | 1245499.4754
145 | 2646158.1474 | 1245496.4712 | 2646158.9965 | 1245499.4754
146 | 2646151.4224 | 1245472.6786 | 2646158.1474 | 1245496.4712
147 | 2646151.4224 | 1245472.6786 | 2646146.3563 | 1245454.7607
148 | 2646146.3563 | 1245454.7607 | 2646144.8174 | 1245449.3158
149 | 2646146.3563 | 1245454.7607 | 2646156.964 | 1245452.7752 | 2646158.183 | 1245453.0591
150 | 2646140.3095 | 1245437.6356 | 2646141.9282 | 1245440.3056 | 2646144.3123 | 1245447.5289 | 2646144.8174 | 1245449.3158
151 | 2646173.258 | 1245442.395 | 2646169.5054 | 1245455.6968 | 2646158.183 | 1245453.0591
152 | 2646140.3095 | 1245437.6356 | 2646136.5223 | 1245436.928 | 2646131.6688 | 1245437.335 | 2646125.7119 | 1245438.5024
153 | 2646112.0298 | 1245441.1838 | 2646125.7119 | 1245438.5024
154 | 2646153.3091 | 1245384.5682 | 2646150.3946 | 1245391.1388
155 | 2646153.3091 | 1245384.5682 | 2646144.8586 | 1245384.0911 | 2646138.1463 | 1245384.5169 | 2646133.4541 | 1245385.1631
156 | 2646081.9561 | 1245447.0775 | 2646112.0298 | 1245441.1838
157 | 2646041.3888 | 1245455.0308 | 2646054.5142 | 1245452.4575
158 | 2646084.3904 | 1245433.9725 | 2646086.5057 | 1245422.5855 | 2646086.5057 | 1245422.5855
159 | 2646081.9561 | 1245447.0775 | 2646084.3904 | 1245433.9725
160 | 2645982.5364 | 1245606.0173 | 2645994.054 | 1245601.8429 | 2646016.1881 | 1245592.2017
161 | 2645966.2116 | 1245611.9339 | 2645982.5364 | 1245606.0173
162 | 2646016.1881 | 1245592.2017 | 2646016.8258 | 1245591.9239 | 2646017.4261 | 1245591.6967
163 | 2646017.4261 | 1245591.6967 | 2646027.4974 | 1245587.8841
164 | 2646044.0809 | 1245581.6062 | 2646027.4974 | 1245587.8841
165 | 2646073.5079 | 1245567.6297 | 2646066.7414 | 1245568.7782
166 | 2646081.5516 | 1245566.2646 | 2646073.5079 | 1245567.6297
167 | 2646081.5516 | 1245566.2646 | 2646088.9727 | 1245565.0102 | 2646087.598 | 1245559.1401 | 2646104.4193 | 1245555.4519
168 | 2646081.5516 | 1245566.2646 | 2646079.1296 | 1245553.2149 | 2646075.8105 | 1245536.1104
169 | 2646123.1107 | 1245551.3536 | 2646104.4193 | 1245555.4519
170 | 2646071.0808 | 1245511.736 | 2646075.8105 | 1245536.1104
171 | 2646123.1107 | 1245551.3536 | 2646126.7767 | 1245550.5498 | 2646129.6818 | 1245549.3354
172 | 2646033.5514 | 1245518.0602 | 2646031.8378 | 1245510.086
173 | 2646031.8378 | 1245510.086 | 2646018.3391 | 1245512.8779
174 | 2646081.9561 | 1245447.0775 | 2646066.1518 | 1245450.176
175 | 2646066.1518 | 1245450.176 | 2646054.5142 | 1245452.4575

## bus_geodata
| x | y | coords
0 | 2645980.2411 | 1245545.6216
1 | 2646001.7774 | 1245541.1403
2 | 2645932.4808 | 1245561.7105
3 | 2645911.1286 | 1245571.9589
4 | 2646008.356 | 1245565.7187
5 | 2645997.7416 | 1245515.9923
6 | 2645916.2026 | 1245591.8558
7 | 2646023.4349 | 1245561.5993
8 | 2645978.288 | 1245574.3802
9 | 2645964.5233 | 1245521.5432
10 | 2645925.6967 | 1245625.3515
11 | 2645905.1164 | 1245596.1729
12 | 2646042.1529 | 1245556.4857
13 | 2645925.1752 | 1245534.9208
14 | 2645947.408 | 1245618.1612
15 | 2645884.9288 | 1245586.5216
16 | 2645908.1005 | 1245609.6271
17 | 2646034.9939 | 1245524.6244
18 | 2646043.4018 | 1245572.7395
19 | 2645953.6237 | 1245616.1027
20 | 2645912.5354 | 1245637.128
21 | 2645980.9368 | 1245460.7588
22 | 2645979.5697 | 1245479.3286
23 | 2646027.295 | 1245457.7939
24 | 2646038.4646 | 1245799.3842
25 | 2646059.1821 | 1245788.7773
26 | 2646080.5965 | 1245777.8136
27 | 2646093.0348 | 1245771.4454
28 | 2646009.9097 | 1245777.1268
29 | 2646001.2289 | 1245762.8832
30 | 2646087.0053 | 1245761.8406
31 | 2646133.5892 | 1245750.0563
32 | 2646012.6596 | 1245756.6396
33 | 2645975.6553 | 1245726.5805
34 | 2646033.9192 | 1245745.0275
35 | 2646035.0468 | 1245744.4116
36 | 2646074.7156 | 1245742.2637
37 | 2646165.5966 | 1245733.175
38 | 2646055.8407 | 1245733.0538
39 | 2646068.0301 | 1245731.6141
40 | 2646072.7871 | 1245739.1917
41 | 2646186.0219 | 1245722.4023
42 | 2646081.0841 | 1245705.2198
43 | 2646071.5258 | 1245684.3575
44 | 2646107.4598 | 1245703.5928
45 | 2646061.6576 | 1245662.8187
46 | 2646131.9512 | 1245696.3535
47 | 2646048.4924 | 1245634.2309
48 | 2646072.7787 | 1245657.6792
49 | 2646125.5387 | 1245675.4098
50 | 2646079.1869 | 1245619.6336
51 | 2646022.8082 | 1245653.4111
52 | 2646045.4095 | 1245614.9881
53 | 2646080.4765 | 1245654.1218
54 | 2646173.0834 | 1245684.1874
55 | 2646178.0477 | 1245698.8497
56 | 2646169.2023 | 1245671.3153
57 | 2646089.3997 | 1245615.9582
58 | 2646007.1375 | 1245660.4832
59 | 2646031.118 | 1245670.4864
60 | 2646045.2275 | 1245598.6489
61 | 2646094.0026 | 1245647.8709
62 | 2645967.5034 | 1245678.2435
63 | 2645969.1245 | 1245677.5413
64 | 2645975.3398 | 1245689.0754
65 | 2645980.6744 | 1245672.4582
66 | 2645995.5305 | 1245696.9063
67 | 2646042.4931 | 1245693.8602
68 | 2646002.697 | 1245648.4651
69 | 2645994.6528 | 1245666.1273
70 | 2646473.0999 | 1245708.0315
71 | 2646429.8154 | 1245712.4976
72 | 2646423.8841 | 1245701.9776
73 | 2646403.5941 | 1245665.9728
74 | 2646377.354 | 1245629.5436
75 | 2646436.3972 | 1245634.7734
76 | 2646461.6703 | 1245666.5864
77 | 2646490.9871 | 1245639.1277
78 | 2646462.3322 | 1245610.1063
79 | 2646430.8501 | 1245589.9875
80 | 2646367.8394 | 1245613.503
81 | 2646360.9403 | 1245601.5606
82 | 2646345.8117 | 1245577.0614
83 | 2646356.1738 | 1245593.3096
84 | 2646334.8879 | 1245559.9324
85 | 2646327.6533 | 1245548.589
86 | 2646315.7826 | 1245568.841
87 | 2646306.6313 | 1245614.1876
88 | 2646281.5753 | 1245624.7466
89 | 2646314.7618 | 1245526.0195
90 | 2646311.7038 | 1245570.7429
91 | 2646275.9887 | 1245627.1009
92 | 2646314.51 | 1245521.5034
93 | 2646289.5745 | 1245562.6006
94 | 2646404.4351 | 1245529.3132
95 | 2646321.1358 | 1245490.5345
96 | 2646290.0575 | 1245484.3213
97 | 2646282.6978 | 1245453.4768
98 | 2646275.9302 | 1245489.1267
99 | 2646250.0112 | 1245428.7196
100 | 2646195.2686 | 1245418.2697
101 | 2646231.0988 | 1245448.3491
102 | 2646226.2733 | 1245457.2951
103 | 2646198.493 | 1245453.9101
104 | 2646243.0839 | 1245468.8609
105 | 2646231.1051 | 1245472.3014
106 | 2646234.7775 | 1245521.7355
107 | 2646210.5936 | 1245522.9852
108 | 2646285.6099 | 1245546.9657
109 | 2646284.5714 | 1245547.4093
110 | 2646256.0922 | 1245557.3567
111 | 2646259.19 | 1245634.1802
112 | 2646247.7227 | 1245638.9124
113 | 2646251.1471 | 1245614.832
114 | 2646218.1576 | 1245651.113
115 | 2646241.7212 | 1245592.1571
116 | 2646199.6106 | 1245658.7668
117 | 2646231.2036 | 1245565.7723
118 | 2646157.9147 | 1245633.5358
119 | 2646155.2155 | 1245624.0975
120 | 2646136.843 | 1245639.5728
121 | 2646146.9786 | 1245595.2365
122 | 2646186.6124 | 1245613.5356
123 | 2646240.3109 | 1245562.6612
124 | 2646220.466 | 1245569.4455
125 | 2646255.8255 | 1245557.4453
126 | 2646211.9319 | 1245572.3648
127 | 2646188.3663 | 1245580.4263
128 | 2646182.4426 | 1245582.4482
129 | 2646200.3927 | 1245576.3123
130 | 2646172.366 | 1245546.7819
131 | 2646166.6085 | 1245588.158
132 | 2646138.8723 | 1245598.1538
133 | 2646168.5246 | 1245533.1851
134 | 2646104.2405 | 1245610.6172
135 | 2646184.6265 | 1245528.2942
136 | 2646206.1306 | 1245523.7666
137 | 2646182.8036 | 1245528.8479
138 | 2646165.5716 | 1245522.7376
139 | 2646158.9965 | 1245499.4754
140 | 2646158.1474 | 1245496.4712
141 | 2646151.4224 | 1245472.6786
142 | 2646146.3563 | 1245454.7607
143 | 2646144.8174 | 1245449.3158
144 | 2646158.183 | 1245453.0591
145 | 2646201.0227 | 1245466.0114
146 | 2646140.3095 | 1245437.6356
147 | 2646173.258 | 1245442.395
148 | 2646125.7119 | 1245438.5024
149 | 2646150.3946 | 1245391.1388
150 | 2646153.3091 | 1245384.5682
151 | 2646112.0298 | 1245441.1838
152 | 2646133.4541 | 1245385.1631
153 | 2646041.3888 | 1245455.0308
154 | 2646086.5057 | 1245422.5855
155 | 2646084.3904 | 1245433.9725
156 | 2645982.5364 | 1245606.0173
157 | 2646016.1881 | 1245592.2017
158 | 2645966.2116 | 1245611.9339
159 | 2646017.4261 | 1245591.6967
160 | 2646027.4974 | 1245587.8841
161 | 2646044.0809 | 1245581.6062
162 | 2646066.7414 | 1245568.7782
163 | 2646095.277 | 1245613.8431
164 | 2646073.5079 | 1245567.6297
165 | 2646081.5516 | 1245566.2646
166 | 2646104.4193 | 1245555.4519
167 | 2646075.8105 | 1245536.1104
168 | 2646123.1107 | 1245551.3536
169 | 2646071.0808 | 1245511.736
170 | 2646129.6818 | 1245549.3354
171 | 2646033.5514 | 1245518.0602
172 | 2646031.8378 | 1245510.086
173 | 2646018.3391 | 1245512.8779
174 | 2646081.9561 | 1245447.0775
175 | 2646066.1518 | 1245450.176
176 | 2646054.5142 | 1245452.4575
177 | 2646152.4502 | 1245614.414

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1