## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4012-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4012-4_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_4012-4_0_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_4012-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4012-4_0_4_node_59 | 0.4 | n |  | TRUE
5 | bus_LV_4012-4_0_4_node_124 | 0.4 | n |  | TRUE
6 | bus_LV_4012-4_0_4_node_15 | 0.4 | n |  | TRUE
7 | bus_LV_4012-4_0_4_node_56 | 0.4 | n |  | TRUE
8 | bus_LV_4012-4_0_4_node_72 | 0.4 | n |  | TRUE
9 | bus_LV_4012-4_0_4_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_4012-4_0_4_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_4012-4_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_4012-4_0_4_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_4012-4_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_4012-4_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_4012-4_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_4012-4_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_4012-4_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_4012-4_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_4012-4_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_4012-4_0_4_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_4012-4_0_4_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_4012-4_0_4_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_4012-4_0_4_node_36 | 0.4 | n |  | TRUE
24 | bus_LV_4012-4_0_4_node_62 | 0.4 | n |  | TRUE
25 | bus_LV_4012-4_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_4012-4_0_4_node_125 | 0.4 | n |  | TRUE
27 | bus_LV_4012-4_0_4_node_70 | 0.4 | n |  | TRUE
28 | bus_LV_4012-4_0_4_node_67 | 0.4 | n |  | TRUE
29 | bus_LV_4012-4_0_4_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_4012-4_0_4_node_38 | 0.4 | n |  | TRUE
31 | bus_LV_4012-4_0_4_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_4012-4_0_4_node_61 | 0.4 | n |  | TRUE
33 | bus_LV_4012-4_0_4_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_4012-4_0_4_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_4012-4_0_4_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_4012-4_0_4_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_4012-4_0_4_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_4012-4_0_4_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_4012-4_0_4_node_45 | 0.4 | n |  | TRUE
40 | bus_LV_4012-4_0_4_node_40 | 0.4 | n |  | TRUE
41 | bus_LV_4012-4_0_4_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_4012-4_0_4_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_4012-4_0_4_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_4012-4_0_4_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_4012-4_0_4_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_4012-4_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_4012-4_0_4_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_4012-4_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_4012-4_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_4012-4_0_4_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_4012-4_0_4_node_71 | 0.4 | n |  | TRUE
52 | bus_LV_4012-4_0_4_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_4012-4_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_4012-4_0_4_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_4012-4_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_4012-4_0_4_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_4012-4_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_4012-4_0_4_node_119 | 0.4 | n |  | TRUE
59 | bus_LV_4012-4_0_4_node_153 | 0.4 | n |  | TRUE
60 | bus_LV_4012-4_0_4_node_87 | 0.4 | n |  | TRUE
61 | bus_LV_4012-4_0_4_node_152 | 0.4 | n |  | TRUE
62 | bus_LV_4012-4_0_4_node_120 | 0.4 | n |  | TRUE
63 | bus_LV_4012-4_0_4_node_154 | 0.4 | n |  | TRUE
64 | bus_LV_4012-4_0_4_node_117 | 0.4 | n |  | TRUE
65 | bus_LV_4012-4_0_4_node_151 | 0.4 | n |  | TRUE
66 | bus_LV_4012-4_0_4_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_4012-4_0_4_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_4012-4_0_4_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_4012-4_0_4_node_60 | 0.4 | n |  | TRUE
70 | bus_LV_4012-4_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_4012-4_0_4_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_4012-4_0_4_node_126 | 0.4 | n |  | TRUE
73 | bus_LV_4012-4_0_4_node_64 | 0.4 | n |  | TRUE
74 | bus_LV_4012-4_0_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_4012-4_0_4_node_121 | 0.4 | n |  | TRUE
76 | bus_LV_4012-4_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_4012-4_0_4_node_133 | 0.4 | n |  | TRUE
78 | bus_LV_4012-4_0_4_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_4012-4_0_4_node_127 | 0.4 | n |  | TRUE
80 | bus_LV_4012-4_0_4_node_123 | 0.4 | n |  | TRUE
81 | bus_LV_4012-4_0_4_node_122 | 0.4 | n |  | TRUE
82 | bus_LV_4012-4_0_4_node_132 | 0.4 | n |  | TRUE
83 | bus_LV_4012-4_0_4_node_130 | 0.4 | n |  | TRUE
84 | bus_LV_4012-4_0_4_node_131 | 0.4 | n |  | TRUE
85 | bus_LV_4012-4_0_4_node_150 | 0.4 | n |  | TRUE
86 | bus_MV_418_1_node_139 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4012-4_0_4_load_0 | 0 | 0.0020119 | 0.00050424 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4012-4_0_4_load_5 | 2 | 0.00030886 | 7.7408e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4012-4_0_4_load_124 | 5 | 0.0092527 | 0.0023189 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4012-4_0_4_load_48 | 10 | 0.011503 | 0.0028828 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4012-4_0_4_load_14 | 11 | 0.0054178 | 0.0013578 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4012-4_0_4_load_17 | 12 | 0.00072414 | 0.00018149 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4012-4_0_4_load_13 | 13 | 0.0018961 | 0.00047521 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4012-4_0_4_load_6 | 14 | 0.025156 | 0.0063047 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4012-4_0_4_load_10 | 18 | 0.0023622 | 0.00059202 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4012-4_0_4_load_11 | 19 | 0.0063013 | 0.0015793 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4012-4_0_4_load_31 | 21 | 0.0041501 | 0.0010401 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4012-4_0_4_load_27 | 22 | 0.014682 | 0.0036797 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4012-4_0_4_load_62 | 24 | 0.012371 | 0.0031004 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4012-4_0_4_load_12 | 25 | 0.012212 | 0.0030607 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4012-4_0_4_load_125 | 26 | 0.007303 | 0.0018303 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4012-4_0_4_load_70 | 27 | 0.0091867 | 0.0023024 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4012-4_0_4_load_67 | 28 | 0.0097592 | 0.0024459 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4012-4_0_4_load_28 | 29 | 0.0078298 | 0.0019623 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4012-4_0_4_load_38 | 30 | 0.0079909 | 0.0020027 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4012-4_0_4_load_35 | 31 | 0.0031704 | 0.00079457 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4012-4_0_4_load_61 | 32 | 0.0066975 | 0.0016786 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4012-4_0_4_load_18 | 33 | 0.0070621 | 0.0017699 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4012-4_0_4_load_19 | 34 | 0.0018201 | 0.00045615 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4012-4_0_4_load_22 | 37 | 0.0051596 | 0.0012931 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4012-4_0_4_load_37 | 38 | 0.0085821 | 0.0021509 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4012-4_0_4_load_45 | 39 | 0.0059605 | 0.0014938 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4012-4_0_4_load_46 | 41 | 0.0062116 | 0.0015568 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4012-4_0_4_load_23 | 42 | 0.0018046 | 0.00045228 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4012-4_0_4_load_24 | 43 | 0.001657 | 0.00041529 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4012-4_0_4_load_25 | 44 | 0.0019823 | 0.00049681 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4012-4_0_4_load_32 | 46 | 0.002494 | 0.00062505 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4012-4_0_4_load_34 | 49 | 0.0008112 | 0.00020331 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4012-4_0_4_load_29 | 50 | 0.0023755 | 0.00059535 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4012-4_0_4_load_71 | 51 | 0.00556 | 0.0013935 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4012-4_0_4_load_65 | 52 | 0.0030996 | 0.00077683 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4012-4_0_4_load_41 | 55 | 0.0086514 | 0.0021682 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4012-4_0_4_load_39 | 56 | 0.0038902 | 0.00097497 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4012-4_0_4_load_44 | 57 | 0.0045229 | 0.0011336 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4012-4_0_4_load_119 | 58 | 0.0073068 | 0.0018313 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4012-4_0_4_load_152 | 61 | 0.0019502 | 0.00048876 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4012-4_0_4_load_120 | 62 | 0.0073031 | 0.0018303 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4012-4_0_4_load_154 | 63 | 0.0053736 | 0.0013467 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4012-4_0_4_load_117 | 64 | 0.00077059 | 0.00019313 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4012-4_0_4_load_151 | 65 | 0.0019148 | 0.00047988 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4012-4_0_4_load_49 | 66 | 0.001353 | 0.0003391 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4012-4_0_4_load_50 | 67 | 0.0089581 | 0.0022451 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4012-4_0_4_load_52 | 68 | 0.0013879 | 0.00034785 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4012-4_0_4_load_60 | 69 | 0.023323 | 0.0058454 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4012-4_0_4_load_126 | 72 | 0.0065597 | 0.001644 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4012-4_0_4_load_68 | 74 | 0.019362 | 0.0048525 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4012-4_0_4_load_121 | 75 | 0.040665 | 0.010192 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4012-4_0_4_load_133 | 77 | 0.0080433 | 0.0020158 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4012-4_0_4_load_66 | 78 | 0.0034487 | 0.00086433 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4012-4_0_4_load_127 | 79 | 0.015791 | 0.0039577 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4012-4_0_4_load_123 | 80 | 0.021379 | 0.0053582 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4012-4_0_4_load_122 | 81 | 0.0020802 | 0.00052136 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4012-4_0_4_load_132 | 82 | 0.0036584 | 0.00091689 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4012-4_0_4_load_130 | 83 | 0.0061357 | 0.0015378 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4012-4_0_4_load_131 | 84 | 0.0034416 | 0.00086255 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4012-4_0_4_load_150 | 85 | 0.0022245 | 0.00055752 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4012-4_0_4_line_0 |  | 0 | 1 | 0.016475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4012-4_0_4_line_1 |  | 1 | 2 | 0.024283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4012-4_0_4_line_2 |  | 2 | 6 | 0.012216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4012-4_0_4_line_3 |  | 3 | 4 | 0.012938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4012-4_0_4_line_4 |  | 3 | 5 | 0.010453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4012-4_0_4_line_5 |  | 4 | 7 | 0.091158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4012-4_0_4_line_6 |  | 5 | 8 | 0.019132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4012-4_0_4_line_7 |  | 6 | 13 | 0.05054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4012-4_0_4_line_8 |  | 6 | 12 | 0.039792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4012-4_0_4_line_9 |  | 7 | 72 | 0.054842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4012-4_0_4_line_10 |  | 8 | 51 | 0.027528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4012-4_0_4_line_11 |  | 8 | 80 | 0.02081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4012-4_0_4_line_12 |  | 9 | 10 | 0.0079639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4012-4_0_4_line_13 |  | 9 | 11 | 0.0096084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4012-4_0_4_line_14 |  | 10 | 20 | 0.024852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4012-4_0_4_line_15 |  | 11 | 13 | 0.020883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4012-4_0_4_line_16 |  | 14 | 15 | 0.039331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4012-4_0_4_line_17 |  | 14 | 16 | 0.031839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4012-4_0_4_line_18 |  | 15 | 17 | 0.011049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_4012-4_0_4_line_19 |  | 15 | 18 | 0.03312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_4012-4_0_4_line_20 |  | 16 | 19 | 0.015243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4012-4_0_4_line_21 |  | 17 | 20 | 0.017009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4012-4_0_4_line_22 |  | 17 | 21 | 0.05266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4012-4_0_4_line_23 |  | 17 | 22 | 0.019035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4012-4_0_4_line_24 |  | 18 | 23 | 0.020764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_4012-4_0_4_line_25 |  | 19 | 24 | 0.018813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4012-4_0_4_line_26 |  | 20 | 27 | 0.0071777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4012-4_0_4_line_27 |  | 21 | 28 | 0.027202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4012-4_0_4_line_28 |  | 22 | 29 | 0.051249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4012-4_0_4_line_29 |  | 23 | 30 | 0.030695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4012-4_0_4_line_30 |  | 23 | 31 | 0.0089662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_4012-4_0_4_line_31 |  | 24 | 32 | 0.031549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4012-4_0_4_line_32 |  | 25 | 26 | 0.018141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4012-4_0_4_line_33 |  | 26 | 30 | 0.0049028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4012-4_0_4_line_34 |  | 27 | 51 | 0.019957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4012-4_0_4_line_35 |  | 28 | 52 | 0.018251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4012-4_0_4_line_36 |  | 29 | 50 | 0.033671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4012-4_0_4_line_37 |  | 31 | 36 | 0.0047994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_4012-4_0_4_line_38 |  | 32 | 70 | 0.027075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4012-4_0_4_line_39 |  | 33 | 34 | 0.020617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4012-4_0_4_line_40 |  | 33 | 35 | 0.014357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4012-4_0_4_line_41 |  | 35 | 36 | 0.034346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4012-4_0_4_line_42 |  | 35 | 37 | 0.013849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4012-4_0_4_line_43 |  | 36 | 38 | 0.019188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4012-4_0_4_line_44 |  | 37 | 39 | 0.0052206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4012-4_0_4_line_45 |  | 38 | 40 | 0.015911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4012-4_0_4_line_46 |  | 39 | 41 | 0.0054897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4012-4_0_4_line_47 |  | 40 | 55 | 0.015761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4012-4_0_4_line_48 |  | 40 | 56 | 0.029407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4012-4_0_4_line_49 |  | 42 | 43 | 0.00075136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4012-4_0_4_line_50 |  | 42 | 44 | 0.013475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4012-4_0_4_line_51 |  | 43 | 45 | 0.018776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4012-4_0_4_line_52 |  | 45 | 46 | 0.028785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4012-4_0_4_line_53 |  | 46 | 47 | 0.081102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4012-4_0_4_line_54 |  | 47 | 53 | 0.029223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4012-4_0_4_line_55 |  | 47 | 54 | 0.016068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4012-4_0_4_line_56 |  | 48 | 49 | 0.048598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4012-4_0_4_line_57 |  | 48 | 50 | 0.024451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4012-4_0_4_line_58 |  | 52 | 73 | 0.0052116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4012-4_0_4_line_59 |  | 53 | 59 | 0.034085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4012-4_0_4_line_60 |  | 53 | 60 | 0.084372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4012-4_0_4_line_61 |  | 53 | 61 | 0.014689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4012-4_0_4_line_62 |  | 54 | 57 | 0.019946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4012-4_0_4_line_63 |  | 54 | 55 | 0.006502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4012-4_0_4_line_64 |  | 57 | 58 | 0.0018488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4012-4_0_4_line_65 |  | 58 | 62 | 0.037177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4012-4_0_4_line_66 |  | 59 | 63 | 0.0058649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4012-4_0_4_line_67 |  | 60 | 64 | 0.0068691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4012-4_0_4_line_68 |  | 61 | 65 | 0.040108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4012-4_0_4_line_69 |  | 62 | 83 | 0.0040342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4012-4_0_4_line_70 |  | 65 | 85 | 0.023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4012-4_0_4_line_71 |  | 66 | 67 | 0.015525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4012-4_0_4_line_72 |  | 67 | 68 | 0.017424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4012-4_0_4_line_73 |  | 68 | 69 | 0.015924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4012-4_0_4_line_74 |  | 69 | 73 | 0.013438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4012-4_0_4_line_75 |  | 70 | 71 | 0.036416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4012-4_0_4_line_76 |  | 71 | 74 | 0.019584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4012-4_0_4_line_77 |  | 72 | 79 | 0.0077062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4012-4_0_4_line_78 |  | 73 | 78 | 0.0084512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4012-4_0_4_line_79 |  | 75 | 76 | 0.021156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4012-4_0_4_line_80 |  | 76 | 81 | 0.0025414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4012-4_0_4_line_81 |  | 77 | 78 | 0.022014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4012-4_0_4_line_82 |  | 81 | 82 | 0.018428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4012-4_0_4_line_83 |  | 82 | 84 | 0.0063745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4012-4_0_4_line_84 |  | 83 | 84 | 0.032807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4012-4_0_4_trafo_6 | 0.63 MVA 20/0.4 kV | 86 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2648134.4976 | 1247107.6647 | 2648118.197 | 1247110.0535
1 | 2648134.4976 | 1247107.6647 | 2648155.6256 | 1247098.0852 | 2648156.5925 | 1247097.5925
2 | 2648168.0046 | 1247093.4826 | 2648161.7462 | 1247094.9661 | 2648156.5925 | 1247097.5925
3 | 2648213.0228 | 1247217.7093 | 2648212.9763 | 1247215.0738 | 2648214.7506 | 1247204.9258
4 | 2648214.7506 | 1247204.9258 | 2648217.3707 | 1247194.807
5 | 2648213.0228 | 1247217.7093 | 2648212.7984 | 1247221.1542 | 2648209.7571 | 1247235.717 | 2648208.0611 | 1247247.3777 | 2648209.9668 | 1247259.1567 | 2648216.9294 | 1247269.5091 | 2648233.2504 | 1247279.8042 | 2648244.4423 | 1247284.6095 | 2648249.1532 | 1247286.7159
6 | 2648225.7507 | 1247177.608 | 2648217.3707 | 1247194.807
7 | 2648168.0046 | 1247093.4826 | 2648172.4417 | 1247086.5473 | 2648178.1092 | 1247080.6338 | 2648185.4457 | 1247079.4036 | 2648192.2637 | 1247083.4172 | 2648201.3741 | 1247099.8224
8 | 2648168.0046 | 1247093.4826 | 2648174.0316 | 1247129.7892 | 2648173.4485 | 1247132.72
9 | 2648249.1532 | 1247286.7159 | 2648251.8967 | 1247272.5731 | 2648254.3261 | 1247260.8183 | 2648265.2714 | 1247234.577
10 | 2648225.7507 | 1247177.608 | 2648233.5702 | 1247162.4836 | 2648237.3032 | 1247152.6679
11 | 2648225.7507 | 1247177.608 | 2648234.4216 | 1247181.3143 | 2648244.925 | 1247185.695
12 | 2648212.5608 | 1247127.7563 | 2648220.456 | 1247126.7124
13 | 2648212.5608 | 1247127.7563 | 2648209.7623 | 1247124.5203 | 2648207.3594 | 1247119.7625
14 | 2648245.281 | 1247126.7437 | 2648223.1766 | 1247126.3527 | 2648220.456 | 1247126.7124
15 | 2648201.3741 | 1247099.8224 | 2648201.4869 | 1247100.0255 | 2648205.9564 | 1247116.9843 | 2648207.3594 | 1247119.7625
16 | 2648265.0442 | 1247107.625 | 2648273.7696 | 1247115.7681 | 2648282.3185 | 1247122.3976 | 2648295.5654 | 1247132.3646
17 | 2648324.364 | 1247145.8111 | 2648317.5212 | 1247143.0091 | 2648297.3024 | 1247133.6716 | 2648295.5654 | 1247132.3646
18 | 2648255.8697 | 1247113.8212 | 2648265.0442 | 1247107.625
19 | 2648265.0442 | 1247107.625 | 2648273.0239 | 1247101.5969 | 2648285.5658 | 1247089.9912 | 2648289.3501 | 1247085.2949
20 | 2648324.364 | 1247145.8111 | 2648330.6272 | 1247148.375 | 2648338.536 | 1247151.4231
21 | 2648255.8697 | 1247113.8212 | 2648250.0773 | 1247118.366 | 2648248.4795 | 1247120.7324 | 2648245.281 | 1247126.7437
22 | 2648255.8697 | 1247113.8212 | 2648265.3773 | 1247120.5141 | 2648277.3872 | 1247131.5748 | 2648285.8334 | 1247143.3959 | 2648290.8831 | 1247152.2318
23 | 2648255.8697 | 1247113.8212 | 2648245.5103 | 1247105.0533 | 2648240.7729 | 1247102.3322
24 | 2648301.9922 | 1247068.8329 | 2648296.8966 | 1247075.9295 | 2648289.3501 | 1247085.2949
25 | 2648356.0904 | 1247158.1888 | 2648338.536 | 1247151.4231
26 | 2648245.281 | 1247126.7437 | 2648243.2529 | 1247133.6289
27 | 2648290.8831 | 1247152.2318 | 2648292.9004 | 1247155.7617 | 2648297.6391 | 1247167.4525 | 2648298.0982 | 1247168.5792 | 2648302.7578 | 1247176.634
28 | 2648201.4438 | 1247069.8515 | 2648210.661 | 1247079.0082 | 2648230.234 | 1247096.2788 | 2648240.7729 | 1247102.3322
29 | 2648301.9922 | 1247068.8329 | 2648324.8655 | 1247089.3028
30 | 2648301.9922 | 1247068.8329 | 2648307.2173 | 1247061.5465
31 | 2648385.5283 | 1247169.5346 | 2648356.0904 | 1247158.1888
32 | 2648328.5189 | 1247092.5723 | 2648337.2496 | 1247100.3856 | 2648339.8376 | 1247106.2662 | 2648339.8376 | 1247106.2662
33 | 2648324.8655 | 1247089.3028 | 2648328.5189 | 1247092.5723
34 | 2648243.2529 | 1247133.6289 | 2648238.8184 | 1247148.6837 | 2648237.3032 | 1247152.6679
35 | 2648311.8966 | 1247192.4318 | 2648302.7578 | 1247176.634
36 | 2648172.8366 | 1247053.2078 | 2648185.6712 | 1247057.2239 | 2648199.512 | 1247067.9324 | 2648201.4438 | 1247069.8515
37 | 2648310.0141 | 1247057.6463 | 2648307.2173 | 1247061.5465
38 | 2648410.7914 | 1247179.2713 | 2648385.5283 | 1247169.5346
39 | 2648275.1136 | 1247023.6053 | 2648269.1228 | 1247017.6089 | 2648261.0229 | 1247026.6521
40 | 2648285.2607 | 1247033.7621 | 2648275.1136 | 1247023.6053
41 | 2648285.2607 | 1247033.7621 | 2648310.0141 | 1247057.6463
42 | 2648285.2607 | 1247033.7621 | 2648275.8038 | 1247043.8799
43 | 2648310.0141 | 1247057.6463 | 2648322.3973 | 1247042.9887
44 | 2648272.2389 | 1247047.6939 | 2648275.8038 | 1247043.8799
45 | 2648332.6653 | 1247030.835 | 2648322.3973 | 1247042.9887
46 | 2648268.4903 | 1247051.7044 | 2648272.2389 | 1247047.6939
47 | 2648332.6653 | 1247030.835 | 2648343.5117 | 1247019.3998
48 | 2648332.6653 | 1247030.835 | 2648311.3873 | 1247010.537
49 | 2648252.2965 | 1246979.1475 | 2648252.4893 | 1246978.4213
50 | 2648248.8381 | 1246992.1713 | 2648252.2965 | 1246979.1475
51 | 2648257.308 | 1246960.2744 | 2648252.4893 | 1246978.4213
52 | 2648257.308 | 1246960.2744 | 2648285.0967 | 1246967.7811
53 | 2648357.4731 | 1247001.6953 | 2648343.4415 | 1246990.3178 | 2648331.0742 | 1246982.3228 | 2648316.2971 | 1246976.2095 | 2648285.0967 | 1246967.7811
54 | 2648357.4731 | 1247001.6953 | 2648362.504 | 1246995.1541 | 2648364.9186 | 1246990.8265 | 2648369.9923 | 1246979.0266 | 2648370.8331 | 1246975.9536
55 | 2648357.4731 | 1247001.6953 | 2648347.9863 | 1247014.6823
56 | 2648148.8358 | 1247048.7304 | 2648151.4687 | 1247034.2309 | 2648153.1762 | 1247026.7286 | 2648158.741 | 1247020.4473 | 2648165.8214 | 1247018.2033 | 2648171.1919 | 1247020.037 | 2648173.8339 | 1247023.95
57 | 2648148.8358 | 1247048.7304 | 2648168.8178 | 1247051.9502 | 2648172.8366 | 1247053.2078
58 | 2648314.5063 | 1247196.9429 | 2648311.8966 | 1247192.4318
59 | 2648375.7146 | 1246942.3598 | 2648373.836 | 1246965.2487 | 2648370.8331 | 1246975.9536
60 | 2648370.8331 | 1246975.9536 | 2648383.3648 | 1246986.952 | 2648417.8497 | 1247018.7546 | 2648423.2318 | 1247017.3087 | 2648424.2754 | 1247018.0844 | 2648435.4543 | 1247026.37
61 | 2648370.8331 | 1246975.9536 | 2648357.7219 | 1246969.3312 | 2648357.7219 | 1246969.3312
62 | 2648347.9863 | 1247014.6823 | 2648353.7472 | 1247019.5658 | 2648363.3469 | 1247027.4049
63 | 2648347.9863 | 1247014.6823 | 2648343.5117 | 1247019.3998
64 | 2648363.3469 | 1247027.4049 | 2648364.7789 | 1247028.5743
65 | 2648364.7789 | 1247028.5743 | 2648365.8498 | 1247029.4488 | 2648380.7122 | 1247041.7449 | 2648392.4394 | 1247053.3589
66 | 2648375.7146 | 1246942.3598 | 2648376.1939 | 1246936.5145
67 | 2648435.4543 | 1247026.37 | 2648440.5736 | 1247030.9501
68 | 2648319.5363 | 1246957.0639 | 2648357.7219 | 1246969.3312
69 | 2648395.3058 | 1247056.1977 | 2648392.4394 | 1247053.3589
70 | 2648296.9502 | 1246949.808 | 2648319.5363 | 1246957.0639
71 | 2648371.4893 | 1247222.1512 | 2648357.2917 | 1247215.8704
72 | 2648357.2917 | 1247215.8704 | 2648341.3574 | 1247208.8214
73 | 2648326.7951 | 1247202.3793 | 2648341.3574 | 1247208.8214
74 | 2648314.5063 | 1247196.9429 | 2648326.7951 | 1247202.3793
75 | 2648413.3734 | 1247143.3239 | 2648409.7986 | 1247157.482 | 2648410.7914 | 1247179.2713
76 | 2648413.3734 | 1247143.3239 | 2648394.8631 | 1247136.9273
77 | 2648268.238 | 1247227.4647 | 2648265.2714 | 1247234.577
78 | 2648314.5063 | 1247196.9429 | 2648318.5336 | 1247204.3729
79 | 2648435.3507 | 1247101.0193 | 2648444.4251 | 1247111.7116 | 2648450.3991 | 1247115.6081
80 | 2648435.3507 | 1247101.0193 | 2648433.7058 | 1247099.0819
81 | 2648328.1152 | 1247224.17 | 2648323.3685 | 1247213.2927 | 2648318.5336 | 1247204.3729
82 | 2648433.7058 | 1247099.0819 | 2648421.7792 | 1247085.0342
83 | 2648421.7792 | 1247085.0342 | 2648417.6535 | 1247080.1748
84 | 2648395.3058 | 1247056.1977 | 2648407.8127 | 1247068.5839 | 2648417.6535 | 1247080.1748

## bus_geodata
| x | y | coords
0 | 2648118.197 | 1247110.0535
1 | 2648134.4976 | 1247107.6647
2 | 2648156.5925 | 1247097.5925
3 | 2648214.7506 | 1247204.9258
4 | 2648213.0228 | 1247217.7093
5 | 2648217.3707 | 1247194.807
6 | 2648168.0046 | 1247093.4826
7 | 2648249.1532 | 1247286.7159
8 | 2648225.7507 | 1247177.608
9 | 2648212.5608 | 1247127.7563
10 | 2648220.456 | 1247126.7124
11 | 2648207.3594 | 1247119.7625
12 | 2648173.4485 | 1247132.72
13 | 2648201.3741 | 1247099.8224
14 | 2648295.5654 | 1247132.3646
15 | 2648265.0442 | 1247107.625
16 | 2648324.364 | 1247145.8111
17 | 2648255.8697 | 1247113.8212
18 | 2648289.3501 | 1247085.2949
19 | 2648338.536 | 1247151.4231
20 | 2648245.281 | 1247126.7437
21 | 2648290.8831 | 1247152.2318
22 | 2648240.7729 | 1247102.3322
23 | 2648301.9922 | 1247068.8329
24 | 2648356.0904 | 1247158.1888
25 | 2648339.8376 | 1247106.2662
26 | 2648328.5189 | 1247092.5723
27 | 2648243.2529 | 1247133.6289
28 | 2648302.7578 | 1247176.634
29 | 2648201.4438 | 1247069.8515
30 | 2648324.8655 | 1247089.3028
31 | 2648307.2173 | 1247061.5465
32 | 2648385.5283 | 1247169.5346
33 | 2648275.1136 | 1247023.6053
34 | 2648261.0229 | 1247026.6521
35 | 2648285.2607 | 1247033.7621
36 | 2648310.0141 | 1247057.6463
37 | 2648275.8038 | 1247043.8799
38 | 2648322.3973 | 1247042.9887
39 | 2648272.2389 | 1247047.6939
40 | 2648332.6653 | 1247030.835
41 | 2648268.4903 | 1247051.7044
42 | 2648252.2965 | 1246979.1475
43 | 2648252.4893 | 1246978.4213
44 | 2648248.8381 | 1246992.1713
45 | 2648257.308 | 1246960.2744
46 | 2648285.0967 | 1246967.7811
47 | 2648357.4731 | 1247001.6953
48 | 2648148.8358 | 1247048.7304
49 | 2648173.8339 | 1247023.95
50 | 2648172.8366 | 1247053.2078
51 | 2648237.3032 | 1247152.6679
52 | 2648311.8966 | 1247192.4318
53 | 2648370.8331 | 1246975.9536
54 | 2648347.9863 | 1247014.6823
55 | 2648343.5117 | 1247019.3998
56 | 2648311.3873 | 1247010.537
57 | 2648363.3469 | 1247027.4049
58 | 2648364.7789 | 1247028.5743
59 | 2648375.7146 | 1246942.3598
60 | 2648435.4543 | 1247026.37
61 | 2648357.7219 | 1246969.3312
62 | 2648392.4394 | 1247053.3589
63 | 2648376.1939 | 1246936.5145
64 | 2648440.5736 | 1247030.9501
65 | 2648319.5363 | 1246957.0639
66 | 2648371.4893 | 1247222.1512
67 | 2648357.2917 | 1247215.8704
68 | 2648341.3574 | 1247208.8214
69 | 2648326.7951 | 1247202.3793
70 | 2648410.7914 | 1247179.2713
71 | 2648413.3734 | 1247143.3239
72 | 2648265.2714 | 1247234.577
73 | 2648314.5063 | 1247196.9429
74 | 2648394.8631 | 1247136.9273
75 | 2648450.3991 | 1247115.6081
76 | 2648435.3507 | 1247101.0193
77 | 2648328.1152 | 1247224.17
78 | 2648318.5336 | 1247204.3729
79 | 2648268.238 | 1247227.4647
80 | 2648244.925 | 1247185.695
81 | 2648433.7058 | 1247099.0819
82 | 2648421.7792 | 1247085.0342
83 | 2648395.3058 | 1247056.1977
84 | 2648417.6535 | 1247080.1748
85 | 2648296.9502 | 1246949.808
86 | 2648324.364 | 1247145.8111

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1