## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4012-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4012-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4012-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4012-9_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4012-9_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4012-9_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_4012-9_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_4012-9_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_4012-9_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_4012-9_0_4_node_101 | 0.4 | n |  | TRUE
10 | bus_LV_4012-9_0_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_4012-9_0_4_node_24 | 0.4 | n |  | TRUE
12 | bus_LV_4012-9_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_4012-9_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_4012-9_0_4_node_93 | 0.4 | n |  | TRUE
15 | bus_LV_4012-9_0_4_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_4012-9_0_4_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_4012-9_0_4_node_95 | 0.4 | n |  | TRUE
18 | bus_LV_4012-9_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_4012-9_0_4_node_97 | 0.4 | n |  | TRUE
20 | bus_LV_4012-9_0_4_node_100 | 0.4 | n |  | TRUE
21 | bus_LV_4012-9_0_4_node_91 | 0.4 | n |  | TRUE
22 | bus_LV_4012-9_0_4_node_103 | 0.4 | n |  | TRUE
23 | bus_LV_4012-9_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_4012-9_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_4012-9_0_4_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_4012-9_0_4_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_4012-9_0_4_node_61 | 0.4 | n |  | TRUE
28 | bus_LV_4012-9_0_4_node_102 | 0.4 | n |  | TRUE
29 | bus_LV_4012-9_0_4_node_59 | 0.4 | n |  | TRUE
30 | bus_LV_4012-9_0_4_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_4012-9_0_4_node_58 | 0.4 | n |  | TRUE
32 | bus_LV_4012-9_0_4_node_64 | 0.4 | n |  | TRUE
33 | bus_LV_4012-9_0_4_node_88 | 0.4 | n |  | TRUE
34 | bus_LV_4012-9_0_4_node_80 | 0.4 | n |  | TRUE
35 | bus_LV_4012-9_0_4_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_4012-9_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_4012-9_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_4012-9_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_4012-9_0_4_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_4012-9_0_4_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_4012-9_0_4_node_57 | 0.4 | n |  | TRUE
42 | bus_LV_4012-9_0_4_node_22 | 0.4 | n |  | TRUE
43 | bus_LV_4012-9_0_4_node_23 | 0.4 | n |  | TRUE
44 | bus_LV_4012-9_0_4_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_4012-9_0_4_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_4012-9_0_4_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_4012-9_0_4_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_4012-9_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_4012-9_0_4_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_4012-9_0_4_node_99 | 0.4 | n |  | TRUE
51 | bus_LV_4012-9_0_4_node_34 | 0.4 | n |  | TRUE
52 | bus_LV_4012-9_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_4012-9_0_4_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_4012-9_0_4_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_4012-9_0_4_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_4012-9_0_4_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_4012-9_0_4_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_4012-9_0_4_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_4012-9_0_4_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_4012-9_0_4_node_39 | 0.4 | n |  | TRUE
61 | bus_LV_4012-9_0_4_node_40 | 0.4 | n |  | TRUE
62 | bus_LV_4012-9_0_4_node_96 | 0.4 | n |  | TRUE
63 | bus_LV_4012-9_0_4_node_87 | 0.4 | n |  | TRUE
64 | bus_LV_4012-9_0_4_node_85 | 0.4 | n |  | TRUE
65 | bus_LV_4012-9_0_4_node_98 | 0.4 | n |  | TRUE
66 | bus_LV_4012-9_0_4_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_4012-9_0_4_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_4012-9_0_4_node_47 | 0.4 | n |  | TRUE
69 | bus_LV_4012-9_0_4_node_48 | 0.4 | n |  | TRUE
70 | bus_LV_4012-9_0_4_node_53 | 0.4 | n |  | TRUE
71 | bus_LV_4012-9_0_4_node_55 | 0.4 | n |  | TRUE
72 | bus_LV_4012-9_0_4_node_51 | 0.4 | n |  | TRUE
73 | bus_LV_4012-9_0_4_node_52 | 0.4 | n |  | TRUE
74 | bus_LV_4012-9_0_4_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_4012-9_0_4_node_68 | 0.4 | n |  | TRUE
76 | bus_LV_4012-9_0_4_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_4012-9_0_4_node_77 | 0.4 | n |  | TRUE
78 | bus_LV_4012-9_0_4_node_75 | 0.4 | n |  | TRUE
79 | bus_LV_4012-9_0_4_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_4012-9_0_4_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_4012-9_0_4_node_67 | 0.4 | n |  | TRUE
82 | bus_LV_4012-9_0_4_node_69 | 0.4 | n |  | TRUE
83 | bus_LV_4012-9_0_4_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_4012-9_0_4_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_4012-9_0_4_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_4012-9_0_4_node_73 | 0.4 | n |  | TRUE
87 | bus_LV_4012-9_0_4_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_4012-9_0_4_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_4012-9_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_4012-9_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_4012-9_0_4_node_83 | 0.4 | n |  | TRUE
92 | bus_LV_4012-9_0_4_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_4012-9_0_4_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_4012-9_0_4_node_86 | 0.4 | n |  | TRUE
95 | bus_LV_4012-9_0_4_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_4012-9_0_4_node_94 | 0.4 | n |  | TRUE
97 | bus_MV_418_1_node_212 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4012-9_0_4_load_0 | 0 | 0.014163 | 0.0035495 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4012-9_0_4_load_1 | 1 | 0.018197 | 0.0045606 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4012-9_0_4_load_3 | 3 | 0.00098341 | 0.00024647 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4012-9_0_4_load_12 | 8 | 0.019853 | 0.0049755 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4012-9_0_4_load_101 | 9 | 0.0024676 | 0.00061844 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4012-9_0_4_load_25 | 10 | 0.0038098 | 0.00095484 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4012-9_0_4_load_24 | 11 | 0.0035631 | 0.00089299 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4012-9_0_4_load_93 | 14 | 0.014331 | 0.0035917 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4012-9_0_4_load_95 | 17 | 0.0066796 | 0.0016741 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4012-9_0_4_load_100 | 20 | 0.0011631 | 0.00029151 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4012-9_0_4_load_91 | 21 | 0.001485 | 0.00037219 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4012-9_0_4_load_103 | 22 | 0.013196 | 0.0033072 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4012-9_0_4_load_102 | 28 | 0.0078532 | 0.0019682 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4012-9_0_4_load_58 | 31 | 0.032826 | 0.008227 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4012-9_0_4_load_64 | 32 | 0.012705 | 0.0031843 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4012-9_0_4_load_88 | 33 | 0.003587 | 0.00089899 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4012-9_0_4_load_80 | 34 | 0.0029038 | 0.00072776 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4012-9_0_4_load_26 | 37 | 0.0041481 | 0.0010396 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4012-9_0_4_load_17 | 38 | 0.0096136 | 0.0024094 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4012-9_0_4_load_57 | 41 | 0.095499 | 0.023934 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4012-9_0_4_load_31 | 44 | 0.002423 | 0.00060726 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4012-9_0_4_load_49 | 46 | 0.0018482 | 0.00046321 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4012-9_0_4_load_33 | 49 | 0.069917 | 0.017523 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4012-9_0_4_load_99 | 50 | 0.011494 | 0.0028806 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4012-9_0_4_load_34 | 51 | 0.0023138 | 0.00057989 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4012-9_0_4_load_35 | 52 | 0.0029793 | 0.00074669 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4012-9_0_4_load_36 | 53 | 0.0024196 | 0.0006064 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4012-9_0_4_load_37 | 54 | 0.0021218 | 0.00053176 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4012-9_0_4_load_50 | 56 | 0.0039738 | 0.00099592 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4012-9_0_4_load_56 | 58 | 0.0046943 | 0.0011765 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4012-9_0_4_load_43 | 59 | 0.0029952 | 0.00075066 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4012-9_0_4_load_39 | 60 | 0.0018937 | 0.00047462 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4012-9_0_4_load_40 | 61 | 0.0029302 | 0.00073438 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4012-9_0_4_load_96 | 62 | 0.0030425 | 0.00076253 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4012-9_0_4_load_87 | 63 | 0.0024607 | 0.00061671 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4012-9_0_4_load_85 | 64 | 0.0043716 | 0.0010956 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4012-9_0_4_load_45 | 66 | 0.0012244 | 0.00030685 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4012-9_0_4_load_46 | 67 | 0.001223 | 0.00030651 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4012-9_0_4_load_47 | 68 | 0.0019511 | 0.00048899 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4012-9_0_4_load_55 | 71 | 0.0016473 | 0.00041285 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4012-9_0_4_load_51 | 72 | 0.0096272 | 0.0024128 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4012-9_0_4_load_52 | 73 | 0.017986 | 0.0045078 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4012-9_0_4_load_68 | 75 | 0.019033 | 0.0047702 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4012-9_0_4_load_65 | 76 | 0.0046747 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4012-9_0_4_load_77 | 77 | 0.0014126 | 0.00035402 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4012-9_0_4_load_66 | 79 | 0.0017315 | 0.00043395 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4012-9_0_4_load_76 | 80 | 0.0015922 | 0.00039904 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4012-9_0_4_load_67 | 81 | 0.0010567 | 0.00026485 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4012-9_0_4_load_69 | 82 | 0.0018382 | 0.0004607 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4012-9_0_4_load_70 | 83 | 0.00086731 | 0.00021737 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4012-9_0_4_load_72 | 85 | 0.0011969 | 0.00029997 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4012-9_0_4_load_73 | 86 | 0.00083101 | 0.00020827 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4012-9_0_4_load_78 | 87 | 0.0059746 | 0.0014974 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4012-9_0_4_load_79 | 88 | 0.0029545 | 0.00074047 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4012-9_0_4_load_81 | 89 | 0.0038314 | 0.00096024 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4012-9_0_4_load_82 | 90 | 0.0038504 | 0.000965 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4012-9_0_4_load_83 | 91 | 0.0078074 | 0.0019567 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4012-9_0_4_load_89 | 93 | 0.0069464 | 0.0017409 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4012-9_0_4_load_86 | 94 | 0.0024442 | 0.00061257 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4012-9_0_4_load_92 | 95 | 0.0038019 | 0.00095283 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4012-9_0_4_load_94 | 96 | 0.0058033 | 0.0014544 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4012-9_0_4_line_0 |  | 0 | 1 | 0.041917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4012-9_0_4_line_1 |  | 1 | 2 | 0.031897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4012-9_0_4_line_2 |  | 2 | 3 | 0.010714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4012-9_0_4_line_3 |  | 2 | 4 | 0.042089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4012-9_0_4_line_4 |  | 3 | 5 | 0.016739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4012-9_0_4_line_5 |  | 4 | 6 | 0.072343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4012-9_0_4_line_6 |  | 4 | 7 | 0.067357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4012-9_0_4_line_7 |  | 4 | 8 | 0.049374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4012-9_0_4_line_8 |  | 5 | 15 | 0.068731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4012-9_0_4_line_9 |  | 6 | 9 | 0.010764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4012-9_0_4_line_10 |  | 7 | 10 | 0.01613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4012-9_0_4_line_11 |  | 7 | 11 | 0.01504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4012-9_0_4_line_12 |  | 9 | 19 | 0.027976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4012-9_0_4_line_13 |  | 12 | 13 | 0.099517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4012-9_0_4_line_14 |  | 12 | 14 | 0.020691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4012-9_0_4_line_15 |  | 13 | 16 | 0.11815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_4012-9_0_4_line_16 |  | 13 | 17 | 0.0064147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_4012-9_0_4_line_17 |  | 14 | 21 | 0.021406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4012-9_0_4_line_18 |  | 15 | 22 | 0.0081769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4012-9_0_4_line_19 |  | 15 | 23 | 0.007084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4012-9_0_4_line_20 |  | 16 | 22 | 0.054142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4012-9_0_4_line_21 |  | 16 | 24 | 0.062753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_4012-9_0_4_line_22 |  | 17 | 25 | 0.013868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_4012-9_0_4_line_23 |  | 18 | 19 | 0.038456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4012-9_0_4_line_24 |  | 18 | 20 | 0.019324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4012-9_0_4_line_25 |  | 21 | 95 | 0.0037612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4012-9_0_4_line_26 |  | 23 | 26 | 0.024969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4012-9_0_4_line_27 |  | 24 | 40 | 0.013946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4012-9_0_4_line_28 |  | 24 | 38 | 0.018961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_4012-9_0_4_line_29 |  | 25 | 62 | 0.041264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4012-9_0_4_line_30 |  | 25 | 61 | 0.0068698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_4012-9_0_4_line_31 |  | 26 | 27 | 0.089061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4012-9_0_4_line_32 |  | 26 | 28 | 0.073071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4012-9_0_4_line_33 |  | 27 | 32 | 0.026787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4012-9_0_4_line_34 |  | 29 | 30 | 0.044258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4012-9_0_4_line_35 |  | 29 | 31 | 0.0034455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4012-9_0_4_line_36 |  | 30 | 32 | 0.02266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4012-9_0_4_line_37 |  | 33 | 34 | 0.023151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4012-9_0_4_line_38 |  | 34 | 88 | 0.022097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4012-9_0_4_line_39 |  | 35 | 36 | 0.068559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4012-9_0_4_line_40 |  | 35 | 37 | 0.02424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4012-9_0_4_line_41 |  | 36 | 45 | 0.039247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4012-9_0_4_line_42 |  | 36 | 46 | 0.015644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4012-9_0_4_line_43 |  | 38 | 39 | 0.015031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_4012-9_0_4_line_44 |  | 40 | 41 | 0.014134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4012-9_0_4_line_45 |  | 41 | 43 | 0.0053081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4012-9_0_4_line_46 |  | 42 | 43 | 0.032371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4012-9_0_4_line_47 |  | 42 | 44 | 0.0085175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4012-9_0_4_line_48 |  | 44 | 45 | 0.015609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4012-9_0_4_line_49 |  | 47 | 48 | 0.032818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_4012-9_0_4_line_50 |  | 47 | 49 | 0.082394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_4012-9_0_4_line_51 |  | 48 | 50 | 0.022525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_4012-9_0_4_line_52 |  | 50 | 65 | 0.060681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_4012-9_0_4_line_53 |  | 51 | 52 | 0.022563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4012-9_0_4_line_54 |  | 51 | 53 | 0.0011163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4012-9_0_4_line_55 |  | 52 | 54 | 0.014706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4012-9_0_4_line_56 |  | 53 | 55 | 0.014511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4012-9_0_4_line_57 |  | 55 | 56 | 0.0044992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_4012-9_0_4_line_58 |  | 55 | 57 | 0.030447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_4012-9_0_4_line_59 |  | 56 | 58 | 0.024032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_4012-9_0_4_line_60 |  | 57 | 59 | 0.015303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4012-9_0_4_line_61 |  | 57 | 60 | 0.0036616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_4012-9_0_4_line_62 |  | 58 | 69 | 0.023511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_4012-9_0_4_line_63 |  | 59 | 63 | 0.015273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4012-9_0_4_line_64 |  | 60 | 61 | 0.012102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_4012-9_0_4_line_65 |  | 63 | 64 | 0.0076757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4012-9_0_4_line_66 |  | 64 | 94 | 0.010199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4012-9_0_4_line_67 |  | 65 | 78 | 0.001727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_4012-9_0_4_line_68 |  | 66 | 67 | 0.019313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4012-9_0_4_line_69 |  | 66 | 68 | 0.0027844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4012-9_0_4_line_70 |  | 67 | 69 | 0.017041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4012-9_0_4_line_71 |  | 69 | 70 | 0.005107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_4012-9_0_4_line_72 |  | 70 | 71 | 0.029692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4012-9_0_4_line_73 |  | 70 | 72 | 0.018047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_4012-9_0_4_line_74 |  | 71 | 77 | 0.015894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4012-9_0_4_line_75 |  | 72 | 73 | 0.033719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_4012-9_0_4_line_76 |  | 73 | 74 | 0.023061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_4012-9_0_4_line_77 |  | 74 | 75 | 0.0084763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_4012-9_0_4_line_78 |  | 74 | 76 | 0.019131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4012-9_0_4_line_79 |  | 75 | 78 | 0.064723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_4012-9_0_4_line_80 |  | 76 | 79 | 0.0038509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4012-9_0_4_line_81 |  | 77 | 80 | 0.0071165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4012-9_0_4_line_82 |  | 79 | 81 | 0.011642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4012-9_0_4_line_83 |  | 80 | 85 | 0.018311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4012-9_0_4_line_84 |  | 82 | 83 | 0.016316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4012-9_0_4_line_85 |  | 82 | 84 | 0.019301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4012-9_0_4_line_86 |  | 83 | 85 | 0.0088026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4012-9_0_4_line_87 |  | 84 | 86 | 0.017387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4012-9_0_4_line_88 |  | 86 | 87 | 0.029302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4012-9_0_4_line_89 |  | 87 | 88 | 0.025718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4012-9_0_4_line_90 |  | 89 | 90 | 0.0009612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4012-9_0_4_line_91 |  | 89 | 91 | 0.014457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4012-9_0_4_line_92 |  | 90 | 92 | 0.028064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4012-9_0_4_line_93 |  | 92 | 93 | 0.007642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4012-9_0_4_line_94 |  | 92 | 94 | 0.0052318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4012-9_0_4_line_95 |  | 95 | 96 | 0.014194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4012-9_0_4_trafo_19 | 0.63 MVA 20/0.4 kV | 97 | 39 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2648391.7318 | 1246855.3011 | 2648394.4177 | 1246850.5619 | 2648394.6944 | 1246834.2421 | 2648395.4532 | 1246831.0461 | 2648394.0352 | 1246814.2428
1 | 2648390.0021 | 1246782.6137 | 2648392.7735 | 1246801.2154 | 2648393.3181 | 1246805.7451 | 2648394.0352 | 1246814.2428
2 | 2648390.0021 | 1246782.6137 | 2648388.3278 | 1246772.0314
3 | 2648390.0021 | 1246782.6137 | 2648396.1167 | 1246780.2842 | 2648401.9702 | 1246777.5523 | 2648405.486 | 1246774.3566 | 2648410.1557 | 1246776.0069 | 2648415.1951 | 1246776.7708 | 2648421.2637 | 1246776.3867 | 2648425.7271 | 1246775.5448 | 2648429.1444 | 1246774.2273
4 | 2648391.4092 | 1246756.4298 | 2648387.1504 | 1246764.5894 | 2648388.3278 | 1246772.0314
5 | 2648429.1444 | 1246774.2273 | 2648431.6428 | 1246777.2275 | 2648435.8784 | 1246782.0876 | 2648438.3359 | 1246784.5315 | 2648437.1606 | 1246786.0118 | 2648436.6094 | 1246790.6103 | 2648445.6523 | 1246799.6791 | 2648448.3767 | 1246800.8911 | 2648453.5084 | 1246804.2352 | 2648455.8698 | 1246806.4337 | 2648456.8921 | 1246810.7338 | 2648471.3297 | 1246827.9188
6 | 2648429.1444 | 1246774.2273 | 2648431.6428 | 1246777.2275 | 2648435.8784 | 1246782.0876 | 2648438.3359 | 1246784.5315 | 2648447.4004 | 1246775.2437 | 2648456.46 | 1246765.6223 | 2648461.4188 | 1246760.5483 | 2648461.4341 | 1246760.5262 | 2648467.3069 | 1246754.5146 | 2648476.0808 | 1246746.592
7 | 2648429.1444 | 1246774.2273 | 2648438.2579 | 1246768.1866 | 2648448.7814 | 1246758.755 | 2648433.4417 | 1246739.8975
8 | 2648374.7293 | 1246689.9715 | 2648379.4612 | 1246701.5957 | 2648383.2366 | 1246713.8013 | 2648383.8092 | 1246716.7635 | 2648386.8971 | 1246732.6882 | 2648391.4092 | 1246756.4298
9 | 2648471.3297 | 1246827.9188 | 2648478.2152 | 1246836.1928
10 | 2648476.0808 | 1246746.592 | 2648481.6054 | 1246741.6116 | 2648488.352 | 1246736.1308
11 | 2648476.0808 | 1246746.592 | 2648485.8167 | 1246758.0556
12 | 2648496.1105 | 1246857.6968 | 2648478.2152 | 1246836.1928
13 | 2648328.5513 | 1246850.7252 | 2648355.9969 | 1246862.2343 | 2648375.9408 | 1246870.191 | 2648380.1092 | 1246873.0936 | 2648384.9593 | 1246878.5368 | 2648381.9536 | 1246888.6635 | 2648379.3082 | 1246900.9057 | 2648377.7391 | 1246913.6348
14 | 2648377.7391 | 1246913.6348 | 2648357.5727 | 1246909.0056
15 | 2648381.2562 | 1246745.4508 | 2648379.7503 | 1246750.4196 | 2648366.0151 | 1246772.0888 | 2648363.0693 | 1246783.2056 | 2648329.7949 | 1246847.3442 | 2648328.5513 | 1246850.7252
16 | 2648328.5513 | 1246850.7252 | 2648322.5985 | 1246848.3348
17 | 2648337.0882 | 1246902.8888 | 2648349.5652 | 1246907.1675 | 2648357.5727 | 1246909.0056
18 | 2648374.7293 | 1246689.9715 | 2648367.3436 | 1246693.4804
19 | 2648380.6455 | 1246686.0505 | 2648379.9469 | 1246686.5118 | 2648374.7293 | 1246689.9715
20 | 2648381.2562 | 1246745.4508 | 2648375.6368 | 1246712.9944 | 2648367.3436 | 1246693.4804
21 | 2648381.2562 | 1246745.4508 | 2648372.3814 | 1246742.6099 | 2648371.6275 | 1246735.9437 | 2648365.9244 | 1246724.8565 | 2648364.8463 | 1246722.7574 | 2648357.2074 | 1246715.6237 | 2648337.0154 | 1246708.3988
22 | 2648309.7295 | 1246843.1669 | 2648322.5985 | 1246848.3348
23 | 2648467.0876 | 1246883.0211 | 2648496.1105 | 1246857.6968
24 | 2648467.0876 | 1246883.0211 | 2648455.245 | 1246867.7517
25 | 2648337.0882 | 1246902.8888 | 2648333.5304 | 1246901.6687
26 | 2648380.6455 | 1246686.0505 | 2648383.1977 | 1246675.9757 | 2648385.1506 | 1246668.998 | 2648386.5086 | 1246661.7932
27 | 2648337.0154 | 1246708.3988 | 2648328.9265 | 1246705.4977 | 2648323.9582 | 1246703.4114
28 | 2648337.0154 | 1246708.3988 | 2648330.9983 | 1246724.7052 | 2648330.2531 | 1246726.0978
29 | 2648326.3902 | 1246805.3995 | 2648318.9493 | 1246822.1834 | 2648309.7295 | 1246843.1669
30 | 2648309.7295 | 1246843.1669 | 2648303.3515 | 1246840.6142
31 | 2648386.5086 | 1246661.7932 | 2648387.3808 | 1246650.2481 | 2648387.9748 | 1246637.6223 | 2648384.6824 | 1246620.8397 | 2648378.5051 | 1246591.0139 | 2648385.1656 | 1246598.651 | 2648386.8311 | 1246605.6026
32 | 2648386.5086 | 1246661.7932 | 2648380.4068 | 1246659.7643 | 2648326.8073 | 1246620.1648
33 | 2648386.8311 | 1246605.6026 | 2648413.5081 | 1246608.0309
34 | 2648436.0745 | 1246610.0851 | 2648438.1821 | 1246596.2041 | 2648440.2921 | 1246585.7143 | 2648459.7283 | 1246587.4964
35 | 2648459.7283 | 1246587.4964 | 2648463.1658 | 1246587.7318
36 | 2648436.0745 | 1246610.0851 | 2648413.5081 | 1246608.0309
37 | 2648250.7623 | 1246934.9699 | 2648272.8038 | 1246942.0508
38 | 2648229.7247 | 1246928.2114 | 2648250.7623 | 1246934.9699
39 | 2648269.9607 | 1246644.6103 | 2648274.1202 | 1246647.7018 | 2648280.948 | 1246635.7271 | 2648295.8379 | 1246616.9579 | 2648305.5917 | 1246624.131 | 2648316.4867 | 1246632.1473
40 | 2648316.4867 | 1246632.1473 | 2648304.0232 | 1246652.9379
41 | 2648253.97 | 1246679.8483 | 2648259.19 | 1246660.2999 | 2648269.9607 | 1246644.6103
42 | 2648269.9607 | 1246644.6103 | 2648267.6181 | 1246642.879 | 2648257.3937 | 1246635.2931
43 | 2648318.3603 | 1246734.0974 | 2648322.8248 | 1246733.122 | 2648328.7355 | 1246728.934 | 2648330.2531 | 1246726.0978
44 | 2648323.9582 | 1246703.4114 | 2648310.9337 | 1246697.922
45 | 2648306.0423 | 1246695.8604 | 2648310.9337 | 1246697.922
46 | 2648274.733 | 1246692.1365 | 2648281.8368 | 1246690.7823 | 2648284.0795 | 1246690.8673 | 2648295.2024 | 1246691.2914 | 2648306.0423 | 1246695.8604
47 | 2648274.733 | 1246692.1365 | 2648267.403 | 1246687.7984
48 | 2648253.97 | 1246679.8483 | 2648267.403 | 1246687.7984
49 | 2648080.3234 | 1246689.8345 | 2648087.4414 | 1246663.4412 | 2648090.0186 | 1246658.6033
50 | 2648090.0186 | 1246658.6033 | 2648129.1233 | 1246684.6933 | 2648136.0068 | 1246685.3496 | 2648142.9361 | 1246680.358 | 2648152.8963 | 1246677.0032 | 2648162.1978 | 1246678.4908
51 | 2648080.3234 | 1246689.8345 | 2648075.4012 | 1246711.8157
52 | 2648062.1412 | 1246771.0305 | 2648075.4012 | 1246711.8157
53 | 2648275.0744 | 1246788.4482 | 2648274.0439 | 1246797.2013 | 2648267.6802 | 1246809.389
54 | 2648267.1635 | 1246810.3786 | 2648267.6802 | 1246809.389
55 | 2648264.2864 | 1246778.4538 | 2648275.0744 | 1246788.4482
56 | 2648260.4474 | 1246823.2415 | 2648267.1635 | 1246810.3786
57 | 2648260.4474 | 1246823.2415 | 2648256.3096 | 1246821.4747
58 | 2648288.7165 | 1246834.7569 | 2648260.4474 | 1246823.2415
59 | 2648234.1024 | 1246812.2975 | 2648242.0508 | 1246815.3866 | 2648256.3096 | 1246821.4747
60 | 2648288.7165 | 1246834.7569 | 2648282.4727 | 1246848.7278
61 | 2648288.7165 | 1246834.7569 | 2648292.1159 | 1246836.1174
62 | 2648212.1884 | 1246803.7806 | 2648234.1024 | 1246812.2975
63 | 2648282.4727 | 1246848.7278 | 2648276.2412 | 1246862.6712
64 | 2648292.1159 | 1246836.1174 | 2648303.3515 | 1246840.6142
65 | 2648273.1094 | 1246869.6789 | 2648276.2412 | 1246862.6712
66 | 2648273.1094 | 1246869.6789 | 2648268.9479 | 1246878.9906
67 | 2648063.8701 | 1246771.1335 | 2648062.1412 | 1246771.0305
68 | 2648226.1287 | 1246770.2055 | 2648218.7231 | 1246788.0419
69 | 2648227.1964 | 1246767.6339 | 2648226.1287 | 1246770.2055
70 | 2648212.1884 | 1246803.7806 | 2648218.7231 | 1246788.0419
71 | 2648207.4146 | 1246801.9295 | 2648212.1884 | 1246803.7806
72 | 2648207.4146 | 1246801.9295 | 2648192.002 | 1246826.5541 | 2648191.6305 | 1246827.0769
73 | 2648207.4146 | 1246801.9295 | 2648190.5989 | 1246795.3778
74 | 2648191.6305 | 1246827.0769 | 2648182.4243 | 1246840.0326
75 | 2648190.5989 | 1246795.3778 | 2648159.1801 | 1246783.1364 | 2648159.1801 | 1246783.1364
76 | 2648136.7757 | 1246777.6732 | 2648159.1801 | 1246783.1364
77 | 2648136.7757 | 1246777.6732 | 2648128.3311 | 1246776.9404
78 | 2648136.7757 | 1246777.6732 | 2648132.4614 | 1246796.3116
79 | 2648063.8701 | 1246771.1335 | 2648087.4487 | 1246773.3926 | 2648128.3311 | 1246776.9404
80 | 2648132.4614 | 1246796.3116 | 2648131.593 | 1246800.0633
81 | 2648178.3021 | 1246845.8336 | 2648178.3021 | 1246845.8336 | 2648182.4243 | 1246840.0326
82 | 2648125.7666 | 1246809.872 | 2648127.1881 | 1246808.6717 | 2648130.9831 | 1246802.6985 | 2648131.593 | 1246800.0633
83 | 2648173.0829 | 1246863.3849 | 2648178.3021 | 1246845.8336
84 | 2648165.9231 | 1246887.4617 | 2648170.5738 | 1246871.8223
85 | 2648160.7878 | 1246906.0651 | 2648164.2312 | 1246893.151 | 2648165.9231 | 1246887.4617
86 | 2648173.0829 | 1246863.3849 | 2648170.5738 | 1246871.8223
87 | 2648160.7878 | 1246906.0651 | 2648177.3416 | 1246911.3831
88 | 2648177.3416 | 1246911.3831 | 2648205.2388 | 1246920.3452
89 | 2648205.2388 | 1246920.3452 | 2648229.7247 | 1246928.2114
90 | 2648238.5931 | 1246876.9766 | 2648239.5277 | 1246877.2015
91 | 2648224.537 | 1246873.5944 | 2648238.5931 | 1246876.9766
92 | 2648266.8132 | 1246883.7671 | 2648239.5277 | 1246877.2015
93 | 2648266.8132 | 1246883.7671 | 2648265.898 | 1246891.3536
94 | 2648266.8132 | 1246883.7671 | 2648268.9479 | 1246878.9906
95 | 2648319.9282 | 1246897.6531 | 2648327.413 | 1246899.5709 | 2648333.5304 | 1246901.6687

## bus_geodata
| x | y | coords
0 | 2648391.7318 | 1246855.3011
1 | 2648394.0352 | 1246814.2428
2 | 2648390.0021 | 1246782.6137
3 | 2648388.3278 | 1246772.0314
4 | 2648429.1444 | 1246774.2273
5 | 2648391.4092 | 1246756.4298
6 | 2648471.3297 | 1246827.9188
7 | 2648476.0808 | 1246746.592
8 | 2648433.4417 | 1246739.8975
9 | 2648478.2152 | 1246836.1928
10 | 2648488.352 | 1246736.1308
11 | 2648485.8167 | 1246758.0556
12 | 2648377.7391 | 1246913.6348
13 | 2648328.5512 | 1246850.7252
14 | 2648357.5727 | 1246909.0056
15 | 2648374.7293 | 1246689.9715
16 | 2648381.2562 | 1246745.4508
17 | 2648322.5985 | 1246848.3348
18 | 2648467.0876 | 1246883.0211
19 | 2648496.1105 | 1246857.6968
20 | 2648455.245 | 1246867.7517
21 | 2648337.0882 | 1246902.8888
22 | 2648367.3436 | 1246693.4804
23 | 2648380.6455 | 1246686.0505
24 | 2648337.0153 | 1246708.3988
25 | 2648309.7295 | 1246843.1669
26 | 2648386.5086 | 1246661.7932
27 | 2648386.8311 | 1246605.6026
28 | 2648326.8073 | 1246620.1648
29 | 2648459.7283 | 1246587.4964
30 | 2648436.0745 | 1246610.0851
31 | 2648463.1658 | 1246587.7318
32 | 2648413.5081 | 1246608.0309
33 | 2648272.8038 | 1246942.0508
34 | 2648250.7623 | 1246934.9699
35 | 2648316.4867 | 1246632.1473
36 | 2648269.9607 | 1246644.6103
37 | 2648304.0232 | 1246652.9379
38 | 2648330.2531 | 1246726.0978
39 | 2648318.3603 | 1246734.0974
40 | 2648323.9582 | 1246703.4114
41 | 2648310.9337 | 1246697.922
42 | 2648274.7329 | 1246692.1365
43 | 2648306.0423 | 1246695.8604
44 | 2648267.403 | 1246687.7984
45 | 2648253.97 | 1246679.8483
46 | 2648257.3937 | 1246635.2931
47 | 2648090.0186 | 1246658.6033
48 | 2648080.3234 | 1246689.8345
49 | 2648162.1978 | 1246678.4908
50 | 2648075.4012 | 1246711.8157
51 | 2648267.6802 | 1246809.389
52 | 2648275.0744 | 1246788.4482
53 | 2648267.1635 | 1246810.3786
54 | 2648264.2864 | 1246778.4538
55 | 2648260.4474 | 1246823.2415
56 | 2648256.3096 | 1246821.4747
57 | 2648288.7165 | 1246834.7569
58 | 2648234.1024 | 1246812.2975
59 | 2648282.4727 | 1246848.7278
60 | 2648292.1159 | 1246836.1174
61 | 2648303.3515 | 1246840.6142
62 | 2648326.3902 | 1246805.3995
63 | 2648276.2412 | 1246862.6712
64 | 2648273.1094 | 1246869.6789
65 | 2648062.1412 | 1246771.0305
66 | 2648226.1287 | 1246770.2055
67 | 2648218.7231 | 1246788.0419
68 | 2648227.1964 | 1246767.6339
69 | 2648212.1884 | 1246803.7806
70 | 2648207.4146 | 1246801.9295
71 | 2648191.6305 | 1246827.0769
72 | 2648190.5989 | 1246795.3778
73 | 2648159.1801 | 1246783.1364
74 | 2648136.7757 | 1246777.6732
75 | 2648128.3311 | 1246776.9404
76 | 2648132.4614 | 1246796.3116
77 | 2648182.4243 | 1246840.0326
78 | 2648063.8701 | 1246771.1335
79 | 2648131.593 | 1246800.0633
80 | 2648178.3021 | 1246845.8336
81 | 2648125.7666 | 1246809.872
82 | 2648165.9231 | 1246887.4617
83 | 2648170.5738 | 1246871.8223
84 | 2648160.7878 | 1246906.0651
85 | 2648173.0829 | 1246863.3849
86 | 2648177.3416 | 1246911.3831
87 | 2648205.2388 | 1246920.3452
88 | 2648229.7247 | 1246928.2114
89 | 2648238.5931 | 1246876.9766
90 | 2648239.5277 | 1246877.2015
91 | 2648224.537 | 1246873.5944
92 | 2648266.8132 | 1246883.7671
93 | 2648265.898 | 1246891.3536
94 | 2648268.9479 | 1246878.9906
95 | 2648333.5304 | 1246901.6687
96 | 2648319.9282 | 1246897.6531
97 | 2648309.3357 | 1246731.0886

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1