## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4023-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4023-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4023-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4023-1_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4023-1_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4023-1_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4023-1_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4023-1_0_6_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_4023-1_0_6_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_4023-1_0_6_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_4023-1_0_6_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_4023-1_0_6_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_4023-1_0_6_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_4023-1_0_6_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_4023-1_0_6_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_4023-1_0_6_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_4023-1_0_6_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_4023-1_0_6_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_4023-1_0_6_node_76 | 0.4 | n |  | TRUE
19 | bus_LV_4023-1_0_6_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_4023-1_0_6_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_4023-1_0_6_node_74 | 0.4 | n |  | TRUE
22 | bus_LV_4023-1_0_6_node_41 | 0.4 | n |  | TRUE
23 | bus_LV_4023-1_0_6_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_4023-1_0_6_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_4023-1_0_6_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_4023-1_0_6_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_4023-1_0_6_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_4023-1_0_6_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_4023-1_0_6_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_4023-1_0_6_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_4023-1_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_4023-1_0_6_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_4023-1_0_6_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_4023-1_0_6_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_4023-1_0_6_node_125 | 0.4 | n |  | TRUE
36 | bus_LV_4023-1_0_6_node_114 | 0.4 | n |  | TRUE
37 | bus_LV_4023-1_0_6_node_110 | 0.4 | n |  | TRUE
38 | bus_LV_4023-1_0_6_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_4023-1_0_6_node_33 | 0.4 | n |  | TRUE
40 | bus_LV_4023-1_0_6_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_4023-1_0_6_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_4023-1_0_6_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_4023-1_0_6_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_4023-1_0_6_node_87 | 0.4 | n |  | TRUE
45 | bus_LV_4023-1_0_6_node_36 | 0.4 | n |  | TRUE
46 | bus_LV_4023-1_0_6_node_37 | 0.4 | n |  | TRUE
47 | bus_LV_4023-1_0_6_node_38 | 0.4 | n |  | TRUE
48 | bus_LV_4023-1_0_6_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_4023-1_0_6_node_181 | 0.4 | n |  | TRUE
50 | bus_LV_4023-1_0_6_node_178 | 0.4 | n |  | TRUE
51 | bus_LV_4023-1_0_6_node_182 | 0.4 | n |  | TRUE
52 | bus_LV_4023-1_0_6_node_185 | 0.4 | n |  | TRUE
53 | bus_LV_4023-1_0_6_node_176 | 0.4 | n |  | TRUE
54 | bus_LV_4023-1_0_6_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_4023-1_0_6_node_83 | 0.4 | n |  | TRUE
56 | bus_LV_4023-1_0_6_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_4023-1_0_6_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_4023-1_0_6_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_4023-1_0_6_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_4023-1_0_6_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_4023-1_0_6_node_171 | 0.4 | n |  | TRUE
62 | bus_LV_4023-1_0_6_node_174 | 0.4 | n |  | TRUE
63 | bus_LV_4023-1_0_6_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_4023-1_0_6_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_4023-1_0_6_node_168 | 0.4 | n |  | TRUE
66 | bus_LV_4023-1_0_6_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_4023-1_0_6_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_4023-1_0_6_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_4023-1_0_6_node_184 | 0.4 | n |  | TRUE
70 | bus_LV_4023-1_0_6_node_153 | 0.4 | n |  | TRUE
71 | bus_LV_4023-1_0_6_node_169 | 0.4 | n |  | TRUE
72 | bus_LV_4023-1_0_6_node_183 | 0.4 | n |  | TRUE
73 | bus_LV_4023-1_0_6_node_152 | 0.4 | n |  | TRUE
74 | bus_LV_4023-1_0_6_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_4023-1_0_6_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_4023-1_0_6_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_4023-1_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_4023-1_0_6_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_4023-1_0_6_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_4023-1_0_6_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_4023-1_0_6_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_4023-1_0_6_node_158 | 0.4 | n |  | TRUE
83 | bus_LV_4023-1_0_6_node_130 | 0.4 | n |  | TRUE
84 | bus_LV_4023-1_0_6_node_133 | 0.4 | n |  | TRUE
85 | bus_LV_4023-1_0_6_node_134 | 0.4 | n |  | TRUE
86 | bus_LV_4023-1_0_6_node_155 | 0.4 | n |  | TRUE
87 | bus_LV_4023-1_0_6_node_132 | 0.4 | n |  | TRUE
88 | bus_LV_4023-1_0_6_node_128 | 0.4 | n |  | TRUE
89 | bus_LV_4023-1_0_6_node_135 | 0.4 | n |  | TRUE
90 | bus_LV_4023-1_0_6_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_4023-1_0_6_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_4023-1_0_6_node_65 | 0.4 | n |  | TRUE
93 | bus_LV_4023-1_0_6_node_66 | 0.4 | n |  | TRUE
94 | bus_LV_4023-1_0_6_node_67 | 0.4 | n |  | TRUE
95 | bus_LV_4023-1_0_6_node_68 | 0.4 | n |  | TRUE
96 | bus_LV_4023-1_0_6_node_69 | 0.4 | n |  | TRUE
97 | bus_LV_4023-1_0_6_node_70 | 0.4 | n |  | TRUE
98 | bus_LV_4023-1_0_6_node_71 | 0.4 | n |  | TRUE
99 | bus_LV_4023-1_0_6_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_4023-1_0_6_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_4023-1_0_6_node_124 | 0.4 | n |  | TRUE
102 | bus_LV_4023-1_0_6_node_107 | 0.4 | n |  | TRUE
103 | bus_LV_4023-1_0_6_node_73 | 0.4 | n |  | TRUE
104 | bus_LV_4023-1_0_6_node_123 | 0.4 | n |  | TRUE
105 | bus_LV_4023-1_0_6_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_4023-1_0_6_node_72 | 0.4 | n |  | TRUE
107 | bus_LV_4023-1_0_6_node_77 | 0.4 | n |  | TRUE
108 | bus_LV_4023-1_0_6_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_4023-1_0_6_node_116 | 0.4 | n |  | TRUE
110 | bus_LV_4023-1_0_6_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_4023-1_0_6_node_79 | 0.4 | n |  | TRUE
112 | bus_LV_4023-1_0_6_node_80 | 0.4 | n |  | TRUE
113 | bus_LV_4023-1_0_6_node_81 | 0.4 | n |  | TRUE
114 | bus_LV_4023-1_0_6_node_82 | 0.4 | n |  | TRUE
115 | bus_LV_4023-1_0_6_node_84 | 0.4 | n |  | TRUE
116 | bus_LV_4023-1_0_6_node_85 | 0.4 | n |  | TRUE
117 | bus_LV_4023-1_0_6_node_88 | 0.4 | n |  | TRUE
118 | bus_LV_4023-1_0_6_node_108 | 0.4 | n |  | TRUE
119 | bus_LV_4023-1_0_6_node_104 | 0.4 | n |  | TRUE
120 | bus_LV_4023-1_0_6_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_4023-1_0_6_node_109 | 0.4 | n |  | TRUE
122 | bus_LV_4023-1_0_6_node_167 | 0.4 | n |  | TRUE
123 | bus_LV_4023-1_0_6_node_166 | 0.4 | n |  | TRUE
124 | bus_LV_4023-1_0_6_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_4023-1_0_6_node_106 | 0.4 | n |  | TRUE
126 | bus_LV_4023-1_0_6_node_102 | 0.4 | n |  | TRUE
127 | bus_LV_4023-1_0_6_node_89 | 0.4 | n |  | TRUE
128 | bus_LV_4023-1_0_6_node_90 | 0.4 | n |  | TRUE
129 | bus_LV_4023-1_0_6_node_92 | 0.4 | n |  | TRUE
130 | bus_LV_4023-1_0_6_node_93 | 0.4 | n |  | TRUE
131 | bus_LV_4023-1_0_6_node_96 | 0.4 | n |  | TRUE
132 | bus_LV_4023-1_0_6_node_97 | 0.4 | n |  | TRUE
133 | bus_LV_4023-1_0_6_node_94 | 0.4 | n |  | TRUE
134 | bus_LV_4023-1_0_6_node_98 | 0.4 | n |  | TRUE
135 | bus_LV_4023-1_0_6_node_99 | 0.4 | n |  | TRUE
136 | bus_LV_4023-1_0_6_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_4023-1_0_6_node_111 | 0.4 | n |  | TRUE
138 | bus_LV_4023-1_0_6_node_115 | 0.4 | n |  | TRUE
139 | bus_LV_4023-1_0_6_node_197 | 0.4 | n |  | TRUE
140 | bus_LV_4023-1_0_6_node_113 | 0.4 | n |  | TRUE
141 | bus_LV_4023-1_0_6_node_117 | 0.4 | n |  | TRUE
142 | bus_LV_4023-1_0_6_node_103 | 0.4 | n |  | TRUE
143 | bus_LV_4023-1_0_6_node_122 | 0.4 | n |  | TRUE
144 | bus_LV_4023-1_0_6_node_121 | 0.4 | n |  | TRUE
145 | bus_LV_4023-1_0_6_node_189 | 0.4 | n |  | TRUE
146 | bus_LV_4023-1_0_6_node_196 | 0.4 | n |  | TRUE
147 | bus_LV_4023-1_0_6_node_118 | 0.4 | n |  | TRUE
148 | bus_LV_4023-1_0_6_node_119 | 0.4 | n |  | TRUE
149 | bus_LV_4023-1_0_6_node_120 | 0.4 | n |  | TRUE
150 | bus_LV_4023-1_0_6_node_207 | 0.4 | n |  | TRUE
151 | bus_LV_4023-1_0_6_node_208 | 0.4 | n |  | TRUE
152 | bus_LV_4023-1_0_6_node_187 | 0.4 | n |  | TRUE
153 | bus_LV_4023-1_0_6_node_126 | 0.4 | n |  | TRUE
154 | bus_LV_4023-1_0_6_node_127 | 0.4 | n |  | TRUE
155 | bus_LV_4023-1_0_6_node_129 | 0.4 | n |  | TRUE
156 | bus_LV_4023-1_0_6_node_131 | 0.4 | n |  | TRUE
157 | bus_LV_4023-1_0_6_node_160 | 0.4 | n |  | TRUE
158 | bus_LV_4023-1_0_6_node_165 | 0.4 | n |  | TRUE
159 | bus_LV_4023-1_0_6_node_162 | 0.4 | n |  | TRUE
160 | bus_LV_4023-1_0_6_node_163 | 0.4 | n |  | TRUE
161 | bus_LV_4023-1_0_6_node_164 | 0.4 | n |  | TRUE
162 | bus_LV_4023-1_0_6_node_136 | 0.4 | n |  | TRUE
163 | bus_LV_4023-1_0_6_node_137 | 0.4 | n |  | TRUE
164 | bus_LV_4023-1_0_6_node_138 | 0.4 | n |  | TRUE
165 | bus_LV_4023-1_0_6_node_139 | 0.4 | n |  | TRUE
166 | bus_LV_4023-1_0_6_node_140 | 0.4 | n |  | TRUE
167 | bus_LV_4023-1_0_6_node_141 | 0.4 | n |  | TRUE
168 | bus_LV_4023-1_0_6_node_142 | 0.4 | n |  | TRUE
169 | bus_LV_4023-1_0_6_node_143 | 0.4 | n |  | TRUE
170 | bus_LV_4023-1_0_6_node_144 | 0.4 | n |  | TRUE
171 | bus_LV_4023-1_0_6_node_145 | 0.4 | n |  | TRUE
172 | bus_LV_4023-1_0_6_node_146 | 0.4 | n |  | TRUE
173 | bus_LV_4023-1_0_6_node_147 | 0.4 | n |  | TRUE
174 | bus_LV_4023-1_0_6_node_148 | 0.4 | n |  | TRUE
175 | bus_LV_4023-1_0_6_node_154 | 0.4 | n |  | TRUE
176 | bus_LV_4023-1_0_6_node_156 | 0.4 | n |  | TRUE
177 | bus_LV_4023-1_0_6_node_149 | 0.4 | n |  | TRUE
178 | bus_LV_4023-1_0_6_node_150 | 0.4 | n |  | TRUE
179 | bus_LV_4023-1_0_6_node_151 | 0.4 | n |  | TRUE
180 | bus_LV_4023-1_0_6_node_157 | 0.4 | n |  | TRUE
181 | bus_LV_4023-1_0_6_node_159 | 0.4 | n |  | TRUE
182 | bus_LV_4023-1_0_6_node_161 | 0.4 | n |  | TRUE
183 | bus_LV_4023-1_0_6_node_170 | 0.4 | n |  | TRUE
184 | bus_LV_4023-1_0_6_node_172 | 0.4 | n |  | TRUE
185 | bus_LV_4023-1_0_6_node_173 | 0.4 | n |  | TRUE
186 | bus_LV_4023-1_0_6_node_198 | 0.4 | n |  | TRUE
187 | bus_LV_4023-1_0_6_node_199 | 0.4 | n |  | TRUE
188 | bus_LV_4023-1_0_6_node_204 | 0.4 | n |  | TRUE
189 | bus_LV_4023-1_0_6_node_200 | 0.4 | n |  | TRUE
190 | bus_LV_4023-1_0_6_node_202 | 0.4 | n |  | TRUE
191 | bus_LV_4023-1_0_6_node_175 | 0.4 | n |  | TRUE
192 | bus_LV_4023-1_0_6_node_177 | 0.4 | n |  | TRUE
193 | bus_LV_4023-1_0_6_node_179 | 0.4 | n |  | TRUE
194 | bus_LV_4023-1_0_6_node_180 | 0.4 | n |  | TRUE
195 | bus_LV_4023-1_0_6_node_186 | 0.4 | n |  | TRUE
196 | bus_LV_4023-1_0_6_node_188 | 0.4 | n |  | TRUE
197 | bus_LV_4023-1_0_6_node_190 | 0.4 | n |  | TRUE
198 | bus_LV_4023-1_0_6_node_191 | 0.4 | n |  | TRUE
199 | bus_LV_4023-1_0_6_node_192 | 0.4 | n |  | TRUE
200 | bus_LV_4023-1_0_6_node_193 | 0.4 | n |  | TRUE
201 | bus_LV_4023-1_0_6_node_194 | 0.4 | n |  | TRUE
202 | bus_LV_4023-1_0_6_node_195 | 0.4 | n |  | TRUE
203 | bus_LV_4023-1_0_6_node_201 | 0.4 | n |  | TRUE
204 | bus_LV_4023-1_0_6_node_203 | 0.4 | n |  | TRUE
205 | bus_LV_4023-1_0_6_node_205 | 0.4 | n |  | TRUE
206 | bus_LV_4023-1_0_6_node_209 | 0.4 | n |  | TRUE
207 | bus_MV_515_1_node_74 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4023-1_0_6_load_0 | 0 | 0.0028869 | 0.00072352 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4023-1_0_6_load_1 | 1 | 0.0046024 | 0.0011535 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4023-1_0_6_load_2 | 2 | 0.00097339 | 0.00024396 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4023-1_0_6_load_3 | 3 | 0.00163 | 0.00040851 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4023-1_0_6_load_4 | 4 | 0.0031535 | 0.00079035 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4023-1_0_6_load_5 | 5 | 0.0026765 | 0.0006708 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4023-1_0_6_load_6 | 6 | 0.0025028 | 0.00062727 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4023-1_0_6_load_27 | 7 | 0.0016594 | 0.00041589 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4023-1_0_6_load_28 | 9 | 0.0020459 | 0.00051275 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4023-1_0_6_load_7 | 11 | 0.0028036 | 0.00070265 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4023-1_0_6_load_8 | 12 | 0.0011726 | 0.00029387 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4023-1_0_6_load_10 | 13 | 0.0011671 | 0.0002925 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4023-1_0_6_load_14 | 15 | 0.0023264 | 0.00058304 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4023-1_0_6_load_16 | 16 | 0.0028037 | 0.00070267 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4023-1_0_6_load_13 | 17 | 0.0053108 | 0.001331 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4023-1_0_6_load_76 | 18 | 0.0019054 | 0.00047753 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4023-1_0_6_load_40 | 19 | 0.0017605 | 0.00044122 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4023-1_0_6_load_15 | 20 | 0.0023973 | 0.00060082 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4023-1_0_6_load_74 | 21 | 0.0040272 | 0.0010093 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4023-1_0_6_load_41 | 22 | 0.00077735 | 0.00019482 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4023-1_0_6_load_17 | 23 | 0.0036692 | 0.00091959 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4023-1_0_6_load_18 | 24 | 0.0036015 | 0.00090261 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4023-1_0_6_load_19 | 25 | 0.0022077 | 0.00055329 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4023-1_0_6_load_29 | 26 | 0.0019458 | 0.00048767 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4023-1_0_6_load_30 | 27 | 0.0018897 | 0.00047361 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4023-1_0_6_load_20 | 28 | 0.0049013 | 0.0012284 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4023-1_0_6_load_24 | 32 | 0.005943 | 0.0014895 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4023-1_0_6_load_26 | 34 | 0.0096706 | 0.0024237 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4023-1_0_6_load_125 | 35 | 0.0063122 | 0.001582 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4023-1_0_6_load_114 | 36 | 0.0065074 | 0.0016309 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4023-1_0_6_load_32 | 38 | 0.0024512 | 0.00061434 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4023-1_0_6_load_33 | 39 | 0.0016826 | 0.0004217 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4023-1_0_6_load_31 | 40 | 0.0019458 | 0.00048767 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4023-1_0_6_load_34 | 41 | 0.002117 | 0.00053058 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4023-1_0_6_load_35 | 42 | 0.0018936 | 0.00047458 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4023-1_0_6_load_43 | 43 | 0.0027125 | 0.0006798 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4023-1_0_6_load_36 | 45 | 0.0014974 | 0.00037529 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4023-1_0_6_load_39 | 48 | 0.0014752 | 0.00036972 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4023-1_0_6_load_181 | 49 | 0.0012846 | 0.00032194 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4023-1_0_6_load_178 | 50 | 0.0018676 | 0.00046806 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4023-1_0_6_load_182 | 51 | 0.0016445 | 0.00041215 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4023-1_0_6_load_185 | 52 | 0.0017356 | 0.00043499 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4023-1_0_6_load_176 | 53 | 0.0019083 | 0.00047826 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4023-1_0_6_load_42 | 54 | 0.00068786 | 0.00017239 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4023-1_0_6_load_83 | 55 | 0.0035067 | 0.00087885 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4023-1_0_6_load_44 | 56 | 0.00092317 | 0.00023137 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4023-1_0_6_load_45 | 57 | 0.0018265 | 0.00045777 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4023-1_0_6_load_46 | 58 | 0.00064518 | 0.0001617 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4023-1_0_6_load_47 | 59 | 0.0010158 | 0.00025459 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4023-1_0_6_load_48 | 60 | 0.0010129 | 0.00025387 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4023-1_0_6_load_171 | 61 | 0.0027918 | 0.00069968 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4023-1_0_6_load_174 | 62 | 0.0031132 | 0.00078024 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4023-1_0_6_load_49 | 64 | 0.00083921 | 0.00021032 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4023-1_0_6_load_168 | 65 | 0.0020284 | 0.00050838 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4023-1_0_6_load_53 | 67 | 0.0014715 | 0.00036879 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4023-1_0_6_load_54 | 68 | 0.00081702 | 0.00020476 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4023-1_0_6_load_184 | 69 | 0.00098623 | 0.00024717 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4023-1_0_6_load_153 | 70 | 0.0012235 | 0.00030663 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4023-1_0_6_load_169 | 71 | 0.0031268 | 0.00078364 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4023-1_0_6_load_183 | 72 | 0.0011628 | 0.00029143 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4023-1_0_6_load_152 | 73 | 0.0016604 | 0.00041615 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4023-1_0_6_load_55 | 74 | 0.0028615 | 0.00071715 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4023-1_0_6_load_56 | 75 | 0.0013543 | 0.00033941 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4023-1_0_6_load_57 | 76 | 0.0013247 | 0.000332 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4023-1_0_6_load_59 | 78 | 0.0041739 | 0.0010461 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4023-1_0_6_load_60 | 79 | 0.0014131 | 0.00035415 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4023-1_0_6_load_61 | 80 | 0.0016344 | 0.00040963 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4023-1_0_6_load_158 | 82 | 0.0024759 | 0.00062053 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4023-1_0_6_load_133 | 84 | 0.0020757 | 0.00052021 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4023-1_0_6_load_134 | 85 | 0.002029 | 0.00050852 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4023-1_0_6_load_132 | 87 | 0.0011995 | 0.00030063 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4023-1_0_6_load_128 | 88 | 0.0022655 | 0.00056779 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4023-1_0_6_load_135 | 89 | 0.0027329 | 0.00068492 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4023-1_0_6_load_63 | 90 | 0.0038671 | 0.00096918 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4023-1_0_6_load_64 | 91 | 0.0011992 | 0.00030055 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4023-1_0_6_load_66 | 93 | 0.0019472 | 0.00048801 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4023-1_0_6_load_67 | 94 | 0.0034045 | 0.00085326 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4023-1_0_6_load_68 | 95 | 0.0023128 | 0.00057964 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4023-1_0_6_load_69 | 96 | 0.0018798 | 0.00047113 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4023-1_0_6_load_70 | 97 | 0.0020239 | 0.00050724 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4023-1_0_6_load_78 | 100 | 0.0041039 | 0.0010285 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4023-1_0_6_load_124 | 101 | 0.00078869 | 0.00019766 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4023-1_0_6_load_107 | 102 | 0.0029511 | 0.00073963 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4023-1_0_6_load_73 | 103 | 0.0056466 | 0.0014152 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4023-1_0_6_load_123 | 104 | 0.001424 | 0.00035689 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4023-1_0_6_load_72 | 106 | 0.0019076 | 0.00047809 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4023-1_0_6_load_77 | 107 | 0.0070536 | 0.0017678 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4023-1_0_6_load_116 | 109 | 0.0071345 | 0.0017881 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4023-1_0_6_load_79 | 111 | 0.0038135 | 0.00095575 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4023-1_0_6_load_82 | 114 | 0.0020175 | 0.00050563 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4023-1_0_6_load_84 | 115 | 0.0015807 | 0.00039616 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4023-1_0_6_load_85 | 116 | 0.0010358 | 0.00025959 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4023-1_0_6_load_108 | 118 | 0.0044998 | 0.0011278 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4023-1_0_6_load_101 | 120 | 0.001552 | 0.00038897 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4023-1_0_6_load_109 | 121 | 0.0028484 | 0.00071387 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4023-1_0_6_load_167 | 122 | 0.0017688 | 0.00044331 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4023-1_0_6_load_105 | 124 | 0.005903 | 0.0014794 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4023-1_0_6_load_106 | 125 | 0.0011775 | 0.00029511 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4023-1_0_6_load_102 | 126 | 0.0021061 | 0.00052783 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4023-1_0_6_load_89 | 127 | 0.0081187 | 0.0020347 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4023-1_0_6_load_92 | 129 | 0.0015581 | 0.00039049 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4023-1_0_6_load_93 | 130 | 0.011776 | 0.0029513 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4023-1_0_6_load_96 | 131 | 0.0018118 | 0.00045408 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4023-1_0_6_load_94 | 133 | 0.0019854 | 0.00049759 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4023-1_0_6_load_99 | 135 | 0.0068827 | 0.001725 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4023-1_0_6_load_111 | 137 | 0.0041488 | 0.0010398 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4023-1_0_6_load_115 | 138 | 0.0043999 | 0.0011027 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4023-1_0_6_load_197 | 139 | 0.0083134 | 0.0020835 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4023-1_0_6_load_113 | 140 | 0.010975 | 0.0027507 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4023-1_0_6_load_117 | 141 | 0.0029611 | 0.00074211 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4023-1_0_6_load_103 | 142 | 0.0014283 | 0.00035797 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4023-1_0_6_load_121 | 144 | 0.0013894 | 0.00034823 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4023-1_0_6_load_189 | 145 | 0.0019211 | 0.00048148 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4023-1_0_6_load_196 | 146 | 0.0087904 | 0.0022031 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4023-1_0_6_load_119 | 148 | 0.0056934 | 0.0014269 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4023-1_0_6_load_120 | 149 | 0.0012762 | 0.00031985 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4023-1_0_6_load_207 | 150 | 0.0071849 | 0.0018007 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4023-1_0_6_load_126 | 153 | 0.0023774 | 0.00059582 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4023-1_0_6_load_127 | 154 | 0.002565 | 0.00064285 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4023-1_0_6_load_129 | 155 | 0.0017758 | 0.00044506 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4023-1_0_6_load_131 | 156 | 0.003036 | 0.0007609 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4023-1_0_6_load_160 | 157 | 0.0070691 | 0.0017717 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4023-1_0_6_load_165 | 158 | 0.0012752 | 0.0003196 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4023-1_0_6_load_162 | 159 | 0.0016238 | 0.00040696 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4023-1_0_6_load_163 | 160 | 0.0028707 | 0.00071946 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4023-1_0_6_load_164 | 161 | 0.0024384 | 0.00061111 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4023-1_0_6_load_136 | 162 | 0.0013002 | 0.00032586 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4023-1_0_6_load_137 | 163 | 0.0015206 | 0.0003811 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4023-1_0_6_load_138 | 164 | 0.0058302 | 0.0014612 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4023-1_0_6_load_139 | 165 | 0.0024124 | 0.00060461 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4023-1_0_6_load_140 | 166 | 0.0017088 | 0.00042826 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4023-1_0_6_load_141 | 167 | 0.0037911 | 0.00095013 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4023-1_0_6_load_142 | 168 | 0.0036479 | 0.00091424 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4023-1_0_6_load_143 | 169 | 0.0042042 | 0.0010537 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4023-1_0_6_load_144 | 170 | 0.0013751 | 0.00034463 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4023-1_0_6_load_145 | 171 | 0.0014609 | 0.00036614 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4023-1_0_6_load_146 | 172 | 0.0012556 | 0.00031469 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4023-1_0_6_load_147 | 173 | 0.00098158 | 0.00024601 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4023-1_0_6_load_148 | 174 | 0.0034987 | 0.00087685 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4023-1_0_6_load_156 | 176 | 0.0027054 | 0.00067803 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4023-1_0_6_load_149 | 177 | 0.0041104 | 0.0010302 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4023-1_0_6_load_150 | 178 | 0.00077357 | 0.00019387 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4023-1_0_6_load_151 | 179 | 0.001739 | 0.00043583 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_4023-1_0_6_load_157 | 180 | 0.0022131 | 0.00055465 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_4023-1_0_6_load_159 | 181 | 0.0012558 | 0.00031474 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_4023-1_0_6_load_161 | 182 | 0.0017129 | 0.00042928 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_4023-1_0_6_load_172 | 184 | 0.0042691 | 0.0010699 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_4023-1_0_6_load_173 | 185 | 0.0027736 | 0.00069513 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_4023-1_0_6_load_198 | 186 | 0.0030237 | 0.0007578 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_4023-1_0_6_load_199 | 187 | 0.0026278 | 0.00065859 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_4023-1_0_6_load_204 | 188 | 0.0010168 | 0.00025484 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_4023-1_0_6_load_200 | 189 | 0.0037247 | 0.00093351 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_4023-1_0_6_load_175 | 191 | 0.0018052 | 0.00045242 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_4023-1_0_6_load_177 | 192 | 0.002123 | 0.00053209 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_4023-1_0_6_load_179 | 193 | 0.0014686 | 0.00036806 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_4023-1_0_6_load_180 | 194 | 0.0024821 | 0.00062207 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_4023-1_0_6_load_186 | 195 | 0.0022227 | 0.00055706 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_4023-1_0_6_load_188 | 196 | 0.0061276 | 0.0015357 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_4023-1_0_6_load_190 | 197 | 0.0016341 | 0.00040955 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_4023-1_0_6_load_191 | 198 | 0.0018048 | 0.00045232 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_4023-1_0_6_load_192 | 199 | 0.0015106 | 0.00037859 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_4023-1_0_6_load_193 | 200 | 0.001576 | 0.00039497 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_4023-1_0_6_load_194 | 201 | 0.0021469 | 0.00053807 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_4023-1_0_6_load_195 | 202 | 0.0080183 | 0.0020096 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_4023-1_0_6_load_201 | 203 | 0.0020552 | 0.00051507 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_4023-1_0_6_load_205 | 205 | 0.0050916 | 0.0012761 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_4023-1_0_6_load_209 | 206 | 0.0032183 | 0.00080658 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4023-1_0_6_line_0 |  | 0 | 1 | 0.0030044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_4023-1_0_6_line_1 |  | 0 | 2 | 0.01427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_4023-1_0_6_line_2 |  | 1 | 3 | 0.02358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_4023-1_0_6_line_3 |  | 2 | 4 | 0.0056011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_4023-1_0_6_line_4 |  | 3 | 5 | 0.0056501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_4023-1_0_6_line_5 |  | 4 | 6 | 0.0089395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_4023-1_0_6_line_6 |  | 5 | 7 | 0.023884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_4023-1_0_6_line_7 |  | 6 | 8 | 0.016175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_4023-1_0_6_line_8 |  | 7 | 9 | 0.0039925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_4023-1_0_6_line_9 |  | 8 | 10 | 0.015765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4023-1_0_6_line_10 |  | 8 | 11 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_4023-1_0_6_line_11 |  | 9 | 38 | 0.023417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_4023-1_0_6_line_12 |  | 10 | 15 | 0.016755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4023-1_0_6_line_13 |  | 11 | 12 | 0.011004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_4023-1_0_6_line_14 |  | 12 | 13 | 0.0083284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_4023-1_0_6_line_15 |  | 13 | 14 | 0.028525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_4023-1_0_6_line_16 |  | 14 | 16 | 0.016287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4023-1_0_6_line_17 |  | 15 | 19 | 0.0014458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4023-1_0_6_line_18 |  | 16 | 20 | 0.0093687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_4023-1_0_6_line_19 |  | 17 | 18 | 0.0028359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4023-1_0_6_line_20 |  | 18 | 21 | 5.1951e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4023-1_0_6_line_21 |  | 19 | 22 | 0.016908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4023-1_0_6_line_22 |  | 20 | 23 | 0.012972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_4023-1_0_6_line_23 |  | 21 | 106 | 0.00082995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4023-1_0_6_line_24 |  | 22 | 54 | 0.015105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4023-1_0_6_line_25 |  | 23 | 24 | 0.020281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_4023-1_0_6_line_26 |  | 24 | 25 | 0.0072825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_4023-1_0_6_line_27 |  | 25 | 26 | 0.014033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_4023-1_0_6_line_28 |  | 26 | 27 | 0.012928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_4023-1_0_6_line_29 |  | 27 | 40 | 0.009979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_4023-1_0_6_line_30 |  | 28 | 29 | 0.056917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_4023-1_0_6_line_31 |  | 28 | 30 | 0.20398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
32 | LV_4023-1_0_6_line_32 |  | 29 | 31 | 0.021131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_4023-1_0_6_line_33 |  | 30 | 32 | 0.055641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4023-1_0_6_line_34 |  | 31 | 33 | 0.025634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_4023-1_0_6_line_35 |  | 31 | 34 | 0.020677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4023-1_0_6_line_36 |  | 33 | 35 | 0.017717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4023-1_0_6_line_37 |  | 33 | 36 | 0.029007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_4023-1_0_6_line_38 |  | 36 | 37 | 0.0059705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_4023-1_0_6_line_39 |  | 37 | 140 | 0.036158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4023-1_0_6_line_40 |  | 37 | 134 | 0.031765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4023-1_0_6_line_41 |  | 38 | 39 | 0.014056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_4023-1_0_6_line_42 |  | 39 | 43 | 0.019921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_4023-1_0_6_line_43 |  | 40 | 41 | 0.016057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_4023-1_0_6_line_44 |  | 41 | 42 | 0.022879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_4023-1_0_6_line_45 |  | 42 | 45 | 0.019006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_4023-1_0_6_line_46 |  | 43 | 44 | 0.018651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_4023-1_0_6_line_47 |  | 44 | 55 | 0.020141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_4023-1_0_6_line_48 |  | 45 | 46 | 0.022935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_4023-1_0_6_line_49 |  | 46 | 47 | 0.015222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_4023-1_0_6_line_50 |  | 46 | 48 | 0.028245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4023-1_0_6_line_51 |  | 47 | 49 | 0.003551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_4023-1_0_6_line_52 |  | 47 | 50 | 0.01476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4023-1_0_6_line_53 |  | 48 | 51 | 0.020754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4023-1_0_6_line_54 |  | 49 | 52 | 0.010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_4023-1_0_6_line_55 |  | 50 | 53 | 0.013983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4023-1_0_6_line_56 |  | 52 | 182 | 0.020403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_4023-1_0_6_line_57 |  | 53 | 191 | 0.011597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4023-1_0_6_line_58 |  | 55 | 112 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_4023-1_0_6_line_59 |  | 56 | 57 | 0.0022554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4023-1_0_6_line_60 |  | 56 | 58 | 0.025382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4023-1_0_6_line_61 |  | 57 | 59 | 0.0011125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4023-1_0_6_line_62 |  | 58 | 60 | 0.0064067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4023-1_0_6_line_63 |  | 59 | 61 | 0.11563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4023-1_0_6_line_64 |  | 60 | 64 | 0.011472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4023-1_0_6_line_65 |  | 61 | 62 | 0.023836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4023-1_0_6_line_66 |  | 61 | 63 | 0.033202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4023-1_0_6_line_67 |  | 62 | 188 | 0.010513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4023-1_0_6_line_68 |  | 63 | 65 | 0.015711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4023-1_0_6_line_69 |  | 63 | 66 | 0.05099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_4023-1_0_6_line_70 |  | 65 | 71 | 0.00016994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4023-1_0_6_line_71 |  | 66 | 67 | 0.016098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_4023-1_0_6_line_72 |  | 66 | 68 | 0.041905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4023-1_0_6_line_73 |  | 67 | 69 | 0.0023471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_4023-1_0_6_line_74 |  | 68 | 70 | 0.02354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4023-1_0_6_line_75 |  | 69 | 72 | 0.029316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_4023-1_0_6_line_76 |  | 70 | 73 | 0.022613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4023-1_0_6_line_77 |  | 71 | 183 | 0.016065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4023-1_0_6_line_78 |  | 72 | 181 | 0.0093942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_4023-1_0_6_line_79 |  | 73 | 179 | 0.0086719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4023-1_0_6_line_80 |  | 74 | 75 | 0.0025249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4023-1_0_6_line_81 |  | 74 | 76 | 0.027594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4023-1_0_6_line_82 |  | 75 | 77 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4023-1_0_6_line_83 |  | 76 | 78 | 0.0070541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4023-1_0_6_line_84 |  | 77 | 79 | 0.019075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_4023-1_0_6_line_85 |  | 77 | 80 | 0.017944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4023-1_0_6_line_86 |  | 78 | 81 | 0.020941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4023-1_0_6_line_87 |  | 79 | 82 | 0.017203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_4023-1_0_6_line_88 |  | 80 | 83 | 0.01108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4023-1_0_6_line_89 |  | 81 | 84 | 0.017205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4023-1_0_6_line_90 |  | 81 | 85 | 0.012924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4023-1_0_6_line_91 |  | 82 | 86 | 0.021179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
92 | LV_4023-1_0_6_line_92 |  | 83 | 87 | 0.040791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4023-1_0_6_line_93 |  | 83 | 88 | 0.016199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4023-1_0_6_line_94 |  | 84 | 89 | 0.00024665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4023-1_0_6_line_95 |  | 86 | 180 | 0.012863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_4023-1_0_6_line_96 |  | 86 | 175 | 0.033189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_4023-1_0_6_line_97 |  | 87 | 157 | 0.014777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4023-1_0_6_line_98 |  | 88 | 153 | 0.0025322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4023-1_0_6_line_99 |  | 89 | 160 | 0.02203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4023-1_0_6_line_100 |  | 90 | 91 | 0.0015973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4023-1_0_6_line_101 |  | 90 | 92 | 0.033865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4023-1_0_6_line_102 |  | 91 | 93 | 0.014253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4023-1_0_6_line_103 |  | 92 | 94 | 0.020684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4023-1_0_6_line_104 |  | 92 | 95 | 0.016388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4023-1_0_6_line_105 |  | 93 | 96 | 0.0076499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4023-1_0_6_line_106 |  | 94 | 97 | 0.015001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4023-1_0_6_line_107 |  | 95 | 98 | 0.026914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4023-1_0_6_line_108 |  | 96 | 99 | 0.021881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4023-1_0_6_line_109 |  | 97 | 100 | 0.0073008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4023-1_0_6_line_110 |  | 98 | 101 | 0.012665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_4023-1_0_6_line_111 |  | 98 | 102 | 0.034419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
112 | LV_4023-1_0_6_line_112 |  | 99 | 103 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4023-1_0_6_line_113 |  | 101 | 104 | 0.011663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_4023-1_0_6_line_114 |  | 102 | 105 | 0.0097668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_4023-1_0_6_line_115 |  | 103 | 106 | 0.024752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4023-1_0_6_line_116 |  | 104 | 131 | 0.0089011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
117 | LV_4023-1_0_6_line_117 |  | 105 | 118 | 0.0058944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_4023-1_0_6_line_118 |  | 107 | 108 | 0.029592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4023-1_0_6_line_119 |  | 108 | 109 | 0.034305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
120 | LV_4023-1_0_6_line_120 |  | 108 | 110 | 0.016569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_4023-1_0_6_line_121 |  | 109 | 141 | 0.0016621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4023-1_0_6_line_122 |  | 110 | 135 | 0.0050343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
123 | LV_4023-1_0_6_line_123 |  | 111 | 112 | 0.0042119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
124 | LV_4023-1_0_6_line_124 |  | 111 | 113 | 0.025962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
125 | LV_4023-1_0_6_line_125 |  | 112 | 114 | 0.015786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4023-1_0_6_line_126 |  | 113 | 115 | 0.032933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4023-1_0_6_line_127 |  | 113 | 116 | 0.018829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_4023-1_0_6_line_128 |  | 116 | 117 | 0.0063389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_4023-1_0_6_line_129 |  | 117 | 119 | 0.002791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_4023-1_0_6_line_130 |  | 117 | 120 | 0.013754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4023-1_0_6_line_131 |  | 118 | 121 | 0.028391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_4023-1_0_6_line_132 |  | 119 | 124 | 0.01987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4023-1_0_6_line_133 |  | 119 | 125 | 0.019707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
134 | LV_4023-1_0_6_line_134 |  | 120 | 126 | 0.0081391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4023-1_0_6_line_135 |  | 121 | 144 | 0.017865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_4023-1_0_6_line_136 |  | 122 | 123 | 0.022249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4023-1_0_6_line_137 |  | 123 | 158 | 0.055384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4023-1_0_6_line_138 |  | 123 | 156 | 0.0057438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4023-1_0_6_line_139 |  | 124 | 143 | 0.019092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4023-1_0_6_line_140 |  | 125 | 144 | 0.013291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
141 | LV_4023-1_0_6_line_141 |  | 126 | 142 | 0.036711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4023-1_0_6_line_142 |  | 127 | 128 | 0.0084792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4023-1_0_6_line_143 |  | 128 | 129 | 0.013878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
144 | LV_4023-1_0_6_line_144 |  | 128 | 130 | 0.018411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
145 | LV_4023-1_0_6_line_145 |  | 129 | 131 | 0.00082732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
146 | LV_4023-1_0_6_line_146 |  | 130 | 132 | 0.0129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
147 | LV_4023-1_0_6_line_147 |  | 132 | 136 | 0.019523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
148 | LV_4023-1_0_6_line_148 |  | 133 | 134 | 0.011984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4023-1_0_6_line_149 |  | 134 | 135 | 0.016569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
150 | LV_4023-1_0_6_line_150 |  | 134 | 137 | 0.010578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
151 | LV_4023-1_0_6_line_151 |  | 136 | 138 | 0.017316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
152 | LV_4023-1_0_6_line_152 |  | 136 | 139 | 0.0072195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4023-1_0_6_line_153 |  | 137 | 138 | 0.010292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
154 | LV_4023-1_0_6_line_154 |  | 139 | 146 | 0.013911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4023-1_0_6_line_155 |  | 141 | 147 | 0.013882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4023-1_0_6_line_156 |  | 143 | 145 | 0.016852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4023-1_0_6_line_157 |  | 145 | 152 | 0.032205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4023-1_0_6_line_158 |  | 146 | 202 | 0.020529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4023-1_0_6_line_159 |  | 147 | 148 | 0.023044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4023-1_0_6_line_160 |  | 147 | 149 | 0.025842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4023-1_0_6_line_161 |  | 148 | 150 | 0.013763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4023-1_0_6_line_162 |  | 150 | 151 | 0.0037255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4023-1_0_6_line_163 |  | 151 | 206 | 0.022327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4023-1_0_6_line_164 |  | 152 | 196 | 0.004931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4023-1_0_6_line_165 |  | 152 | 195 | 0.023849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4023-1_0_6_line_166 |  | 153 | 154 | 0.021961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4023-1_0_6_line_167 |  | 154 | 155 | 0.035154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4023-1_0_6_line_168 |  | 155 | 156 | 0.0077065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4023-1_0_6_line_169 |  | 157 | 159 | 0.013851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4023-1_0_6_line_170 |  | 159 | 167 | 0.0049826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4023-1_0_6_line_171 |  | 160 | 161 | 0.001156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4023-1_0_6_line_172 |  | 162 | 163 | 0.015798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4023-1_0_6_line_173 |  | 162 | 164 | 0.0003202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4023-1_0_6_line_174 |  | 163 | 165 | 0.02734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4023-1_0_6_line_175 |  | 165 | 166 | 0.0071114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4023-1_0_6_line_176 |  | 166 | 167 | 0.017735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4023-1_0_6_line_177 |  | 168 | 169 | 0.024343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_4023-1_0_6_line_178 |  | 168 | 170 | 0.0031555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_4023-1_0_6_line_179 |  | 169 | 171 | 0.0051273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_4023-1_0_6_line_180 |  | 170 | 172 | 0.027763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_4023-1_0_6_line_181 |  | 171 | 173 | 0.00093515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_4023-1_0_6_line_182 |  | 172 | 174 | 0.0016266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_4023-1_0_6_line_183 |  | 173 | 175 | 0.018633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_4023-1_0_6_line_184 |  | 175 | 176 | 0.0029409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
185 | LV_4023-1_0_6_line_185 |  | 176 | 181 | 0.031369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
186 | LV_4023-1_0_6_line_186 |  | 177 | 178 | 0.010356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_4023-1_0_6_line_187 |  | 177 | 179 | 0.03433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_4023-1_0_6_line_188 |  | 180 | 182 | 0.00070279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
189 | LV_4023-1_0_6_line_189 |  | 183 | 184 | 0.021625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_4023-1_0_6_line_190 |  | 183 | 185 | 0.019183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_4023-1_0_6_line_191 |  | 184 | 186 | 0.018036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_4023-1_0_6_line_192 |  | 185 | 187 | 0.015067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_4023-1_0_6_line_193 |  | 187 | 189 | 0.010847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_4023-1_0_6_line_194 |  | 188 | 190 | 0.021745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_4023-1_0_6_line_195 |  | 190 | 203 | 0.013251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_4023-1_0_6_line_196 |  | 191 | 192 | 0.035738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_4023-1_0_6_line_197 |  | 192 | 193 | 0.026969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_4023-1_0_6_line_198 |  | 193 | 194 | 0.017195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_4023-1_0_6_line_199 |  | 197 | 198 | 0.00094152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_4023-1_0_6_line_200 |  | 197 | 199 | 0.021755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_4023-1_0_6_line_201 |  | 198 | 200 | 0.028412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_4023-1_0_6_line_202 |  | 199 | 201 | 0.0064269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_4023-1_0_6_line_203 |  | 201 | 202 | 0.015259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_4023-1_0_6_line_204 |  | 203 | 204 | 0.018949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_4023-1_0_6_line_205 |  | 204 | 205 | 0.025104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4023-1_0_6_trafo_27 | 0.63 MVA 20/0.4 kV | 207 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2670793.9084 | 1249876.4488 | 2670791.7971 | 1249878.5864
1 | 2670793.9084 | 1249876.4488 | 2670800.5226 | 1249869.7519 | 2670803.7224 | 1249866.0972
2 | 2670791.7971 | 1249878.5864 | 2670788.8983 | 1249881.5215 | 2670775.3265 | 1249895.4609
3 | 2670807.4617 | 1249861.9283 | 2670806.3706 | 1249863.0725 | 2670803.7224 | 1249866.0972
4 | 2670771.385 | 1249899.5092 | 2670775.3265 | 1249895.4609
5 | 2670807.4617 | 1249861.9283 | 2670813.6308 | 1249855.4587
6 | 2670771.385 | 1249899.5092 | 2670767.121 | 1249903.8887 | 2670754.0521 | 1249915.9318
7 | 2670825.9147 | 1249845.0152 | 2670824.2082 | 1249846.2957 | 2670817.7554 | 1249851.1332 | 2670813.6308 | 1249855.4587
8 | 2670751.1161 | 1249918.6373 | 2670754.0521 | 1249915.9318
9 | 2670825.9147 | 1249845.0152 | 2670813.6438 | 1249835.0726
10 | 2670825.9147 | 1249845.0152 | 2670836.9497 | 1249838.9761 | 2670846.9134 | 1249836.2294
11 | 2670731.8005 | 1249931.7795 | 2670735.379 | 1249929.9619 | 2670749.7536 | 1249919.8928 | 2670751.1161 | 1249918.6373
12 | 2670813.6438 | 1249835.0726 | 2670822.1363 | 1249820.6291
13 | 2670846.9134 | 1249836.2294 | 2670853.0316 | 1249834.5428 | 2670857.6798 | 1249834.2499
14 | 2670857.6798 | 1249834.2499 | 2670860.5949 | 1249834.0662 | 2670865.9933 | 1249833.7528
15 | 2670894.511 | 1249833.36 | 2670870.2809 | 1249833.5038 | 2670865.9933 | 1249833.7528
16 | 2670894.511 | 1249833.36 | 2670895.0653 | 1249844.4524 | 2670895.3983 | 1249849.6228
17 | 2670822.8691 | 1249819.3829 | 2670822.1363 | 1249820.6291
18 | 2670896.0003 | 1249858.9721 | 2670895.3983 | 1249849.6228
19 | 2670770.7624 | 1249808.2156 | 2670773.1656 | 1249809.7212
20 | 2670770.7183 | 1249808.188 | 2670770.7624 | 1249808.2156
21 | 2670822.8691 | 1249819.3829 | 2670831.4389 | 1249804.808
22 | 2670895.1644 | 1249871.8543 | 2670895.386 | 1249871.2865 | 2670896.2305 | 1249862.5459 | 2670896.0003 | 1249858.9721
23 | 2670770.015 | 1249807.7474 | 2670770.7183 | 1249808.188
24 | 2670846.1211 | 1249801.2586 | 2670831.4389 | 1249804.808
25 | 2670895.1644 | 1249871.8543 | 2670892.2159 | 1249879.41 | 2670888.7926 | 1249885.3511 | 2670885.2193 | 1249889.2837
26 | 2670885.2193 | 1249889.2837 | 2670880.3219 | 1249894.6735
27 | 2670870.4588 | 1249904.6515 | 2670878.5482 | 1249896.6256 | 2670880.3219 | 1249894.6735
28 | 2670870.4588 | 1249904.6515 | 2670864.7949 | 1249910.271 | 2670860.9756 | 1249913.419
29 | 2670853.2752 | 1249919.7659 | 2670860.9756 | 1249913.419
30 | 2670598.8715 | 1249686.961 | 2670554.5561 | 1249651.2433
31 | 2670554.5561 | 1249651.2433 | 2670497.0533 | 1249455.5397
32 | 2670598.8715 | 1249686.961 | 2670609.5687 | 1249689.6236 | 2670619.4857 | 1249691.8655
33 | 2670497.0533 | 1249455.5397 | 2670484.5509 | 1249454.1567 | 2670472.4724 | 1249450.1436 | 2670459.6395 | 1249443.5308 | 2670451.4283 | 1249439.397 | 2670445.2884 | 1249436.702
34 | 2670619.4857 | 1249691.8655 | 2670628.825 | 1249693.8004 | 2670638.6855 | 1249695.7192 | 2670644.6566 | 1249697.0802
35 | 2670619.4857 | 1249691.8655 | 2670616.3373 | 1249699.4668 | 2670611.1265 | 1249710.773
36 | 2670644.6566 | 1249697.0802 | 2670646.5759 | 1249687.4517 | 2670647.1757 | 1249679.5755
37 | 2670644.6566 | 1249697.0802 | 2670658.2843 | 1249703.4583 | 2670670.857 | 1249709.5266
38 | 2670674.9755 | 1249713.7979 | 2670671.3466 | 1249709.7629 | 2670670.857 | 1249709.5266
39 | 2670705.2601 | 1249710.59 | 2670696.2068 | 1249704.3109 | 2670686.9352 | 1249713.7849 | 2670674.9755 | 1249713.7979
40 | 2670674.9755 | 1249713.7979 | 2670674.5775 | 1249718.6745 | 2670674.44 | 1249723.8765 | 2670673.4265 | 1249732.882 | 2670672.1192 | 1249739.9381 | 2670670.7504 | 1249745.1923
41 | 2670731.8005 | 1249931.7795 | 2670719.2681 | 1249938.1449
42 | 2670719.2681 | 1249938.1449 | 2670717.7333 | 1249938.9245 | 2670702.622 | 1249944.9374 | 2670700.9621 | 1249945.934
43 | 2670853.2752 | 1249919.7659 | 2670847.9737 | 1249924.1354 | 2670840.1573 | 1249928.9626
44 | 2670820.8194 | 1249941.1793 | 2670824.2882 | 1249938.7629 | 2670840.1573 | 1249928.9626
45 | 2670820.8194 | 1249941.1793 | 2670814.5431 | 1249945.5514 | 2670808.5312 | 1249952.6736 | 2670807.7332 | 1249954.5476
46 | 2670684.9721 | 1249955.5346 | 2670700.9621 | 1249945.934
47 | 2670684.9721 | 1249955.5346 | 2670680.347 | 1249950.8538 | 2670673.912 | 1249942.1932 | 2670672.2737 | 1249939.9579
48 | 2670804.1592 | 1249976.7275 | 2670803.5669 | 1249968.8036 | 2670804.4142 | 1249962.3424 | 2670807.7332 | 1249954.5476
49 | 2670804.1592 | 1249976.7275 | 2670809.4017 | 1249991.0225
50 | 2670804.1592 | 1249976.7275 | 2670797.7851 | 1249976.2621 | 2670776.5563 | 1249971.0716
51 | 2670809.4017 | 1249991.0225 | 2670810.5367 | 1249994.3873
52 | 2670809.4017 | 1249991.0225 | 2670816.7488 | 1249988.4084 | 2670823.2906 | 1249986.0274
53 | 2670766.3297 | 1249986.5718 | 2670768.3818 | 1249977.2118 | 2670771.0441 | 1249972.3957 | 2670776.5563 | 1249971.0716
54 | 2670810.5367 | 1249994.3873 | 2670813.7444 | 1250003.8966
55 | 2670823.2906 | 1249986.0274 | 2670830.1478 | 1249983.5317 | 2670836.2841 | 1249980.8769
56 | 2670820.2657 | 1250023.2291 | 2670813.7444 | 1250003.8966
57 | 2670846.0296 | 1249974.6798 | 2670838.9512 | 1249979.723 | 2670836.2841 | 1249980.8769
58 | 2670660.0141 | 1249924.3369 | 2670667.9019 | 1249933.9934 | 2670672.2737 | 1249939.9579
59 | 2671078.2443 | 1250044.0919 | 2671079.6664 | 1250042.3413
60 | 2671078.2443 | 1250044.0919 | 2671074.2212 | 1250049.044 | 2671074.5509 | 1250064.3589 | 2671072.2714 | 1250067.2523
61 | 2671080.3679 | 1250041.4778 | 2671079.6664 | 1250042.3413
62 | 2671068.3066 | 1250072.2849 | 2671072.2714 | 1250067.2523
63 | 2670992.874 | 1249965.8782 | 2671080.3679 | 1250041.4778
64 | 2671061.2071 | 1250081.2963 | 2671068.3066 | 1250072.2849
65 | 2671007.289 | 1249946.8944 | 2671003.0278 | 1249952.5218 | 2670992.874 | 1249965.8782
66 | 2670973.5824 | 1249992.8981 | 2670990.4629 | 1249969.0498 | 2670992.874 | 1249965.8782
67 | 2671007.289 | 1249946.8944 | 2671013.6357 | 1249938.513
68 | 2670973.5824 | 1249992.8981 | 2670964.6376 | 1249986.442 | 2670960.8528 | 1249983.6899
69 | 2670973.5824 | 1249992.8981 | 2670959.1437 | 1250012.7062 | 2670951.7151 | 1250024.0143 | 2670945.9511 | 1250035.6536
70 | 2670960.8528 | 1249983.6899 | 2670960.7154 | 1249983.59
71 | 2670945.9511 | 1250035.6536 | 2670939.9359 | 1250032.9575 | 2670931.1101 | 1250029.4261
72 | 2670945.9511 | 1250035.6536 | 2670933.5653 | 1250063.1029 | 2670928.5386 | 1250073.7682
73 | 2670928.931 | 1250028.5542 | 2670931.1101 | 1250029.4261
74 | 2670928.5386 | 1250073.7682 | 2670918.5028 | 1250095.0613
75 | 2670928.931 | 1250028.5542 | 2670924.8105 | 1250026.9055 | 2670918.6194 | 1250026.9204 | 2670912.5878 | 1250028.1157 | 2670900.5944 | 1250031.7705
76 | 2670918.5028 | 1250095.0613 | 2670914.2996 | 1250103.9795 | 2670908.9444 | 1250115.5544
77 | 2670947.722 | 1249974.1418 | 2670960.7154 | 1249983.59
78 | 2670891.574 | 1250034.3937 | 2670899.5621 | 1250032.085 | 2670900.5944 | 1250031.7705
79 | 2670908.9444 | 1250115.5544 | 2670905.3031 | 1250123.4248
80 | 2670794.589 | 1250103.4595 | 2670795.4485 | 1250101.0854
81 | 2670794.589 | 1250103.4595 | 2670794.589 | 1250103.4595 | 2670792.4322 | 1250113.9969 | 2670791.5365 | 1250123.2484 | 2670790.6127 | 1250130.7346
82 | 2670803.887 | 1250088.5821 | 2670798.2142 | 1250095.7751 | 2670796.0881 | 1250099.3189 | 2670795.4485 | 1250101.0854
83 | 2670788.3949 | 1250137.4013 | 2670790.4665 | 1250131.9196 | 2670790.6127 | 1250130.7346
84 | 2670803.887 | 1250088.5821 | 2670809.6862 | 1250079.6561 | 2670813.8426 | 1250073.6348 | 2670814.415 | 1250072.6797
85 | 2670803.887 | 1250088.5821 | 2670793.511 | 1250081.8423 | 2670788.5471 | 1250079.3126
86 | 2670779.357 | 1250156.26 | 2670781.722 | 1250151.6738 | 2670786.4047 | 1250142.6677 | 2670788.3949 | 1250137.4013
87 | 2670814.415 | 1250072.6797 | 2670818.0641 | 1250066.5913 | 2670821.1312 | 1250058.8557 | 2670821.5406 | 1250057.12
88 | 2670778.6754 | 1250074.282 | 2670788.5471 | 1250079.3126
89 | 2670779.357 | 1250156.26 | 2670771.7618 | 1250164.4863 | 2670768.2781 | 1250169.3823
90 | 2670779.357 | 1250156.26 | 2670784.9322 | 1250159.7513 | 2670789.9113 | 1250163.6856
91 | 2670824.2636 | 1250036.188 | 2670823.9473 | 1250044.9571 | 2670822.682 | 1250052.2806 | 2670821.5406 | 1250057.12
92 | 2670778.6754 | 1250074.282 | 2670773.9368 | 1250082.9094 | 2670767.5523 | 1250090.9055 | 2670758.2284 | 1250102.9029 | 2670754.3045 | 1250106.7877
93 | 2670778.6754 | 1250074.282 | 2670771.5449 | 1250070.1494 | 2670764.6208 | 1250066.2283
94 | 2670768.1351 | 1250169.5833 | 2670768.2781 | 1250169.3823
95 | 2670824.2636 | 1250036.188 | 2670822.3149 | 1250029.3042 | 2670820.4903 | 1250023.8951
96 | 2670824.2636 | 1250036.188 | 2670829.4567 | 1250035.6496 | 2670836.9045 | 1250034.7157 | 2670844.188 | 1250034.8918 | 2670857.4356 | 1250035.7285
97 | 2670743.5616 | 1250116.9312 | 2670750.405 | 1250110.6484 | 2670754.3045 | 1250106.7877
98 | 2670762.4175 | 1250064.9806 | 2670764.6208 | 1250066.2283
99 | 2670768.1351 | 1250169.5833 | 2670763.0697 | 1250176.7024 | 2670755.2068 | 1250187.4207
100 | 2670704.4485 | 1249830.3118 | 2670705.4733 | 1249829.0866
101 | 2670681.9486 | 1249855.2045 | 2670684.2233 | 1249854.3977 | 2670686.2442 | 1249852.0757 | 2670704.4485 | 1249830.3118
102 | 2670714.6181 | 1249818.1536 | 2670705.4733 | 1249829.0866
103 | 2670681.9486 | 1249855.2045 | 2670691.9373 | 1249873.3172
104 | 2670681.9486 | 1249855.2045 | 2670678.4981 | 1249855.2189 | 2670674.3189 | 1249853.6568 | 2670666.8444 | 1249849.6595
105 | 2670719.5262 | 1249812.2859 | 2670714.6181 | 1249818.1536
106 | 2670701.7058 | 1249884.6401 | 2670692.8492 | 1249874.9708 | 2670691.9373 | 1249873.3172
107 | 2670642.2642 | 1249838.842 | 2670656.7111 | 1249844.2402 | 2670666.8444 | 1249849.6595
108 | 2670733.3172 | 1249795.3075 | 2670730.3164 | 1249799.3858 | 2670719.5262 | 1249812.2859
109 | 2670706.6371 | 1249890.0238 | 2670701.7058 | 1249884.6401
110 | 2670642.2642 | 1249838.842 | 2670644.9716 | 1249831.5024 | 2670647.7572 | 1249827.5422
111 | 2670642.2642 | 1249838.842 | 2670640.0673 | 1249845.7875 | 2670639.4925 | 1249852.2074 | 2670640.6831 | 1249868.8669 | 2670640.9135 | 1249872.8468
112 | 2670733.3172 | 1249795.3075 | 2670737.4802 | 1249791.2765 | 2670742.4536 | 1249791.4582 | 2670748.1532 | 1249794.0503 | 2670749.0401 | 1249794.606
113 | 2670654.4684 | 1249818.0035 | 2670654.4107 | 1249818.083 | 2670647.7572 | 1249827.5422
114 | 2670641.4782 | 1249882.5973 | 2670640.9135 | 1249872.8468
115 | 2670749.0401 | 1249794.606 | 2670766.5887 | 1249805.6008 | 2670770.015 | 1249807.7474
116 | 2670654.4684 | 1249818.0035 | 2670659.6959 | 1249810.7991
117 | 2670641.4782 | 1249882.5973 | 2670637.7694 | 1249887.1786 | 2670637.7694 | 1249887.1786
118 | 2670708.5175 | 1249740.6838 | 2670711.9797 | 1249746.0289 | 2670721.666 | 1249754.9397 | 2670721.3769 | 1249758.9168 | 2670718.3073 | 1249764.1587
119 | 2670708.5175 | 1249740.6838 | 2670712.9928 | 1249738.9581 | 2670721.5445 | 1249735.3909 | 2670733.4714 | 1249730.5408 | 2670739.981 | 1249727.0908
120 | 2670692.3089 | 1249744.3375 | 2670708.5175 | 1249740.6838
121 | 2670741.4496 | 1249726.3125 | 2670739.981 | 1249727.0908
122 | 2670692.3089 | 1249744.3375 | 2670687.3071 | 1249744.9089
123 | 2670660.0141 | 1249924.3369 | 2670660.662 | 1249928.4987
124 | 2670659.8162 | 1249953.5889 | 2670662.2605 | 1249949.9487 | 2670662.5486 | 1249944.7818 | 2670661.7883 | 1249935.7329 | 2670660.662 | 1249928.4987
125 | 2670660.0141 | 1249924.3369 | 2670653.6297 | 1249915.2321 | 2670651.7114 | 1249910.9792
126 | 2670659.8162 | 1249953.5889 | 2670677.8333 | 1249981.19
127 | 2670659.8162 | 1249953.5889 | 2670656.4593 | 1249955.8838 | 2670652.0932 | 1249958.6004 | 2670643.1287 | 1249962.0904
128 | 2670637.2188 | 1249964.3829 | 2670638.8192 | 1249963.7682 | 2670643.1287 | 1249962.0904
129 | 2670637.2188 | 1249964.3829 | 2670634.5657 | 1249965.2741
130 | 2670637.2188 | 1249964.3829 | 2670644.0552 | 1249976.3181
131 | 2670637.7694 | 1249887.1786 | 2670634.5712 | 1249902.7517 | 2670632.4866 | 1249915.0696
132 | 2670634.5657 | 1249965.2741 | 2670623.2589 | 1249973.89 | 2670619.3739 | 1249976.7903 | 2670618.7229 | 1249977.2656
133 | 2670634.5657 | 1249965.2741 | 2670633.3732 | 1249960.1785 | 2670630.62 | 1249945.9696
134 | 2670644.0552 | 1249976.3181 | 2670648.1006 | 1249983.3807
135 | 2670632.4866 | 1249915.0696 | 2670630.3477 | 1249927.7081 | 2670629.9804 | 1249932.7417
136 | 2670723.4519 | 1250012.0228 | 2670721.7021 | 1250001.7501 | 2670719.841 | 1249996.3796 | 2670717.3606 | 1249991.024 | 2670717.2142 | 1249990.8308
137 | 2670723.4519 | 1250012.0228 | 2670720.2241 | 1250018.6779 | 2670712.8793 | 1250040.7172 | 2670702.2935 | 1250063.0967
138 | 2670723.4519 | 1250012.0228 | 2670724.3819 | 1250017.6908
139 | 2670605.6694 | 1249990.8371 | 2670608.6825 | 1249985.7138 | 2670613.8293 | 1249980.8383 | 2670618.7229 | 1249977.2656
140 | 2670629.9804 | 1249932.7417 | 2670629.6709 | 1249936.9844 | 2670630.514 | 1249945.4228 | 2670630.62 | 1249945.9696
141 | 2670672.6066 | 1250007.3242 | 2670670.1854 | 1249999.5342 | 2670652.7504 | 1249991.4985 | 2670648.1006 | 1249983.3807
142 | 2670668.1333 | 1249798.7549 | 2670672.1981 | 1249793.4552 | 2670673.0874 | 1249791.8901
143 | 2670668.1333 | 1249798.7549 | 2670660.1803 | 1249810.1285
144 | 2670668.1333 | 1249798.7549 | 2670666.1506 | 1249794.7062 | 2670662.2923 | 1249789.0228 | 2670657.1916 | 1249784.1793
145 | 2670659.6959 | 1249810.7991 | 2670660.1219 | 1249810.2121 | 2670660.1803 | 1249810.1285
146 | 2670649.6883 | 1249774.0619 | 2670649.9521 | 1249775.9998 | 2670654.5131 | 1249781.6359 | 2670657.1916 | 1249784.1793
147 | 2670649.6883 | 1249774.0619 | 2670644.3346 | 1249774.1093 | 2670639.3931 | 1249769.9919 | 2670642.1081 | 1249766.4439 | 2670639.482 | 1249764.4334
148 | 2670670.7504 | 1249745.1923 | 2670672.3959 | 1249748.3919 | 2670676.1273 | 1249753.9515 | 2670676.851 | 1249755.4793
149 | 2670670.7504 | 1249745.1923 | 2670677.7668 | 1249744.998 | 2670685.8749 | 1249745.0725 | 2670687.3071 | 1249744.9089
150 | 2670670.7504 | 1249745.1923 | 2670665.561 | 1249746.6537 | 2670660.5226 | 1249747.8875
151 | 2670639.482 | 1249764.4334 | 2670643.2051 | 1249759.9301 | 2670648.3886 | 1249753.2537 | 2670651.1026 | 1249751.9268
152 | 2670639.482 | 1249764.4334 | 2670634.6822 | 1249769.8263
153 | 2670651.1026 | 1249751.9268 | 2670658.2007 | 1249748.4561 | 2670660.5226 | 1249747.8875
154 | 2670625.6462 | 1249780.4014 | 2670631.7068 | 1249773.1692 | 2670634.6822 | 1249769.8263
155 | 2670752.518 | 1249718.1147 | 2670746.4797 | 1249723.6466 | 2670741.4496 | 1249726.3125
156 | 2670605.6694 | 1249990.8371 | 2670606.5816 | 1249997.2859 | 2670608.388 | 1250003.4563 | 2670609.6746 | 1250007.1485
157 | 2670624.8619 | 1250035.1196 | 2670620.5016 | 1250030.3977 | 2670613.9362 | 1250019.3782 | 2670609.6746 | 1250007.1485
158 | 2670625.6462 | 1249780.4014 | 2670621.1525 | 1249785.7636 | 2670614.3424 | 1249792.0871 | 2670611.0591 | 1249794.7696
159 | 2670752.518 | 1249718.1147 | 2670763.9949 | 1249719.3415 | 2670775.2033 | 1249721.9237
160 | 2670752.518 | 1249718.1147 | 2670750.0123 | 1249711.7136 | 2670751.6142 | 1249701.4921 | 2670753.415 | 1249693.0605
161 | 2670788.6152 | 1249725.0136 | 2670775.2033 | 1249721.9237
162 | 2670792.2457 | 1249725.85 | 2670788.6152 | 1249725.0136
163 | 2670792.2457 | 1249725.85 | 2670798.602 | 1249727.1936 | 2670814.151 | 1249730.1642
164 | 2670624.8619 | 1250035.1196 | 2670628.1093 | 1250038.8388
165 | 2670624.8619 | 1250035.1196 | 2670629.2928 | 1250035.8285 | 2670648.632 | 1250036.7596
166 | 2670762.4175 | 1250064.9806 | 2670759.0289 | 1250063.0616 | 2670753.1217 | 1250059.5442 | 2670747.2941 | 1250056.3056 | 2670743.5534 | 1250053.7598
167 | 2670743.5534 | 1250053.7598 | 2670740.8087 | 1250051.8918 | 2670735.9831 | 1250048.1982 | 2670732.1892 | 1250044.0944 | 2670729.1487 | 1250039.4993 | 2670726.457 | 1250030.3384 | 2670725.6296 | 1250025.2956
168 | 2670724.3819 | 1250017.6908 | 2670725.6296 | 1250025.2956
169 | 2670743.5616 | 1250116.9312 | 2670743.5425 | 1250116.9488 | 2670737.397 | 1250123.2689 | 2670734.2162 | 1250127.1393
170 | 2670731.0615 | 1250130.9955 | 2670731.1533 | 1250130.8665 | 2670734.2162 | 1250127.1393
171 | 2670754.523 | 1250188.3528 | 2670755.2068 | 1250187.4207
172 | 2670710.0998 | 1250186.4573 | 2670716.619 | 1250172.0671
173 | 2670710.0998 | 1250186.4573 | 2670709.9676 | 1250186.7489
174 | 2670717.3287 | 1250151.6917 | 2670717.0687 | 1250152.1026 | 2670708.6157 | 1250167.6907 | 2670716.619 | 1250172.0671 | 2670716.619 | 1250172.0671
175 | 2670717.3287 | 1250151.6917 | 2670721.1314 | 1250145.6824
176 | 2670731.0615 | 1250130.9955 | 2670725.3022 | 1250139.0915 | 2670721.1314 | 1250145.6824
177 | 2670853.7055 | 1250084.2717 | 2670856.3185 | 1250077.3672 | 2670856.902 | 1250060.4168
178 | 2670853.7055 | 1250084.2717 | 2670853.5119 | 1250084.7834 | 2670852.4298 | 1250087.1567
179 | 2670856.902 | 1250060.4168 | 2670856.9433 | 1250059.2172 | 2670857.0664 | 1250055.2922
180 | 2670840.0156 | 1250111.5887 | 2670842.54 | 1250102.6317 | 2670845.191 | 1250098.1268 | 2670847.9455 | 1250095.0687 | 2670851.0464 | 1250090.1911 | 2670852.4298 | 1250087.1567
181 | 2670857.0957 | 1250054.3575 | 2670857.0664 | 1250055.2922
182 | 2670839.5744 | 1250113.1542 | 2670840.0156 | 1250111.5887
183 | 2670857.4356 | 1250035.7285 | 2670857.2971 | 1250047.9355 | 2670857.0957 | 1250054.3575
184 | 2670857.4356 | 1250035.7285 | 2670860.3758 | 1250035.7937
185 | 2670891.574 | 1250034.3937 | 2670887.9253 | 1250035.4483 | 2670881.2765 | 1250035.858 | 2670874.8108 | 1250036.1142 | 2670860.3758 | 1250035.7937
186 | 2670890.1823 | 1250154.2353 | 2670885.3975 | 1250163.4201
187 | 2670905.3031 | 1250123.4248 | 2670897.9233 | 1250139.3757 | 2670890.1823 | 1250154.2353
188 | 2670820.4903 | 1250023.8951 | 2670820.2657 | 1250023.2291
189 | 2670947.722 | 1249974.1418 | 2670948.7177 | 1249969.1724 | 2670955.2305 | 1249959.3211 | 2670957.9598 | 1249955.4372
190 | 2670947.722 | 1249974.1418 | 2670929.3765 | 1249979.7486 | 2670929.3765 | 1249979.7486
191 | 2670968.3295 | 1249940.6803 | 2670957.9598 | 1249955.4372
192 | 2670915.4215 | 1249985.384 | 2670915.8285 | 1249985.0792 | 2670929.3765 | 1249979.7486
193 | 2670906.74 | 1249991.8865 | 2670915.4215 | 1249985.384
194 | 2671026.8454 | 1249921.2402 | 2671015.9694 | 1249935.4312 | 2671013.6357 | 1249938.513
195 | 2671026.8454 | 1249921.2402 | 2671017.9792 | 1249913.8954 | 2671016.7813 | 1249912.6361
196 | 2670871.337 | 1249949.5162 | 2670848.7896 | 1249972.7133 | 2670846.0296 | 1249974.6798
197 | 2670871.337 | 1249949.5162 | 2670874.8251 | 1249945.9275 | 2670888.4314 | 1249935.0935 | 2670891.9846 | 1249932.2169
198 | 2670905.3488 | 1249921.3971 | 2670891.9846 | 1249932.2169
199 | 2670585.4294 | 1249829.1596 | 2670584.997 | 1249829.996
200 | 2670585.4294 | 1249829.1596 | 2670589.1773 | 1249821.9087 | 2670595.8722 | 1249810.0796
201 | 2670570.5492 | 1249854.3991 | 2670579.5978 | 1249840.786 | 2670582.871 | 1249834.109 | 2670584.997 | 1249829.996
202 | 2670599.875 | 1249805.1277 | 2670597.1597 | 1249807.8048 | 2670595.8722 | 1249810.0796
203 | 2670599.875 | 1249805.1277 | 2670607.0992 | 1249798.005 | 2670611.0591 | 1249794.7696
204 | 2671003.9293 | 1249898.7162 | 2671008.6814 | 1249904.1214 | 2671016.7813 | 1249912.6361
205 | 2671003.9293 | 1249898.7162 | 2670998.0298 | 1249903.3711 | 2670987.3223 | 1249917.3641

## bus_geodata
| x | y | coords
0 | 2670793.9084 | 1249876.4488
1 | 2670791.7971 | 1249878.5864
2 | 2670803.7224 | 1249866.0972
3 | 2670775.3265 | 1249895.4609
4 | 2670807.4617 | 1249861.9283
5 | 2670771.385 | 1249899.5092
6 | 2670813.6308 | 1249855.4587
7 | 2670754.0521 | 1249915.9318
8 | 2670825.9147 | 1249845.0152
9 | 2670751.1161 | 1249918.6373
10 | 2670813.6438 | 1249835.0726
11 | 2670846.9134 | 1249836.2294
12 | 2670857.6798 | 1249834.2499
13 | 2670865.9933 | 1249833.7528
14 | 2670894.511 | 1249833.36
15 | 2670822.1363 | 1249820.6291
16 | 2670895.3983 | 1249849.6228
17 | 2670773.1656 | 1249809.7212
18 | 2670770.7624 | 1249808.2156
19 | 2670822.8691 | 1249819.3829
20 | 2670896.0003 | 1249858.9721
21 | 2670770.7183 | 1249808.188
22 | 2670831.4389 | 1249804.808
23 | 2670895.1644 | 1249871.8543
24 | 2670885.2193 | 1249889.2837
25 | 2670880.3219 | 1249894.6735
26 | 2670870.4588 | 1249904.6515
27 | 2670860.9756 | 1249913.419
28 | 2670554.5561 | 1249651.2433
29 | 2670598.8715 | 1249686.961
30 | 2670497.0533 | 1249455.5397
31 | 2670619.4857 | 1249691.8655
32 | 2670445.2884 | 1249436.702
33 | 2670644.6566 | 1249697.0802
34 | 2670611.1265 | 1249710.773
35 | 2670647.1757 | 1249679.5755
36 | 2670670.857 | 1249709.5266
37 | 2670674.9755 | 1249713.7979
38 | 2670731.8005 | 1249931.7795
39 | 2670719.2681 | 1249938.1449
40 | 2670853.2752 | 1249919.7659
41 | 2670840.1573 | 1249928.9626
42 | 2670820.8194 | 1249941.1793
43 | 2670700.9621 | 1249945.934
44 | 2670684.9721 | 1249955.5346
45 | 2670807.7332 | 1249954.5476
46 | 2670804.1592 | 1249976.7275
47 | 2670809.4017 | 1249991.0225
48 | 2670776.5563 | 1249971.0716
49 | 2670810.5367 | 1249994.3873
50 | 2670823.2906 | 1249986.0274
51 | 2670766.3297 | 1249986.5718
52 | 2670813.7444 | 1250003.8966
53 | 2670836.2841 | 1249980.8769
54 | 2670846.1211 | 1249801.2586
55 | 2670672.2737 | 1249939.9579
56 | 2671078.2443 | 1250044.0919
57 | 2671079.6664 | 1250042.3413
58 | 2671072.2714 | 1250067.2523
59 | 2671080.3679 | 1250041.4778
60 | 2671068.3066 | 1250072.2849
61 | 2670992.874 | 1249965.8782
62 | 2671007.289 | 1249946.8944
63 | 2670973.5824 | 1249992.8981
64 | 2671061.2071 | 1250081.2963
65 | 2670960.8528 | 1249983.6899
66 | 2670945.9511 | 1250035.6536
67 | 2670931.1101 | 1250029.4261
68 | 2670928.5386 | 1250073.7682
69 | 2670928.931 | 1250028.5542
70 | 2670918.5028 | 1250095.0613
71 | 2670960.7154 | 1249983.59
72 | 2670900.5944 | 1250031.7705
73 | 2670908.9444 | 1250115.5544
74 | 2670794.589 | 1250103.4595
75 | 2670795.4485 | 1250101.0854
76 | 2670790.6127 | 1250130.7346
77 | 2670803.887 | 1250088.5821
78 | 2670788.3949 | 1250137.4013
79 | 2670814.415 | 1250072.6797
80 | 2670788.5471 | 1250079.3126
81 | 2670779.357 | 1250156.26
82 | 2670821.5406 | 1250057.12
83 | 2670778.6754 | 1250074.282
84 | 2670768.2781 | 1250169.3823
85 | 2670789.9113 | 1250163.6856
86 | 2670824.2636 | 1250036.188
87 | 2670754.3045 | 1250106.7877
88 | 2670764.6208 | 1250066.2283
89 | 2670768.1351 | 1250169.5833
90 | 2670704.4485 | 1249830.3118
91 | 2670705.4733 | 1249829.0866
92 | 2670681.9486 | 1249855.2045
93 | 2670714.6181 | 1249818.1536
94 | 2670691.9373 | 1249873.3172
95 | 2670666.8444 | 1249849.6595
96 | 2670719.5262 | 1249812.2859
97 | 2670701.7058 | 1249884.6401
98 | 2670642.2642 | 1249838.842
99 | 2670733.3172 | 1249795.3075
100 | 2670706.6371 | 1249890.0238
101 | 2670647.7572 | 1249827.5422
102 | 2670640.9135 | 1249872.8468
103 | 2670749.0401 | 1249794.606
104 | 2670654.4684 | 1249818.0035
105 | 2670641.4782 | 1249882.5973
106 | 2670770.015 | 1249807.7474
107 | 2670718.3073 | 1249764.1587
108 | 2670708.5175 | 1249740.6838
109 | 2670739.981 | 1249727.0908
110 | 2670692.3089 | 1249744.3375
111 | 2670660.662 | 1249928.4987
112 | 2670660.0141 | 1249924.3369
113 | 2670659.8162 | 1249953.5889
114 | 2670651.7114 | 1249910.9792
115 | 2670677.8333 | 1249981.19
116 | 2670643.1287 | 1249962.0904
117 | 2670637.2188 | 1249964.3829
118 | 2670637.7694 | 1249887.1786
119 | 2670634.5657 | 1249965.2741
120 | 2670644.0552 | 1249976.3181
121 | 2670632.4866 | 1249915.0696
122 | 2670717.2142 | 1249990.8308
123 | 2670723.4519 | 1250012.0228
124 | 2670618.7229 | 1249977.2656
125 | 2670630.62 | 1249945.9696
126 | 2670648.1006 | 1249983.3807
127 | 2670673.0874 | 1249791.8901
128 | 2670668.1333 | 1249798.7549
129 | 2670660.1803 | 1249810.1285
130 | 2670657.1916 | 1249784.1793
131 | 2670659.6959 | 1249810.7991
132 | 2670649.6883 | 1249774.0619
133 | 2670676.851 | 1249755.4793
134 | 2670670.7504 | 1249745.1923
135 | 2670687.3071 | 1249744.9089
136 | 2670639.482 | 1249764.4334
137 | 2670660.5226 | 1249747.8875
138 | 2670651.1026 | 1249751.9268
139 | 2670634.6822 | 1249769.8263
140 | 2670705.2601 | 1249710.59
141 | 2670741.4496 | 1249726.3125
142 | 2670672.6066 | 1250007.3242
143 | 2670605.6694 | 1249990.8371
144 | 2670629.9804 | 1249932.7417
145 | 2670609.6746 | 1250007.1485
146 | 2670625.6462 | 1249780.4014
147 | 2670752.518 | 1249718.1147
148 | 2670775.2033 | 1249721.9237
149 | 2670753.415 | 1249693.0605
150 | 2670788.6152 | 1249725.0136
151 | 2670792.2457 | 1249725.85
152 | 2670624.8619 | 1250035.1196
153 | 2670762.4175 | 1250064.9806
154 | 2670743.5534 | 1250053.7598
155 | 2670725.6296 | 1250025.2956
156 | 2670724.3819 | 1250017.6908
157 | 2670743.5616 | 1250116.9312
158 | 2670702.2935 | 1250063.0967
159 | 2670734.2162 | 1250127.1393
160 | 2670755.2068 | 1250187.4207
161 | 2670754.523 | 1250188.3528
162 | 2670710.0998 | 1250186.4573
163 | 2670716.619 | 1250172.0671
164 | 2670709.9676 | 1250186.7489
165 | 2670717.3287 | 1250151.6917
166 | 2670721.1314 | 1250145.6824
167 | 2670731.0615 | 1250130.9955
168 | 2670853.7055 | 1250084.2717
169 | 2670856.902 | 1250060.4168
170 | 2670852.4298 | 1250087.1567
171 | 2670857.0664 | 1250055.2922
172 | 2670840.0156 | 1250111.5887
173 | 2670857.0957 | 1250054.3575
174 | 2670839.5744 | 1250113.1542
175 | 2670857.4356 | 1250035.7285
176 | 2670860.3758 | 1250035.7937
177 | 2670890.1823 | 1250154.2353
178 | 2670885.3975 | 1250163.4201
179 | 2670905.3031 | 1250123.4248
180 | 2670820.4903 | 1250023.8951
181 | 2670891.574 | 1250034.3937
182 | 2670820.2657 | 1250023.2291
183 | 2670947.722 | 1249974.1418
184 | 2670957.9598 | 1249955.4372
185 | 2670929.3765 | 1249979.7486
186 | 2670968.3295 | 1249940.6803
187 | 2670915.4215 | 1249985.384
188 | 2671013.6357 | 1249938.513
189 | 2670906.74 | 1249991.8865
190 | 2671026.8454 | 1249921.2402
191 | 2670846.0296 | 1249974.6798
192 | 2670871.337 | 1249949.5162
193 | 2670891.9846 | 1249932.2169
194 | 2670905.3488 | 1249921.3971
195 | 2670648.632 | 1250036.7596
196 | 2670628.1093 | 1250038.8388
197 | 2670585.4294 | 1249829.1596
198 | 2670584.997 | 1249829.996
199 | 2670595.8722 | 1249810.0796
200 | 2670570.5492 | 1249854.3991
201 | 2670599.875 | 1249805.1277
202 | 2670611.0591 | 1249794.7696
203 | 2671016.7813 | 1249912.6361
204 | 2671003.9293 | 1249898.7162
205 | 2670987.3223 | 1249917.3641
206 | 2670814.151 | 1249730.1642
207 | 2670754.0521 | 1249915.9318

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1