## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4034-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4034-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4034-3_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4034-3_0_4_node_92 | 0.4 | n |  | TRUE
4 | bus_LV_4034-3_0_4_node_73 | 0.4 | n |  | TRUE
5 | bus_LV_4034-3_0_4_node_96 | 0.4 | n |  | TRUE
6 | bus_LV_4034-3_0_4_node_94 | 0.4 | n |  | TRUE
7 | bus_LV_4034-3_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4034-3_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_4034-3_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4034-3_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4034-3_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_4034-3_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_4034-3_0_4_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_4034-3_0_4_node_97 | 0.4 | n |  | TRUE
15 | bus_LV_4034-3_0_4_node_72 | 0.4 | n |  | TRUE
16 | bus_LV_4034-3_0_4_node_79 | 0.4 | n |  | TRUE
17 | bus_LV_4034-3_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_4034-3_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_4034-3_0_4_node_98 | 0.4 | n |  | TRUE
20 | bus_LV_4034-3_0_4_node_70 | 0.4 | n |  | TRUE
21 | bus_LV_4034-3_0_4_node_78 | 0.4 | n |  | TRUE
22 | bus_LV_4034-3_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_4034-3_0_4_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_4034-3_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_4034-3_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_4034-3_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_4034-3_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_4034-3_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_4034-3_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_4034-3_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_4034-3_0_4_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_4034-3_0_4_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_4034-3_0_4_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_4034-3_0_4_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_4034-3_0_4_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_4034-3_0_4_node_46 | 0.4 | n |  | TRUE
37 | bus_LV_4034-3_0_4_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_4034-3_0_4_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_4034-3_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_4034-3_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_4034-3_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_4034-3_0_4_node_40 | 0.4 | n |  | TRUE
43 | bus_LV_4034-3_0_4_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_4034-3_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_4034-3_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_4034-3_0_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_4034-3_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_4034-3_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_4034-3_0_4_node_62 | 0.4 | n |  | TRUE
50 | bus_LV_4034-3_0_4_node_63 | 0.4 | n |  | TRUE
51 | bus_LV_4034-3_0_4_node_64 | 0.4 | n |  | TRUE
52 | bus_LV_4034-3_0_4_node_65 | 0.4 | n |  | TRUE
53 | bus_LV_4034-3_0_4_node_41 | 0.4 | n |  | TRUE
54 | bus_LV_4034-3_0_4_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_4034-3_0_4_node_99 | 0.4 | n |  | TRUE
56 | bus_LV_4034-3_0_4_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_4034-3_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_4034-3_0_4_node_100 | 0.4 | n |  | TRUE
59 | bus_LV_4034-3_0_4_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_4034-3_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_4034-3_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_4034-3_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_4034-3_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_4034-3_0_4_node_50 | 0.4 | n |  | TRUE
65 | bus_LV_4034-3_0_4_node_88 | 0.4 | n |  | TRUE
66 | bus_LV_4034-3_0_4_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_4034-3_0_4_node_66 | 0.4 | n |  | TRUE
68 | bus_LV_4034-3_0_4_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_4034-3_0_4_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_4034-3_0_4_node_52 | 0.4 | n |  | TRUE
71 | bus_LV_4034-3_0_4_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_4034-3_0_4_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_4034-3_0_4_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_4034-3_0_4_node_76 | 0.4 | n |  | TRUE
75 | bus_LV_4034-3_0_4_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_4034-3_0_4_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_4034-3_0_4_node_71 | 0.4 | n |  | TRUE
78 | bus_LV_4034-3_0_4_node_56 | 0.4 | n |  | TRUE
79 | bus_LV_4034-3_0_4_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_4034-3_0_4_node_85 | 0.4 | n |  | TRUE
81 | bus_LV_4034-3_0_4_node_86 | 0.4 | n |  | TRUE
82 | bus_LV_4034-3_0_4_node_87 | 0.4 | n |  | TRUE
83 | bus_LV_4034-3_0_4_node_108 | 0.4 | n |  | TRUE
84 | bus_LV_4034-3_0_4_node_106 | 0.4 | n |  | TRUE
85 | bus_LV_4034-3_0_4_node_67 | 0.4 | n |  | TRUE
86 | bus_LV_4034-3_0_4_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_4034-3_0_4_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_4034-3_0_4_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_4034-3_0_4_node_89 | 0.4 | n |  | TRUE
90 | bus_LV_4034-3_0_4_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_4034-3_0_4_node_69 | 0.4 | n |  | TRUE
92 | bus_LV_4034-3_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_4034-3_0_4_node_107 | 0.4 | n |  | TRUE
94 | bus_LV_4034-3_0_4_node_105 | 0.4 | n |  | TRUE
95 | bus_LV_4034-3_0_4_node_90 | 0.4 | n |  | TRUE
96 | bus_LV_4034-3_0_4_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_4034-3_0_4_node_95 | 0.4 | n |  | TRUE
98 | bus_LV_4034-3_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_4034-3_0_4_node_101 | 0.4 | n |  | TRUE
100 | bus_LV_4034-3_0_4_node_91 | 0.4 | n |  | TRUE
101 | bus_LV_4034-3_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_4034-3_0_4_node_103 | 0.4 | n |  | TRUE
103 | bus_LV_4034-3_0_4_node_104 | 0.4 | n |  | TRUE
104 | bus_MV_615_0_node_23 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4034-3_0_4_load_0 | 0 | 0.0028306 | 0.00070941 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4034-3_0_4_load_3 | 2 | 0.00038644 | 9.685e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4034-3_0_4_load_92 | 3 | 0.00046739 | 0.00011714 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4034-3_0_4_load_73 | 4 | 0.00045792 | 0.00011477 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4034-3_0_4_load_96 | 5 | 0.003394 | 0.00085061 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4034-3_0_4_load_5 | 7 | 0.0034225 | 0.00085776 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4034-3_0_4_load_6 | 8 | 0.0029445 | 0.00073796 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4034-3_0_4_load_7 | 9 | 0.0028686 | 0.00071894 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4034-3_0_4_load_14 | 12 | 0.0024725 | 0.00061967 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4034-3_0_4_load_13 | 13 | 0.0057649 | 0.0014448 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4034-3_0_4_load_97 | 14 | 0.0023328 | 0.00058465 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4034-3_0_4_load_72 | 15 | 0.001184 | 0.00029675 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4034-3_0_4_load_79 | 16 | 0.0025392 | 0.00063639 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4034-3_0_4_load_15 | 17 | 0.0021026 | 0.00052695 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4034-3_0_4_load_11 | 18 | 0.0017428 | 0.00043678 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4034-3_0_4_load_98 | 19 | 0.0027416 | 0.00068711 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4034-3_0_4_load_70 | 20 | 0.0020147 | 0.00050492 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4034-3_0_4_load_78 | 21 | 0.0014372 | 0.00036021 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4034-3_0_4_load_10 | 22 | 0.0035428 | 0.0008879 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4034-3_0_4_load_16 | 23 | 0.0018054 | 0.00045247 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4034-3_0_4_load_18 | 25 | 0.006087 | 0.0015255 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4034-3_0_4_load_26 | 26 | 0.0034808 | 0.00087238 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4034-3_0_4_load_27 | 27 | 0.0095232 | 0.0023867 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4034-3_0_4_load_19 | 28 | 0.0018838 | 0.00047213 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4034-3_0_4_load_20 | 29 | 0.0021895 | 0.00054873 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4034-3_0_4_load_21 | 30 | 0.0019077 | 0.00047811 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4034-3_0_4_load_22 | 31 | 0.001869 | 0.00046843 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4034-3_0_4_load_23 | 32 | 0.001862 | 0.00046666 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4034-3_0_4_load_38 | 33 | 0.0018848 | 0.00047237 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4034-3_0_4_load_24 | 34 | 0.0022277 | 0.00055831 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4034-3_0_4_load_39 | 35 | 0.0020142 | 0.0005048 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4034-3_0_4_load_28 | 38 | 0.0051672 | 0.001295 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4034-3_0_4_load_29 | 39 | 0.013502 | 0.0033839 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4034-3_0_4_load_31 | 41 | 0.010424 | 0.0026124 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4034-3_0_4_load_42 | 43 | 0.0063817 | 0.0015994 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4034-3_0_4_load_32 | 44 | 0.0019626 | 0.00049188 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4034-3_0_4_load_33 | 45 | 0.001978 | 0.00049573 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4034-3_0_4_load_34 | 46 | 0.0018057 | 0.00045254 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4034-3_0_4_load_37 | 48 | 0.0020939 | 0.00052479 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4034-3_0_4_load_62 | 49 | 0.0028485 | 0.00071389 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4034-3_0_4_load_64 | 51 | 0.0022304 | 0.000559 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4034-3_0_4_load_65 | 52 | 0.0020676 | 0.00051819 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4034-3_0_4_load_43 | 54 | 0.0033638 | 0.00084304 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4034-3_0_4_load_99 | 55 | 0.0063239 | 0.0015849 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4034-3_0_4_load_59 | 56 | 0.0038149 | 0.00095611 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4034-3_0_4_load_44 | 57 | 0.010308 | 0.0025835 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4034-3_0_4_load_100 | 58 | 0.0058866 | 0.0014753 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4034-3_0_4_load_57 | 59 | 0.0036822 | 0.00092284 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4034-3_0_4_load_47 | 60 | 0.0081725 | 0.0020482 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4034-3_0_4_load_49 | 61 | 0.0015965 | 0.00040011 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4034-3_0_4_load_48 | 62 | 0.0024007 | 0.00060168 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4034-3_0_4_load_50 | 64 | 0.0035955 | 0.00090113 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4034-3_0_4_load_88 | 65 | 0.0022194 | 0.00055623 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4034-3_0_4_load_68 | 68 | 0.005539 | 0.0013882 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4034-3_0_4_load_51 | 69 | 0.0022036 | 0.00055227 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4034-3_0_4_load_52 | 70 | 0.0021476 | 0.00053825 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4034-3_0_4_load_53 | 71 | 0.0020693 | 0.00051863 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4034-3_0_4_load_54 | 72 | 0.0021085 | 0.00052845 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4034-3_0_4_load_55 | 73 | 0.0024015 | 0.00060188 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4034-3_0_4_load_76 | 74 | 0.0021086 | 0.00052847 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4034-3_0_4_load_74 | 75 | 0.002026 | 0.00050776 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4034-3_0_4_load_77 | 76 | 0.0020765 | 0.00052042 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4034-3_0_4_load_56 | 78 | 0.0041545 | 0.0010412 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4034-3_0_4_load_60 | 79 | 0.003698 | 0.00092682 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4034-3_0_4_load_87 | 82 | 0.025345 | 0.0063522 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4034-3_0_4_load_108 | 83 | 0.0022478 | 0.00056336 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4034-3_0_4_load_106 | 84 | 0.001974 | 0.00049473 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4034-3_0_4_load_67 | 85 | 0.0053053 | 0.0013296 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4034-3_0_4_load_82 | 86 | 0.0064024 | 0.0016046 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4034-3_0_4_load_83 | 88 | 0.005596 | 0.0014025 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4034-3_0_4_load_89 | 89 | 0.0023851 | 0.00059777 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4034-3_0_4_load_69 | 91 | 0.00075558 | 0.00018937 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4034-3_0_4_load_107 | 93 | 0.00055038 | 0.00013794 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4034-3_0_4_load_90 | 95 | 0.002723 | 0.00068244 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4034-3_0_4_load_95 | 97 | 0.0024478 | 0.00061347 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4034-3_0_4_load_93 | 98 | 0.0038624 | 0.00096801 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4034-3_0_4_load_91 | 100 | 0.0037585 | 0.00094197 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4034-3_0_4_load_102 | 101 | 0.0022428 | 0.0005621 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4034-3_0_4_load_103 | 102 | 0.0025894 | 0.00064897 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4034-3_0_4_load_104 | 103 | 0.0022233 | 0.00055722 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4034-3_0_4_line_0 |  | 0 | 1 | 0.034134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4034-3_0_4_line_1 |  | 1 | 2 | 0.0084431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4034-3_0_4_line_2 |  | 2 | 3 | 0.029727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4034-3_0_4_line_3 |  | 3 | 4 | 0.031663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4034-3_0_4_line_4 |  | 4 | 77 | 0.030512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4034-3_0_4_line_5 |  | 5 | 6 | 0.014356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4034-3_0_4_line_6 |  | 6 | 97 | 0.036588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4034-3_0_4_line_7 |  | 6 | 98 | 0.018148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4034-3_0_4_line_8 |  | 7 | 8 | 0.00087694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_4034-3_0_4_line_9 |  | 7 | 9 | 0.01405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_4034-3_0_4_line_10 |  | 8 | 10 | 0.015162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_4034-3_0_4_line_11 |  | 9 | 11 | 0.027526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_4034-3_0_4_line_12 |  | 10 | 12 | 0.011774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_4034-3_0_4_line_13 |  | 10 | 13 | 0.028556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4034-3_0_4_line_14 |  | 11 | 14 | 0.012614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4034-3_0_4_line_15 |  | 11 | 15 | 0.01131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4034-3_0_4_line_16 |  | 11 | 16 | 0.018013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4034-3_0_4_line_17 |  | 12 | 17 | 0.0045744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_4034-3_0_4_line_18 |  | 13 | 18 | 0.0089433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4034-3_0_4_line_19 |  | 14 | 19 | 0.0095314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4034-3_0_4_line_20 |  | 15 | 20 | 0.012641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4034-3_0_4_line_21 |  | 16 | 21 | 0.0042691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_4034-3_0_4_line_22 |  | 17 | 23 | 0.017924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_4034-3_0_4_line_23 |  | 18 | 22 | 0.0080991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4034-3_0_4_line_24 |  | 20 | 91 | 0.017479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4034-3_0_4_line_25 |  | 21 | 90 | 0.0051891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_4034-3_0_4_line_26 |  | 23 | 24 | 0.020502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_4034-3_0_4_line_27 |  | 24 | 25 | 0.021756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_4034-3_0_4_line_28 |  | 25 | 26 | 0.019903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_4034-3_0_4_line_29 |  | 26 | 27 | 0.019386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_4034-3_0_4_line_30 |  | 27 | 36 | 0.019049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_4034-3_0_4_line_31 |  | 28 | 29 | 0.013143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4034-3_0_4_line_32 |  | 28 | 30 | 0.0099414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4034-3_0_4_line_33 |  | 29 | 31 | 0.0053685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4034-3_0_4_line_34 |  | 30 | 32 | 0.0085036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4034-3_0_4_line_35 |  | 31 | 33 | 0.014882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4034-3_0_4_line_36 |  | 32 | 34 | 0.0057737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4034-3_0_4_line_37 |  | 33 | 35 | 0.012782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4034-3_0_4_line_38 |  | 35 | 51 | 0.0053939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4034-3_0_4_line_39 |  | 36 | 37 | 0.02394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_4034-3_0_4_line_40 |  | 37 | 56 | 0.012681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4034-3_0_4_line_41 |  | 37 | 53 | 0.002213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4034-3_0_4_line_42 |  | 38 | 39 | 0.0098301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4034-3_0_4_line_43 |  | 38 | 40 | 0.017103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4034-3_0_4_line_44 |  | 40 | 41 | 0.042662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4034-3_0_4_line_45 |  | 41 | 42 | 0.019285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4034-3_0_4_line_46 |  | 42 | 43 | 0.019762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4034-3_0_4_line_47 |  | 43 | 55 | 0.037317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4034-3_0_4_line_48 |  | 44 | 45 | 0.01322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4034-3_0_4_line_49 |  | 44 | 46 | 0.0059817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4034-3_0_4_line_50 |  | 46 | 47 | 0.017789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4034-3_0_4_line_51 |  | 47 | 48 | 0.0084286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4034-3_0_4_line_52 |  | 48 | 49 | 0.0085042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4034-3_0_4_line_53 |  | 49 | 50 | 0.0035598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4034-3_0_4_line_54 |  | 50 | 76 | 0.019209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4034-3_0_4_line_55 |  | 51 | 52 | 0.021842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4034-3_0_4_line_56 |  | 52 | 83 | 0.0010299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4034-3_0_4_line_57 |  | 53 | 54 | 0.0137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4034-3_0_4_line_58 |  | 54 | 57 | 0.015517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4034-3_0_4_line_59 |  | 55 | 58 | 0.038592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4034-3_0_4_line_60 |  | 56 | 59 | 0.021633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_4034-3_0_4_line_61 |  | 58 | 99 | 0.042982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4034-3_0_4_line_62 |  | 59 | 78 | 0.01974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_4034-3_0_4_line_63 |  | 60 | 61 | 0.010464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4034-3_0_4_line_64 |  | 61 | 64 | 0.023509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4034-3_0_4_line_65 |  | 62 | 63 | 0.0026442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4034-3_0_4_line_66 |  | 63 | 65 | 0.024868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_4034-3_0_4_line_67 |  | 63 | 66 | 0.023007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_4034-3_0_4_line_68 |  | 64 | 67 | 0.002466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_4034-3_0_4_line_69 |  | 65 | 81 | 0.018464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_4034-3_0_4_line_70 |  | 66 | 79 | 0.014978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4034-3_0_4_line_71 |  | 66 | 78 | 0.026945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_4034-3_0_4_line_72 |  | 67 | 68 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_4034-3_0_4_line_73 |  | 68 | 87 | 0.020893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_4034-3_0_4_line_74 |  | 69 | 70 | 0.0063019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4034-3_0_4_line_75 |  | 69 | 71 | 0.015594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4034-3_0_4_line_76 |  | 70 | 72 | 0.0085206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4034-3_0_4_line_77 |  | 71 | 73 | 0.0079899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4034-3_0_4_line_78 |  | 72 | 74 | 0.01551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4034-3_0_4_line_79 |  | 73 | 75 | 0.01113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4034-3_0_4_line_80 |  | 74 | 76 | 0.0039718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4034-3_0_4_line_81 |  | 75 | 77 | 0.015112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4034-3_0_4_line_82 |  | 77 | 92 | 0.040971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4034-3_0_4_line_83 |  | 77 | 91 | 0.012899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4034-3_0_4_line_84 |  | 80 | 81 | 0.023669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_4034-3_0_4_line_85 |  | 80 | 82 | 0.032289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_4034-3_0_4_line_86 |  | 81 | 96 | 0.028127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4034-3_0_4_line_87 |  | 82 | 99 | 0.019658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_4034-3_0_4_line_88 |  | 83 | 84 | 0.018442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4034-3_0_4_line_89 |  | 84 | 103 | 0.0015145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4034-3_0_4_line_90 |  | 85 | 86 | 0.012548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4034-3_0_4_line_91 |  | 86 | 88 | 0.023496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4034-3_0_4_line_92 |  | 87 | 89 | 0.013321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4034-3_0_4_line_93 |  | 87 | 90 | 0.010266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_4034-3_0_4_line_94 |  | 88 | 96 | 0.014682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4034-3_0_4_line_95 |  | 89 | 95 | 0.023393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4034-3_0_4_line_96 |  | 92 | 93 | 0.025158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4034-3_0_4_line_97 |  | 93 | 94 | 0.0073028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4034-3_0_4_line_98 |  | 94 | 102 | 0.025727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4034-3_0_4_line_99 |  | 95 | 100 | 0.023951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4034-3_0_4_line_100 |  | 98 | 100 | 0.02736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4034-3_0_4_line_101 |  | 101 | 102 | 0.010339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4034-3_0_4_line_102 |  | 101 | 103 | 0.0079199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4034-3_0_4_trafo_50 | 0.63 MVA 20/0.4 kV | 104 | 64 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2666296.2086 | 1256064.001 | 2666288.423 | 1256043.3211 | 2666299.7003 | 1256039.111
1 | 2666296.2086 | 1256064.001 | 2666304.6051 | 1256064.8869
2 | 2666334.1685 | 1256068.006 | 2666304.6051 | 1256064.8869
3 | 2666334.1685 | 1256068.006 | 2666351.8634 | 1256069.8729 | 2666365.7081 | 1256069.0371
4 | 2666395.8977 | 1256064.8183 | 2666372.9878 | 1256068.5976 | 2666365.7081 | 1256069.0371
5 | 2666286.8247 | 1256116.6676 | 2666285.0158 | 1256102.4259
6 | 2666286.8247 | 1256116.6676 | 2666250.1285 | 1256116.4012
7 | 2666286.8247 | 1256116.6676 | 2666304.9697 | 1256116.3635
8 | 2666451.4416 | 1256143.7664 | 2666450.9974 | 1256143.0103
9 | 2666450.9974 | 1256143.0103 | 2666443.8794 | 1256130.8964
10 | 2666459.1226 | 1256156.8386 | 2666451.4416 | 1256143.7664
11 | 2666429.9348 | 1256107.164 | 2666443.8794 | 1256130.8964
12 | 2666459.1226 | 1256156.8386 | 2666463.0512 | 1256167.9378
13 | 2666459.1226 | 1256156.8386 | 2666486.2759 | 1256147.998
14 | 2666429.9348 | 1256107.164 | 2666440.4881 | 1256100.2551
15 | 2666429.9348 | 1256107.164 | 2666422.8491 | 1256098.3486
16 | 2666429.9348 | 1256107.164 | 2666412.3734 | 1256111.1738
17 | 2666464.5775 | 1256172.2501 | 2666463.0512 | 1256167.9378
18 | 2666494.7798 | 1256145.2293 | 2666486.2759 | 1256147.998
19 | 2666440.4881 | 1256100.2551 | 2666440.4881 | 1256100.2551 | 2666449.9181 | 1256098.8687
20 | 2666422.8491 | 1256098.3486 | 2666414.9293 | 1256088.4956
21 | 2666408.2114 | 1256112.1241 | 2666412.3734 | 1256111.1738
22 | 2666464.5775 | 1256172.2501 | 2666470.558 | 1256189.1466
23 | 2666494.7798 | 1256145.2293 | 2666502.481 | 1256142.7219
24 | 2666403.979 | 1256074.8724 | 2666414.9293 | 1256088.4956
25 | 2666403.1524 | 1256113.2792 | 2666408.2114 | 1256112.1241
26 | 2666476.7086 | 1256208.6958 | 2666473.1577 | 1256196.4915 | 2666470.558 | 1256189.1466
27 | 2666476.7086 | 1256208.6958 | 2666462.474 | 1256211.6604 | 2666455.2938 | 1256212.3812
28 | 2666435.4521 | 1256213.8043 | 2666444.0436 | 1256213.5105 | 2666455.2938 | 1256212.3812
29 | 2666435.4521 | 1256213.8043 | 2666416.0775 | 1256214.4669
30 | 2666397.0398 | 1256215.1179 | 2666416.0775 | 1256214.4669
31 | 2666520.0029 | 1256028.9283 | 2666506.8849 | 1256028.1133
32 | 2666520.0029 | 1256028.9283 | 2666529.9253 | 1256029.5448
33 | 2666501.5268 | 1256027.7804 | 2666506.8849 | 1256028.1133
34 | 2666538.4125 | 1256030.0721 | 2666529.9253 | 1256029.5448
35 | 2666501.5268 | 1256027.7804 | 2666495.7671 | 1256027.4226 | 2666486.7252 | 1256026.2989
36 | 2666538.4125 | 1256030.0721 | 2666541.6513 | 1256030.2733 | 2666544.1561 | 1256030.6201
37 | 2666474.041 | 1256024.7226 | 2666486.7252 | 1256026.2989
38 | 2666474.041 | 1256024.7226 | 2666468.6883 | 1256024.0574
39 | 2666397.0398 | 1256215.1179 | 2666396.7562 | 1256239.0543
40 | 2666396.7562 | 1256239.0543 | 2666384.0784 | 1256239.3427
41 | 2666396.7314 | 1256241.2668 | 2666396.7562 | 1256239.0543
42 | 2666455.8942 | 1256253.0389 | 2666456.8905 | 1256262.8184
43 | 2666458.6239 | 1256279.8334 | 2666456.8905 | 1256262.8184
44 | 2666458.6239 | 1256279.8334 | 2666442.819 | 1256281.6129 | 2666416.1819 | 1256284.1508
45 | 2666396.984 | 1256285.9798 | 2666416.1819 | 1256284.1508
46 | 2666396.984 | 1256285.9798 | 2666381.075 | 1256286.2795 | 2666377.2318 | 1256286.054
47 | 2666340.3322 | 1256281.3862 | 2666348.6368 | 1256283.692 | 2666365.1422 | 1256285.3447 | 2666377.2318 | 1256286.054
48 | 2666509.4479 | 1256086.557 | 2666522.5712 | 1256084.9619
49 | 2666509.4479 | 1256086.557 | 2666503.5099 | 1256087.2788
50 | 2666490.0712 | 1256096.72 | 2666496.503 | 1256088.1305 | 2666503.5099 | 1256087.2788
51 | 2666490.0712 | 1256096.72 | 2666481.686 | 1256095.866
52 | 2666481.686 | 1256095.866 | 2666478.5376 | 1256095.5453 | 2666473.2041 | 1256095.7989
53 | 2666469.6484 | 1256095.9681 | 2666473.2041 | 1256095.7989
54 | 2666469.6484 | 1256095.9681 | 2666464.0996 | 1256077.5778
55 | 2666468.6883 | 1256024.0574 | 2666462.9144 | 1256023.3398 | 2666448.0503 | 1256017.3565
56 | 2666448.0503 | 1256017.3565 | 2666447.0949 | 1256016.9719
57 | 2666396.7314 | 1256241.2668 | 2666410.4138 | 1256240.5662
58 | 2666410.4138 | 1256240.5662 | 2666425.9108 | 1256239.7726
59 | 2666340.3322 | 1256281.3862 | 2666332.1941 | 1256279.1267 | 2666312.4607 | 1256271.4224 | 2666304.442 | 1256267.4198
60 | 2666384.0784 | 1256239.3427 | 2666367.2904 | 1256239.7246 | 2666367.141 | 1256234.8861 | 2666367.141 | 1256234.8861
61 | 2666267.2152 | 1256246.042 | 2666278.7287 | 1256253.6986 | 2666292.2711 | 1256261.3446 | 2666304.442 | 1256267.4198
62 | 2666349.4615 | 1256233.354 | 2666354.2091 | 1256233.3289 | 2666354.3879 | 1256235.5437 | 2666367.141 | 1256234.8861
63 | 2666395.6935 | 1256186.7678 | 2666395.1972 | 1256176.3158
64 | 2666394.082 | 1256152.833 | 2666395.1972 | 1256176.3158
65 | 2666334.292 | 1256195.5673 | 2666336.6911 | 1256196.6792
66 | 2666334.292 | 1256195.5673 | 2666311.7293 | 1256185.111
67 | 2666334.292 | 1256195.5673 | 2666334.2529 | 1256218.5725
68 | 2666393.965 | 1256150.3698 | 2666394.082 | 1256152.833
69 | 2666294.9767 | 1256177.3473 | 2666311.7293 | 1256185.111
70 | 2666334.2529 | 1256218.5725 | 2666319.2754 | 1256218.4122
71 | 2666334.2529 | 1256218.5725 | 2666334.2311 | 1256229.2689 | 2666342.0736 | 1256233.393 | 2666349.4615 | 1256233.354
72 | 2666393.965 | 1256150.3698 | 2666393.561 | 1256135.7732
73 | 2666392.9829 | 1256114.8886 | 2666393.561 | 1256135.7732
74 | 2666444.3388 | 1256056.1068 | 2666450.6301 | 1256055.7407
75 | 2666444.3388 | 1256056.1068 | 2666428.7709 | 1256057.0126
76 | 2666458.4722 | 1256058.9269 | 2666458.4722 | 1256058.9269 | 2666451.1699 | 1256055.7093 | 2666450.6301 | 1256055.7407
77 | 2666420.7944 | 1256057.4767 | 2666428.7709 | 1256057.0126
78 | 2666458.4722 | 1256058.9269 | 2666462.9523 | 1256073.7753
79 | 2666420.7944 | 1256057.4767 | 2666413.0426 | 1256057.9277 | 2666409.9198 | 1256059.1828
80 | 2666462.9523 | 1256073.7753 | 2666464.0996 | 1256077.5778
81 | 2666395.8977 | 1256064.8183 | 2666409.9198 | 1256059.1828
82 | 2666365.7857 | 1256036.9384 | 2666395.8977 | 1256064.8183
83 | 2666395.8977 | 1256064.8183 | 2666403.979 | 1256074.8724
84 | 2666294.9767 | 1256177.3473 | 2666292.836 | 1256181.96 | 2666290.352 | 1256200.3789
85 | 2666290.352 | 1256200.3789 | 2666288.9048 | 1256211.0816 | 2666283.9228 | 1256219.5542 | 2666277.6535 | 1256229.3853
86 | 2666294.9767 | 1256177.3473 | 2666293.1436 | 1256151.7971 | 2666294.3748 | 1256149.6093
87 | 2666267.2152 | 1256246.042 | 2666270.8418 | 1256240.0671 | 2666277.6535 | 1256229.3853
88 | 2666429.9872 | 1256010.0855 | 2666447.0949 | 1256016.9719
89 | 2666428.5822 | 1256009.52 | 2666429.9872 | 1256010.0855
90 | 2666332.5522 | 1256149.9008 | 2666345.1002 | 1256149.9966
91 | 2666332.5522 | 1256149.9008 | 2666309.0564 | 1256149.7214
92 | 2666392.9829 | 1256114.8886 | 2666379.6634 | 1256115.1118
93 | 2666403.1524 | 1256113.2792 | 2666392.9829 | 1256114.8886
94 | 2666294.3748 | 1256149.6093 | 2666309.0564 | 1256149.7214
95 | 2666379.6634 | 1256115.1118 | 2666356.2735 | 1256115.5038
96 | 2666365.7857 | 1256036.9384 | 2666383.8454 | 1256019.4229
97 | 2666389.0877 | 1256014.3387 | 2666383.8454 | 1256019.4229
98 | 2666389.0877 | 1256014.3387 | 2666396.8845 | 1256007.0986 | 2666408.3768 | 1256003.2357 | 2666411.2615 | 1256003.9122
99 | 2666332.3261 | 1256115.9051 | 2666356.2735 | 1256115.5038
100 | 2666304.9697 | 1256116.3635 | 2666332.3261 | 1256115.9051
101 | 2666421.2352 | 1256006.5626 | 2666419.382 | 1256005.8165 | 2666411.2615 | 1256003.9122
102 | 2666421.2352 | 1256006.5626 | 2666428.5822 | 1256009.52

## bus_geodata
| x | y | coords
0 | 2666299.7003 | 1256039.111
1 | 2666296.2086 | 1256064.001
2 | 2666304.6051 | 1256064.8869
3 | 2666334.1685 | 1256068.006
4 | 2666365.7081 | 1256069.0371
5 | 2666285.0158 | 1256102.4259
6 | 2666286.8247 | 1256116.6676
7 | 2666450.9974 | 1256143.0103
8 | 2666451.4416 | 1256143.7664
9 | 2666443.8794 | 1256130.8964
10 | 2666459.1226 | 1256156.8386
11 | 2666429.9348 | 1256107.164
12 | 2666463.0512 | 1256167.9378
13 | 2666486.2759 | 1256147.998
14 | 2666440.4881 | 1256100.2551
15 | 2666422.8491 | 1256098.3486
16 | 2666412.3734 | 1256111.1738
17 | 2666464.5775 | 1256172.2501
18 | 2666494.7798 | 1256145.2293
19 | 2666449.9181 | 1256098.8687
20 | 2666414.9293 | 1256088.4956
21 | 2666408.2114 | 1256112.1241
22 | 2666502.481 | 1256142.7219
23 | 2666470.558 | 1256189.1466
24 | 2666476.7086 | 1256208.6958
25 | 2666455.2938 | 1256212.3812
26 | 2666435.4521 | 1256213.8043
27 | 2666416.0775 | 1256214.4669
28 | 2666520.0029 | 1256028.9283
29 | 2666506.8849 | 1256028.1133
30 | 2666529.9253 | 1256029.5448
31 | 2666501.5268 | 1256027.7804
32 | 2666538.4125 | 1256030.0721
33 | 2666486.7252 | 1256026.2989
34 | 2666544.1561 | 1256030.6201
35 | 2666474.041 | 1256024.7226
36 | 2666397.0398 | 1256215.1179
37 | 2666396.7562 | 1256239.0543
38 | 2666456.8905 | 1256262.8184
39 | 2666455.8942 | 1256253.0389
40 | 2666458.6239 | 1256279.8334
41 | 2666416.1819 | 1256284.1508
42 | 2666396.984 | 1256285.9798
43 | 2666377.2318 | 1256286.054
44 | 2666509.4479 | 1256086.557
45 | 2666522.5712 | 1256084.9619
46 | 2666503.5099 | 1256087.2788
47 | 2666490.0712 | 1256096.72
48 | 2666481.686 | 1256095.866
49 | 2666473.2041 | 1256095.7989
50 | 2666469.6484 | 1256095.9681
51 | 2666468.6883 | 1256024.0574
52 | 2666448.0503 | 1256017.3565
53 | 2666396.7314 | 1256241.2668
54 | 2666410.4138 | 1256240.5662
55 | 2666340.3322 | 1256281.3862
56 | 2666384.0784 | 1256239.3427
57 | 2666425.9108 | 1256239.7726
58 | 2666304.442 | 1256267.4198
59 | 2666367.141 | 1256234.8861
60 | 2666395.6935 | 1256186.7678
61 | 2666395.1972 | 1256176.3158
62 | 2666336.6911 | 1256196.6792
63 | 2666334.292 | 1256195.5673
64 | 2666394.082 | 1256152.833
65 | 2666311.7293 | 1256185.111
66 | 2666334.2529 | 1256218.5725
67 | 2666393.965 | 1256150.3698
68 | 2666393.561 | 1256135.7732
69 | 2666444.3388 | 1256056.1068
70 | 2666450.6301 | 1256055.7407
71 | 2666428.7709 | 1256057.0126
72 | 2666458.4722 | 1256058.9269
73 | 2666420.7944 | 1256057.4767
74 | 2666462.9523 | 1256073.7753
75 | 2666409.9198 | 1256059.1828
76 | 2666464.0996 | 1256077.5778
77 | 2666395.8977 | 1256064.8183
78 | 2666349.4615 | 1256233.354
79 | 2666319.2754 | 1256218.4122
80 | 2666290.352 | 1256200.3789
81 | 2666294.9767 | 1256177.3473
82 | 2666277.6535 | 1256229.3853
83 | 2666447.0949 | 1256016.9719
84 | 2666429.9872 | 1256010.0855
85 | 2666345.1002 | 1256149.9966
86 | 2666332.5522 | 1256149.9008
87 | 2666392.9829 | 1256114.8886
88 | 2666309.0564 | 1256149.7214
89 | 2666379.6634 | 1256115.1118
90 | 2666403.1524 | 1256113.2792
91 | 2666403.979 | 1256074.8724
92 | 2666365.7857 | 1256036.9384
93 | 2666383.8454 | 1256019.4229
94 | 2666389.0877 | 1256014.3387
95 | 2666356.2735 | 1256115.5038
96 | 2666294.3748 | 1256149.6093
97 | 2666250.1285 | 1256116.4012
98 | 2666304.9697 | 1256116.3635
99 | 2666267.2152 | 1256246.042
100 | 2666332.3261 | 1256115.9051
101 | 2666421.2352 | 1256006.5626
102 | 2666411.2615 | 1256003.9122
103 | 2666428.5822 | 1256009.52
104 | 2666393.965 | 1256150.3698

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1