## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_404-22_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_404-22_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_404-22_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_404-22_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_404-22_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_404-22_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_404-22_0_4_node_51 | 0.4 | n |  | TRUE
7 | bus_LV_404-22_0_4_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_404-22_0_4_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_404-22_0_4_node_69 | 0.4 | n |  | TRUE
10 | bus_LV_404-22_0_4_node_71 | 0.4 | n |  | TRUE
11 | bus_LV_404-22_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_404-22_0_4_node_53 | 0.4 | n |  | TRUE
13 | bus_LV_404-22_0_4_node_57 | 0.4 | n |  | TRUE
14 | bus_LV_404-22_0_4_node_95 | 0.4 | n |  | TRUE
15 | bus_LV_404-22_0_4_node_96 | 0.4 | n |  | TRUE
16 | bus_LV_404-22_0_4_node_93 | 0.4 | n |  | TRUE
17 | bus_LV_404-22_0_4_node_75 | 0.4 | n |  | TRUE
18 | bus_LV_404-22_0_4_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_404-22_0_4_node_100 | 0.4 | n |  | TRUE
20 | bus_LV_404-22_0_4_node_99 | 0.4 | n |  | TRUE
21 | bus_LV_404-22_0_4_node_6 | 0.4 | n |  | TRUE
22 | bus_LV_404-22_0_4_node_7 | 0.4 | n |  | TRUE
23 | bus_LV_404-22_0_4_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_404-22_0_4_node_10 | 0.4 | n |  | TRUE
25 | bus_LV_404-22_0_4_node_12 | 0.4 | n |  | TRUE
26 | bus_LV_404-22_0_4_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_404-22_0_4_node_88 | 0.4 | n |  | TRUE
28 | bus_LV_404-22_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_404-22_0_4_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_404-22_0_4_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_404-22_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_404-22_0_4_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_404-22_0_4_node_89 | 0.4 | n |  | TRUE
34 | bus_LV_404-22_0_4_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_404-22_0_4_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_404-22_0_4_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_404-22_0_4_node_59 | 0.4 | n |  | TRUE
38 | bus_LV_404-22_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_404-22_0_4_node_42 | 0.4 | n |  | TRUE
40 | bus_LV_404-22_0_4_node_18 | 0.4 | n |  | TRUE
41 | bus_LV_404-22_0_4_node_19 | 0.4 | n |  | TRUE
42 | bus_LV_404-22_0_4_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_404-22_0_4_node_21 | 0.4 | n |  | TRUE
44 | bus_LV_404-22_0_4_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_404-22_0_4_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_404-22_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_404-22_0_4_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_404-22_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_404-22_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_404-22_0_4_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_404-22_0_4_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_404-22_0_4_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_404-22_0_4_node_32 | 0.4 | n |  | TRUE
54 | bus_LV_404-22_0_4_node_102 | 0.4 | n |  | TRUE
55 | bus_LV_404-22_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_404-22_0_4_node_34 | 0.4 | n |  | TRUE
57 | bus_LV_404-22_0_4_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_404-22_0_4_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_404-22_0_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_404-22_0_4_node_61 | 0.4 | n |  | TRUE
61 | bus_LV_404-22_0_4_node_83 | 0.4 | n |  | TRUE
62 | bus_LV_404-22_0_4_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_404-22_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_404-22_0_4_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_404-22_0_4_node_67 | 0.4 | n |  | TRUE
66 | bus_LV_404-22_0_4_node_46 | 0.4 | n |  | TRUE
67 | bus_LV_404-22_0_4_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_404-22_0_4_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_404-22_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_404-22_0_4_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_404-22_0_4_node_77 | 0.4 | n |  | TRUE
72 | bus_LV_404-22_0_4_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_404-22_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_404-22_0_4_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_404-22_0_4_node_64 | 0.4 | n |  | TRUE
76 | bus_LV_404-22_0_4_node_92 | 0.4 | n |  | TRUE
77 | bus_LV_404-22_0_4_node_94 | 0.4 | n |  | TRUE
78 | bus_LV_404-22_0_4_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_404-22_0_4_node_101 | 0.4 | n |  | TRUE
80 | bus_LV_404-22_0_4_node_85 | 0.4 | n |  | TRUE
81 | bus_LV_404-22_0_4_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_404-22_0_4_node_68 | 0.4 | n |  | TRUE
83 | bus_LV_404-22_0_4_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_404-22_0_4_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_404-22_0_4_node_72 | 0.4 | n |  | TRUE
86 | bus_LV_404-22_0_4_node_78 | 0.4 | n |  | TRUE
87 | bus_LV_404-22_0_4_node_76 | 0.4 | n |  | TRUE
88 | bus_LV_404-22_0_4_node_80 | 0.4 | n |  | TRUE
89 | bus_LV_404-22_0_4_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_404-22_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_404-22_0_4_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_404-22_0_4_node_90 | 0.4 | n |  | TRUE
93 | bus_LV_404-22_0_4_node_97 | 0.4 | n |  | TRUE
94 | bus_MV_182_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_404-22_0_4_load_0 | 0 | 0.032016 | 0.0080239 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_404-22_0_4_load_1 | 1 | 0.01134 | 0.002842 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_404-22_0_4_load_5 | 4 | 0.0048315 | 0.0012109 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_404-22_0_4_load_51 | 6 | 0.011422 | 0.0028627 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_404-22_0_4_load_48 | 7 | 0.006756 | 0.0016932 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_404-22_0_4_load_69 | 9 | 0.0054533 | 0.0013667 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_404-22_0_4_load_71 | 10 | 0.0062534 | 0.0015673 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_404-22_0_4_load_57 | 13 | 0.0075822 | 0.0019003 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_404-22_0_4_load_95 | 14 | 0.015902 | 0.0039853 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_404-22_0_4_load_96 | 15 | 0.043626 | 0.010934 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_404-22_0_4_load_93 | 16 | 0.0083404 | 0.0020903 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_404-22_0_4_load_75 | 17 | 0.0042628 | 0.0010684 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_404-22_0_4_load_100 | 19 | 0.0050453 | 0.0012645 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_404-22_0_4_load_99 | 20 | 0.013132 | 0.0032911 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_404-22_0_4_load_6 | 21 | 0.0028534 | 0.00071512 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_404-22_0_4_load_9 | 23 | 0.0021476 | 0.00053824 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_404-22_0_4_load_10 | 24 | 0.0032761 | 0.00082107 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_404-22_0_4_load_88 | 27 | 0.0064391 | 0.0016138 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_404-22_0_4_load_17 | 28 | 0.0028674 | 0.00071863 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_404-22_0_4_load_44 | 30 | 0.0061244 | 0.0015349 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_404-22_0_4_load_41 | 32 | 0.022468 | 0.0056309 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_404-22_0_4_load_89 | 33 | 0.024506 | 0.0061418 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_404-22_0_4_load_25 | 34 | 0.0017769 | 0.00044534 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_404-22_0_4_load_56 | 36 | 0.0093793 | 0.0023507 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_404-22_0_4_load_59 | 37 | 0.00574 | 0.0014386 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_404-22_0_4_load_22 | 38 | 0.0026505 | 0.00066427 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_404-22_0_4_load_42 | 39 | 0.0037081 | 0.00092934 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_404-22_0_4_load_18 | 40 | 0.0031735 | 0.00079535 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_404-22_0_4_load_21 | 43 | 0.0017677 | 0.00044302 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_404-22_0_4_load_35 | 46 | 0.0052023 | 0.0013038 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_404-22_0_4_load_28 | 47 | 0.0096257 | 0.0024124 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_404-22_0_4_load_38 | 48 | 0.0083446 | 0.0020914 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_404-22_0_4_load_39 | 49 | 0.0074126 | 0.0018578 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_404-22_0_4_load_27 | 50 | 0.0076566 | 0.0019189 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_404-22_0_4_load_31 | 51 | 0.020733 | 0.0051961 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_404-22_0_4_load_33 | 52 | 0.011007 | 0.0027585 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_404-22_0_4_load_102 | 54 | 0.0054527 | 0.0013666 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_404-22_0_4_load_37 | 57 | 0.0022178 | 0.00055584 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_404-22_0_4_load_60 | 58 | 0.0092436 | 0.0023167 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_404-22_0_4_load_83 | 61 | 0.0062573 | 0.0015682 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_404-22_0_4_load_49 | 63 | 0.01129 | 0.0028296 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_404-22_0_4_load_67 | 65 | 0.012458 | 0.0031222 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_404-22_0_4_load_46 | 66 | 0.0069392 | 0.0017391 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_404-22_0_4_load_43 | 67 | 0.0041576 | 0.001042 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_404-22_0_4_load_45 | 68 | 0.0065196 | 0.001634 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_404-22_0_4_load_58 | 69 | 0.0062724 | 0.001572 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_404-22_0_4_load_65 | 70 | 0.0044867 | 0.0011245 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_404-22_0_4_load_62 | 73 | 0.0072321 | 0.0018125 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_404-22_0_4_load_92 | 76 | 0.0099827 | 0.0025019 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_404-22_0_4_load_74 | 78 | 0.0042412 | 0.0010629 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_404-22_0_4_load_101 | 79 | 0.0070776 | 0.0017738 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_404-22_0_4_load_85 | 80 | 0.011718 | 0.0029368 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_404-22_0_4_load_66 | 81 | 0.0045454 | 0.0011392 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_404-22_0_4_load_68 | 82 | 0.0049264 | 0.0012347 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_404-22_0_4_load_79 | 83 | 0.0043573 | 0.001092 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_404-22_0_4_load_73 | 84 | 0.0073388 | 0.0018393 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_404-22_0_4_load_72 | 85 | 0.0064252 | 0.0016103 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_404-22_0_4_load_78 | 86 | 0.0061538 | 0.0015423 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_404-22_0_4_load_80 | 88 | 0.0052144 | 0.0013069 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_404-22_0_4_load_81 | 89 | 0.0043121 | 0.0010807 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_404-22_0_4_load_84 | 91 | 0.0047148 | 0.0011816 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_404-22_0_4_load_90 | 92 | 0.010225 | 0.0025626 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_404-22_0_4_load_97 | 93 | 0.0075948 | 0.0019034 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_404-22_0_4_line_0 |  | 0 | 1 | 0.015913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_404-22_0_4_line_1 |  | 0 | 2 | 0.0020547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_404-22_0_4_line_2 |  | 2 | 3 | 0.026466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_404-22_0_4_line_3 |  | 2 | 4 | 0.012247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_404-22_0_4_line_4 |  | 3 | 8 | 0.026611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_404-22_0_4_line_5 |  | 3 | 9 | 0.018681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_404-22_0_4_line_6 |  | 5 | 6 | 0.012178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_404-22_0_4_line_7 |  | 5 | 7 | 0.013305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_404-22_0_4_line_8 |  | 6 | 10 | 9.6741e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_404-22_0_4_line_9 |  | 8 | 17 | 0.024995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_404-22_0_4_line_10 |  | 10 | 72 | 0.012254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_404-22_0_4_line_11 |  | 11 | 12 | 0.040853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_404-22_0_4_line_12 |  | 11 | 13 | 0.028649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_404-22_0_4_line_13 |  | 12 | 14 | 0.026023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_404-22_0_4_line_14 |  | 12 | 15 | 0.022308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_404-22_0_4_line_15 |  | 12 | 16 | 0.014293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_404-22_0_4_line_16 |  | 13 | 36 | 0.0098177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_404-22_0_4_line_17 |  | 14 | 76 | 0.014534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_404-22_0_4_line_18 |  | 15 | 20 | 0.042419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_404-22_0_4_line_19 |  | 16 | 77 | 0.050188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_404-22_0_4_line_20 |  | 17 | 78 | 0.0075384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_404-22_0_4_line_21 |  | 18 | 19 | 0.013921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_404-22_0_4_line_22 |  | 18 | 20 | 0.019926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_404-22_0_4_line_23 |  | 19 | 79 | 0.015519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_404-22_0_4_line_24 |  | 21 | 22 | 0.039053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_404-22_0_4_line_25 |  | 22 | 23 | 0.0054243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_404-22_0_4_line_26 |  | 22 | 24 | 0.023872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_404-22_0_4_line_27 |  | 22 | 25 | 0.0418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_404-22_0_4_line_28 |  | 24 | 26 | 0.03621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_404-22_0_4_line_29 |  | 25 | 27 | 0.025698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_404-22_0_4_line_30 |  | 26 | 28 | 0.014987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_404-22_0_4_line_31 |  | 27 | 33 | 0.051053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_404-22_0_4_line_32 |  | 29 | 30 | 0.022151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_404-22_0_4_line_33 |  | 29 | 31 | 0.004079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_404-22_0_4_line_34 |  | 29 | 32 | 0.013281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_404-22_0_4_line_35 |  | 30 | 37 | 0.0067383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_404-22_0_4_line_36 |  | 31 | 38 | 0.023204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_404-22_0_4_line_37 |  | 32 | 39 | 0.00016013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_404-22_0_4_line_38 |  | 33 | 92 | 0.026697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_404-22_0_4_line_39 |  | 34 | 35 | 0.011727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_404-22_0_4_line_40 |  | 35 | 44 | 0.031085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_404-22_0_4_line_41 |  | 35 | 42 | 0.018258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_404-22_0_4_line_42 |  | 36 | 69 | 0.0089222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_404-22_0_4_line_43 |  | 37 | 69 | 0.0067458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_404-22_0_4_line_44 |  | 38 | 42 | 0.032734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_404-22_0_4_line_45 |  | 39 | 67 | 0.0098971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_404-22_0_4_line_46 |  | 40 | 41 | 0.021056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_404-22_0_4_line_47 |  | 41 | 42 | 0.005194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_404-22_0_4_line_48 |  | 41 | 43 | 0.007417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_404-22_0_4_line_49 |  | 44 | 45 | 0.00724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_404-22_0_4_line_50 |  | 45 | 46 | 0.0084519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_404-22_0_4_line_51 |  | 45 | 47 | 0.02271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_404-22_0_4_line_52 |  | 46 | 55 | 0.0062878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_404-22_0_4_line_53 |  | 47 | 50 | 0.0025908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_404-22_0_4_line_54 |  | 48 | 49 | 0.00048837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_404-22_0_4_line_55 |  | 49 | 62 | 0.02378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_404-22_0_4_line_56 |  | 51 | 52 | 0.011944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_404-22_0_4_line_57 |  | 52 | 56 | 0.015702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_404-22_0_4_line_58 |  | 53 | 54 | 0.013294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_404-22_0_4_line_59 |  | 53 | 55 | 0.006469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_404-22_0_4_line_60 |  | 55 | 57 | 0.02433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_404-22_0_4_line_61 |  | 56 | 58 | 0.012312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_404-22_0_4_line_62 |  | 56 | 59 | 0.003729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_404-22_0_4_line_63 |  | 58 | 60 | 0.0095546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_404-22_0_4_line_64 |  | 59 | 61 | 0.021953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_404-22_0_4_line_65 |  | 60 | 73 | 0.009993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_404-22_0_4_line_66 |  | 61 | 71 | 0.0098618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_404-22_0_4_line_67 |  | 62 | 63 | 0.018393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_404-22_0_4_line_68 |  | 62 | 64 | 0.022318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_404-22_0_4_line_69 |  | 63 | 65 | 0.0073945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_404-22_0_4_line_70 |  | 64 | 66 | 0.0011879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_404-22_0_4_line_71 |  | 65 | 70 | 0.0039638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_404-22_0_4_line_72 |  | 66 | 68 | 0.0062586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_404-22_0_4_line_73 |  | 67 | 68 | 0.0035777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_404-22_0_4_line_74 |  | 70 | 81 | 0.0056025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_404-22_0_4_line_75 |  | 71 | 88 | 0.015107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_404-22_0_4_line_76 |  | 71 | 87 | 0.013337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_404-22_0_4_line_77 |  | 72 | 85 | 0.011198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_404-22_0_4_line_78 |  | 72 | 84 | 0.013989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_404-22_0_4_line_79 |  | 73 | 74 | 0.036756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_404-22_0_4_line_80 |  | 74 | 75 | 0.00434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_404-22_0_4_line_81 |  | 75 | 80 | 0.025174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_404-22_0_4_line_82 |  | 76 | 92 | 0.008384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_404-22_0_4_line_83 |  | 77 | 93 | 0.020526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_404-22_0_4_line_84 |  | 78 | 87 | 0.013746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_404-22_0_4_line_85 |  | 81 | 82 | 0.0017155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_404-22_0_4_line_86 |  | 82 | 83 | 0.0049938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_404-22_0_4_line_87 |  | 83 | 84 | 0.0020458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_404-22_0_4_line_88 |  | 85 | 86 | 7.0708e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_404-22_0_4_line_89 |  | 86 | 87 | 0.015039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
90 | LV_404-22_0_4_line_90 |  | 88 | 89 | 0.0016362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_404-22_0_4_line_91 |  | 89 | 90 | 0.0060216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_404-22_0_4_line_92 |  | 90 | 91 | 0.0010447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_404-22_0_4_trafo_48 | 0.63 MVA 20/0.4 kV | 94 | 7 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2614278.5919 | 1211929.1779 | 2614290.7327 | 1211918.8913
1 | 2614277.0242 | 1211930.5062 | 2614278.5919 | 1211929.1779
2 | 2614277.0242 | 1211930.5062 | 2614260.4274 | 1211909.8551
3 | 2614277.0242 | 1211930.5062 | 2614268.1665 | 1211938.9633
4 | 2614244.5617 | 1211888.4609 | 2614260.4274 | 1211909.8551
5 | 2614260.4274 | 1211909.8551 | 2614274.8846 | 1211898.0242
6 | 2614313.6367 | 1211898.5089 | 2614305.4249 | 1211889.5158
7 | 2614313.6367 | 1211898.5089 | 2614317.9523 | 1211895.2508 | 2614323.1146 | 1211889.2736
8 | 2614305.4183 | 1211889.5086 | 2614305.4249 | 1211889.5158
9 | 2614244.5617 | 1211888.4609 | 2614257.3566 | 1211878.5525 | 2614261.8024 | 1211874.861 | 2614264.1831 | 1211872.9804
10 | 2614297.1553 | 1211880.4595 | 2614305.4183 | 1211889.5086
11 | 2614333.1533 | 1211949.8399 | 2614329.0073 | 1211945.7277 | 2614344.0588 | 1211932.6342 | 2614355.1223 | 1211922.4105
12 | 2614355.1223 | 1211922.4105 | 2614342.2069 | 1211909.6613 | 2614349.6634 | 1211902.2671
13 | 2614333.1533 | 1211949.8399 | 2614342.1295 | 1211941.9459 | 2614350.9233 | 1211934.107 | 2614352.6278 | 1211932.5786
14 | 2614333.1533 | 1211949.8399 | 2614327.0618 | 1211955.5063 | 2614316.6097 | 1211964.8026
15 | 2614333.1533 | 1211949.8399 | 2614334.0855 | 1211950.7649 | 2614343.2997 | 1211959.906
16 | 2614356.6346 | 1211895.3541 | 2614349.6634 | 1211902.2671
17 | 2614352.6278 | 1211932.5786 | 2614363.4485 | 1211922.8754
18 | 2614316.6097 | 1211964.8026 | 2614298.1531 | 1211981.2183 | 2614285.93 | 1211994.0458
19 | 2614378.9173 | 1211995.2639 | 2614376.7724 | 1211993.1131 | 2614343.2997 | 1211959.906
20 | 2614270.0985 | 1211868.3076 | 2614264.1831 | 1211872.9804
21 | 2614273.0833 | 1212009.252 | 2614281.0042 | 1212020.7
22 | 2614273.0833 | 1212009.252 | 2614281.1151 | 1211999.0987 | 2614285.93 | 1211994.0458
23 | 2614289.834 | 1212033.4616 | 2614281.0042 | 1212020.7
24 | 2614441.8507 | 1211892.5467 | 2614455.938 | 1211888.7452 | 2614473.9893 | 1211872.2367
25 | 2614441.8507 | 1211892.5467 | 2614440.3717 | 1211891.5092 | 2614438.6331 | 1211891.0158 | 2614436.8247 | 1211891.1004
26 | 2614441.8507 | 1211892.5467 | 2614447.7449 | 1211886.8799 | 2614459.0628 | 1211876.0051
27 | 2614441.8507 | 1211892.5467 | 2614442.9185 | 1211894.0056 | 2614443.4461 | 1211895.7301 | 2614443.3886 | 1211897.531 | 2614442.7463 | 1211899.2192 | 2614449.694 | 1211904.0276 | 2614465.0228 | 1211914.6372 | 2614459.8132 | 1211920.0165
28 | 2614485.1735 | 1211850.9169 | 2614459.0628 | 1211876.0051
29 | 2614459.8132 | 1211920.0165 | 2614455.077 | 1211914.9467 | 2614452.7493 | 1211912.9955 | 2614448.8322 | 1211911.6742 | 2614443.2761 | 1211909.5263 | 2614438.7944 | 1211909.182 | 2614437.7183 | 1211908.8135
30 | 2614485.1735 | 1211850.9169 | 2614475.0138 | 1211839.8992
31 | 2614437.7183 | 1211908.8135 | 2614435.3936 | 1211908.0176 | 2614432.5051 | 1211905.4536 | 2614427.9855 | 1211901.9519 | 2614422.7199 | 1211899.0042 | 2614417.1173 | 1211897.2231 | 2614411.3757 | 1211896.3643 | 2614405.1222 | 1211896.6828 | 2614398.8134 | 1211897.8794 | 2614392.5096 | 1211900.1878 | 2614390.8673 | 1211901.1458
32 | 2614388.2736 | 1211863.9795 | 2614372.5446 | 1211879.5771
33 | 2614388.2736 | 1211863.9795 | 2614390.6672 | 1211860.6723
34 | 2614388.2736 | 1211863.9795 | 2614376.5074 | 1211857.8197
35 | 2614372.5446 | 1211879.5771 | 2614367.76 | 1211884.3217
36 | 2614390.6672 | 1211860.6723 | 2614397.2887 | 1211868.4481 | 2614400.3446 | 1211870.8902 | 2614405.0318 | 1211871.1127 | 2614407.4764 | 1211868.6728 | 2614407.8604 | 1211867.8226
37 | 2614376.5074 | 1211857.8197 | 2614376.3656 | 1211857.7454
38 | 2614390.8673 | 1211901.1458 | 2614385.4492 | 1211904.3064 | 2614379.1853 | 1211908.994 | 2614369.7303 | 1211917.323
39 | 2614408.2419 | 1211825.2614 | 2614411.1226 | 1211821.5996 | 2614415.945 | 1211816.4318
40 | 2614408.2419 | 1211825.2614 | 2614385.8354 | 1211803.651
41 | 2614408.2419 | 1211825.2614 | 2614416.0418 | 1211832.7399 | 2614421.3322 | 1211837.9889
42 | 2614356.6346 | 1211895.3541 | 2614362.97 | 1211889.0717
43 | 2614367.76 | 1211884.3217 | 2614362.97 | 1211889.0717
44 | 2614421.3322 | 1211837.9889 | 2614407.8604 | 1211867.8226
45 | 2614367.5974 | 1211853.1551 | 2614376.3656 | 1211857.7454
46 | 2614425.2976 | 1211841.3559 | 2614440.2041 | 1211826.4853
47 | 2614421.3322 | 1211837.9889 | 2614425.2976 | 1211841.3559
48 | 2614431.7085 | 1211845.1179 | 2614425.2976 | 1211841.3559
49 | 2614385.8354 | 1211803.651 | 2614385.2075 | 1211802.5267 | 2614384.3618 | 1211797.1883 | 2614384.2416 | 1211796.6544
50 | 2614384.2416 | 1211796.6544 | 2614385.6677 | 1211794.4232 | 2614389.8856 | 1211790.4365
51 | 2614384.2416 | 1211796.6544 | 2614380.2253 | 1211795.4441 | 2614370.4407 | 1211785.5039 | 2614367.2063 | 1211782.2785
52 | 2614394.4553 | 1211786.1175 | 2614389.8856 | 1211790.4365
53 | 2614367.2063 | 1211782.2785 | 2614365.3718 | 1211780.449
54 | 2614351.5432 | 1211819.8106 | 2614351.2546 | 1211820.2046
55 | 2614337.2013 | 1211839.3878 | 2614351.2546 | 1211820.2046
56 | 2614329.8069 | 1211808.1192 | 2614321.9649 | 1211817.1286
57 | 2614310.6297 | 1211827.94 | 2614318.2962 | 1211821.3436 | 2614321.9649 | 1211817.1286
58 | 2614398.13 | 1211780.8456 | 2614388.7088 | 1211771.4399
59 | 2614398.13 | 1211780.8456 | 2614396.9085 | 1211783.2773 | 2614394.4553 | 1211786.1175
60 | 2614394.4553 | 1211786.1175 | 2614402.8026 | 1211787.1492 | 2614409.2352 | 1211788.1875 | 2614414.218 | 1211785.5536 | 2614416.9597 | 1211782.9695
61 | 2614310.6297 | 1211827.94 | 2614303.8966 | 1211825.4226 | 2614299.2955 | 1211823.1686
62 | 2614314.1061 | 1211829.3158 | 2614310.6297 | 1211827.94
63 | 2614290.7151 | 1211818.9653 | 2614299.2955 | 1211823.1686
64 | 2614314.1061 | 1211829.3158 | 2614298.5722 | 1211844.8283
65 | 2614290.7151 | 1211818.9653 | 2614287.938 | 1211811.0764 | 2614287.1383 | 1211809.6565
66 | 2614291.594 | 1211851.7968 | 2614298.5722 | 1211844.8283
67 | 2614337.2013 | 1211839.3878 | 2614330.4643 | 1211848.0654 | 2614329.506 | 1211851.654 | 2614326.9451 | 1211854.3144
68 | 2614357.8306 | 1211848.042 | 2614348.8971 | 1211844.4075 | 2614340.1083 | 1211840.5954 | 2614337.2013 | 1211839.3878
69 | 2614326.9451 | 1211854.3144 | 2614321.8169 | 1211859.6418
70 | 2614357.8306 | 1211848.042 | 2614358.8831 | 1211848.593
71 | 2614319.068 | 1211862.4975 | 2614321.8169 | 1211859.6418
72 | 2614364.4278 | 1211851.4958 | 2614358.8831 | 1211848.593
73 | 2614364.4278 | 1211851.4958 | 2614367.5974 | 1211853.1551
74 | 2614319.068 | 1211862.4975 | 2614317.8681 | 1211863.744 | 2614314.8546 | 1211866.1759
75 | 2614291.594 | 1211851.7968 | 2614280.1374 | 1211841.95
76 | 2614280.8852 | 1211859.7869 | 2614291.594 | 1211851.7968
77 | 2614297.1553 | 1211880.4595 | 2614290.2298 | 1211871.6599
78 | 2614297.1553 | 1211880.4595 | 2614308.0414 | 1211871.6743
79 | 2614267.8824 | 1211778.377 | 2614278.64 | 1211794.5673 | 2614287.1383 | 1211809.6565
80 | 2614267.8824 | 1211778.377 | 2614271.3304 | 1211775.7282
81 | 2614271.3304 | 1211775.7282 | 2614280.6793 | 1211770.9589 | 2614292.0345 | 1211761.6568
82 | 2614369.7303 | 1211917.323 | 2614364.6358 | 1211921.8107 | 2614363.4485 | 1211922.8754
83 | 2614378.9173 | 1211995.2639 | 2614394.5305 | 1211981.9396
84 | 2614280.8852 | 1211859.7869 | 2614270.0985 | 1211868.3076
85 | 2614314.8546 | 1211866.1759 | 2614313.5196 | 1211867.2533
86 | 2614309.6335 | 1211870.3895 | 2614313.5196 | 1211867.2533
87 | 2614308.0414 | 1211871.6743 | 2614309.6335 | 1211870.3895
88 | 2614290.2298 | 1211871.6599 | 2614290.1861 | 1211871.6044
89 | 2614280.8852 | 1211859.7869 | 2614290.1861 | 1211871.6044
90 | 2614280.1374 | 1211841.95 | 2614278.8965 | 1211840.8835
91 | 2614274.3298 | 1211836.9585 | 2614278.8965 | 1211840.8835
92 | 2614274.3298 | 1211836.9585 | 2614273.5431 | 1211836.2711

## bus_geodata
| x | y | coords
0 | 2614278.5919 | 1211929.1779
1 | 2614290.7327 | 1211918.8913
2 | 2614277.0242 | 1211930.5062
3 | 2614260.4274 | 1211909.8551
4 | 2614268.1665 | 1211938.9633
5 | 2614313.6367 | 1211898.5089
6 | 2614305.4249 | 1211889.5158
7 | 2614323.1146 | 1211889.2736
8 | 2614244.5617 | 1211888.4609
9 | 2614274.8846 | 1211898.0242
10 | 2614305.4183 | 1211889.5086
11 | 2614355.1223 | 1211922.4105
12 | 2614333.1533 | 1211949.8399
13 | 2614349.6634 | 1211902.2671
14 | 2614352.6278 | 1211932.5786
15 | 2614316.6097 | 1211964.8026
16 | 2614343.2997 | 1211959.906
17 | 2614264.1831 | 1211872.9804
18 | 2614273.0833 | 1212009.252
19 | 2614281.0042 | 1212020.7
20 | 2614285.93 | 1211994.0458
21 | 2614473.9893 | 1211872.2367
22 | 2614441.8507 | 1211892.5467
23 | 2614436.8247 | 1211891.1004
24 | 2614459.0628 | 1211876.0051
25 | 2614459.8132 | 1211920.0165
26 | 2614485.1735 | 1211850.9169
27 | 2614437.7183 | 1211908.8135
28 | 2614475.0138 | 1211839.8992
29 | 2614388.2736 | 1211863.9795
30 | 2614372.5446 | 1211879.5771
31 | 2614390.6672 | 1211860.6723
32 | 2614376.5074 | 1211857.8197
33 | 2614390.8673 | 1211901.1458
34 | 2614415.945 | 1211816.4318
35 | 2614408.2419 | 1211825.2614
36 | 2614356.6346 | 1211895.3541
37 | 2614367.76 | 1211884.3217
38 | 2614407.8604 | 1211867.8226
39 | 2614376.3656 | 1211857.7454
40 | 2614440.2041 | 1211826.4853
41 | 2614425.2976 | 1211841.3559
42 | 2614421.3322 | 1211837.9889
43 | 2614431.7085 | 1211845.1179
44 | 2614385.8354 | 1211803.651
45 | 2614384.2416 | 1211796.6544
46 | 2614389.8856 | 1211790.4365
47 | 2614367.2063 | 1211782.2785
48 | 2614351.5432 | 1211819.8106
49 | 2614351.2546 | 1211820.2046
50 | 2614365.3718 | 1211780.449
51 | 2614329.8069 | 1211808.1192
52 | 2614321.9649 | 1211817.1286
53 | 2614398.13 | 1211780.8456
54 | 2614388.7088 | 1211771.4399
55 | 2614394.4553 | 1211786.1175
56 | 2614310.6297 | 1211827.94
57 | 2614416.9597 | 1211782.9695
58 | 2614299.2955 | 1211823.1686
59 | 2614314.106 | 1211829.3158
60 | 2614290.7151 | 1211818.9653
61 | 2614298.5722 | 1211844.8283
62 | 2614337.2013 | 1211839.3878
63 | 2614326.9451 | 1211854.3144
64 | 2614357.8306 | 1211848.042
65 | 2614321.8169 | 1211859.6418
66 | 2614358.8831 | 1211848.593
67 | 2614367.5974 | 1211853.1551
68 | 2614364.4278 | 1211851.4958
69 | 2614362.97 | 1211889.0717
70 | 2614319.068 | 1211862.4975
71 | 2614291.594 | 1211851.7968
72 | 2614297.1553 | 1211880.4595
73 | 2614287.1383 | 1211809.6565
74 | 2614267.8824 | 1211778.377
75 | 2614271.3304 | 1211775.7282
76 | 2614363.4485 | 1211922.8754
77 | 2614378.9173 | 1211995.2639
78 | 2614270.0985 | 1211868.3076
79 | 2614289.834 | 1212033.4616
80 | 2614292.0345 | 1211761.6568
81 | 2614314.8546 | 1211866.1759
82 | 2614313.5196 | 1211867.2533
83 | 2614309.6335 | 1211870.3895
84 | 2614308.0414 | 1211871.6743
85 | 2614290.2298 | 1211871.6599
86 | 2614290.1861 | 1211871.6044
87 | 2614280.8852 | 1211859.7869
88 | 2614280.1374 | 1211841.95
89 | 2614278.8965 | 1211840.8835
90 | 2614274.3298 | 1211836.9585
91 | 2614273.5431 | 1211836.2711
92 | 2614369.7303 | 1211917.323
93 | 2614394.5305 | 1211981.9396
94 | 2614313.6367 | 1211898.5089

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1