## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4042-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4042-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4042-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4042-1_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4042-1_0_6_node_141 | 0.4 | n |  | TRUE
5 | bus_LV_4042-1_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_4042-1_0_6_node_154 | 0.4 | n |  | TRUE
7 | bus_LV_4042-1_0_6_node_139 | 0.4 | n |  | TRUE
8 | bus_LV_4042-1_0_6_node_169 | 0.4 | n |  | TRUE
9 | bus_LV_4042-1_0_6_node_168 | 0.4 | n |  | TRUE
10 | bus_LV_4042-1_0_6_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_4042-1_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_4042-1_0_6_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_4042-1_0_6_node_70 | 0.4 | n |  | TRUE
14 | bus_LV_4042-1_0_6_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_4042-1_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_4042-1_0_6_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_4042-1_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_4042-1_0_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_4042-1_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_4042-1_0_6_node_36 | 0.4 | n |  | TRUE
21 | bus_LV_4042-1_0_6_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_4042-1_0_6_node_67 | 0.4 | n |  | TRUE
23 | bus_LV_4042-1_0_6_node_34 | 0.4 | n |  | TRUE
24 | bus_LV_4042-1_0_6_node_44 | 0.4 | n |  | TRUE
25 | bus_LV_4042-1_0_6_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_4042-1_0_6_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_4042-1_0_6_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_4042-1_0_6_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_4042-1_0_6_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_4042-1_0_6_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_4042-1_0_6_node_63 | 0.4 | n |  | TRUE
32 | bus_LV_4042-1_0_6_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_4042-1_0_6_node_64 | 0.4 | n |  | TRUE
34 | bus_LV_4042-1_0_6_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_4042-1_0_6_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_4042-1_0_6_node_66 | 0.4 | n |  | TRUE
37 | bus_LV_4042-1_0_6_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_4042-1_0_6_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_4042-1_0_6_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_4042-1_0_6_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_4042-1_0_6_node_52 | 0.4 | n |  | TRUE
42 | bus_LV_4042-1_0_6_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_4042-1_0_6_node_133 | 0.4 | n |  | TRUE
44 | bus_LV_4042-1_0_6_node_50 | 0.4 | n |  | TRUE
45 | bus_LV_4042-1_0_6_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_4042-1_0_6_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_4042-1_0_6_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_4042-1_0_6_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_4042-1_0_6_node_26 | 0.4 | n |  | TRUE
50 | bus_LV_4042-1_0_6_node_27 | 0.4 | n |  | TRUE
51 | bus_LV_4042-1_0_6_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_4042-1_0_6_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_4042-1_0_6_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_4042-1_0_6_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_4042-1_0_6_node_71 | 0.4 | n |  | TRUE
56 | bus_LV_4042-1_0_6_node_104 | 0.4 | n |  | TRUE
57 | bus_LV_4042-1_0_6_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_4042-1_0_6_node_28 | 0.4 | n |  | TRUE
59 | bus_LV_4042-1_0_6_node_30 | 0.4 | n |  | TRUE
60 | bus_LV_4042-1_0_6_node_32 | 0.4 | n |  | TRUE
61 | bus_LV_4042-1_0_6_node_65 | 0.4 | n |  | TRUE
62 | bus_LV_4042-1_0_6_node_35 | 0.4 | n |  | TRUE
63 | bus_LV_4042-1_0_6_node_37 | 0.4 | n |  | TRUE
64 | bus_LV_4042-1_0_6_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_4042-1_0_6_node_40 | 0.4 | n |  | TRUE
66 | bus_LV_4042-1_0_6_node_74 | 0.4 | n |  | TRUE
67 | bus_LV_4042-1_0_6_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_4042-1_0_6_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_4042-1_0_6_node_73 | 0.4 | n |  | TRUE
70 | bus_LV_4042-1_0_6_node_69 | 0.4 | n |  | TRUE
71 | bus_LV_4042-1_0_6_node_105 | 0.4 | n |  | TRUE
72 | bus_LV_4042-1_0_6_node_45 | 0.4 | n |  | TRUE
73 | bus_LV_4042-1_0_6_node_47 | 0.4 | n |  | TRUE
74 | bus_LV_4042-1_0_6_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_4042-1_0_6_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_4042-1_0_6_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_4042-1_0_6_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_4042-1_0_6_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_4042-1_0_6_node_60 | 0.4 | n |  | TRUE
80 | bus_LV_4042-1_0_6_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_4042-1_0_6_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_4042-1_0_6_node_136 | 0.4 | n |  | TRUE
83 | bus_LV_4042-1_0_6_node_101 | 0.4 | n |  | TRUE
84 | bus_LV_4042-1_0_6_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_4042-1_0_6_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_4042-1_0_6_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_4042-1_0_6_node_78 | 0.4 | n |  | TRUE
88 | bus_LV_4042-1_0_6_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_4042-1_0_6_node_80 | 0.4 | n |  | TRUE
90 | bus_LV_4042-1_0_6_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_4042-1_0_6_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_4042-1_0_6_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_4042-1_0_6_node_89 | 0.4 | n |  | TRUE
94 | bus_LV_4042-1_0_6_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_4042-1_0_6_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_4042-1_0_6_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_4042-1_0_6_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_4042-1_0_6_node_85 | 0.4 | n |  | TRUE
99 | bus_LV_4042-1_0_6_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_4042-1_0_6_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_4042-1_0_6_node_98 | 0.4 | n |  | TRUE
102 | bus_LV_4042-1_0_6_node_125 | 0.4 | n |  | TRUE
103 | bus_LV_4042-1_0_6_node_155 | 0.4 | n |  | TRUE
104 | bus_LV_4042-1_0_6_node_156 | 0.4 | n |  | TRUE
105 | bus_LV_4042-1_0_6_node_109 | 0.4 | n |  | TRUE
106 | bus_LV_4042-1_0_6_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_4042-1_0_6_node_116 | 0.4 | n |  | TRUE
108 | bus_LV_4042-1_0_6_node_117 | 0.4 | n |  | TRUE
109 | bus_LV_4042-1_0_6_node_99 | 0.4 | n |  | TRUE
110 | bus_LV_4042-1_0_6_node_126 | 0.4 | n |  | TRUE
111 | bus_LV_4042-1_0_6_node_134 | 0.4 | n |  | TRUE
112 | bus_LV_4042-1_0_6_node_107 | 0.4 | n |  | TRUE
113 | bus_LV_4042-1_0_6_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_4042-1_0_6_node_115 | 0.4 | n |  | TRUE
115 | bus_LV_4042-1_0_6_node_118 | 0.4 | n |  | TRUE
116 | bus_LV_4042-1_0_6_node_120 | 0.4 | n |  | TRUE
117 | bus_LV_4042-1_0_6_node_122 | 0.4 | n |  | TRUE
118 | bus_LV_4042-1_0_6_node_123 | 0.4 | n |  | TRUE
119 | bus_LV_4042-1_0_6_node_92 | 0.4 | n |  | TRUE
120 | bus_LV_4042-1_0_6_node_93 | 0.4 | n |  | TRUE
121 | bus_LV_4042-1_0_6_node_94 | 0.4 | n |  | TRUE
122 | bus_LV_4042-1_0_6_node_95 | 0.4 | n |  | TRUE
123 | bus_LV_4042-1_0_6_node_96 | 0.4 | n |  | TRUE
124 | bus_LV_4042-1_0_6_node_97 | 0.4 | n |  | TRUE
125 | bus_LV_4042-1_0_6_node_113 | 0.4 | n |  | TRUE
126 | bus_LV_4042-1_0_6_node_121 | 0.4 | n |  | TRUE
127 | bus_LV_4042-1_0_6_node_131 | 0.4 | n |  | TRUE
128 | bus_LV_4042-1_0_6_node_100 | 0.4 | n |  | TRUE
129 | bus_LV_4042-1_0_6_node_127 | 0.4 | n |  | TRUE
130 | bus_LV_4042-1_0_6_node_128 | 0.4 | n |  | TRUE
131 | bus_LV_4042-1_0_6_node_148 | 0.4 | n |  | TRUE
132 | bus_LV_4042-1_0_6_node_164 | 0.4 | n |  | TRUE
133 | bus_LV_4042-1_0_6_node_106 | 0.4 | n |  | TRUE
134 | bus_LV_4042-1_0_6_node_108 | 0.4 | n |  | TRUE
135 | bus_LV_4042-1_0_6_node_110 | 0.4 | n |  | TRUE
136 | bus_LV_4042-1_0_6_node_111 | 0.4 | n |  | TRUE
137 | bus_LV_4042-1_0_6_node_114 | 0.4 | n |  | TRUE
138 | bus_LV_4042-1_0_6_node_119 | 0.4 | n |  | TRUE
139 | bus_LV_4042-1_0_6_node_124 | 0.4 | n |  | TRUE
140 | bus_LV_4042-1_0_6_node_129 | 0.4 | n |  | TRUE
141 | bus_LV_4042-1_0_6_node_132 | 0.4 | n |  | TRUE
142 | bus_LV_4042-1_0_6_node_130 | 0.4 | n |  | TRUE
143 | bus_LV_4042-1_0_6_node_149 | 0.4 | n |  | TRUE
144 | bus_LV_4042-1_0_6_node_147 | 0.4 | n |  | TRUE
145 | bus_LV_4042-1_0_6_node_138 | 0.4 | n |  | TRUE
146 | bus_LV_4042-1_0_6_node_140 | 0.4 | n |  | TRUE
147 | bus_LV_4042-1_0_6_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_4042-1_0_6_node_143 | 0.4 | n |  | TRUE
149 | bus_LV_4042-1_0_6_node_167 | 0.4 | n |  | TRUE
150 | bus_LV_4042-1_0_6_node_158 | 0.4 | n |  | TRUE
151 | bus_LV_4042-1_0_6_node_162 | 0.4 | n |  | TRUE
152 | bus_LV_4042-1_0_6_node_157 | 0.4 | n |  | TRUE
153 | bus_LV_4042-1_0_6_node_163 | 0.4 | n |  | TRUE
154 | bus_LV_4042-1_0_6_node_144 | 0.4 | n |  | TRUE
155 | bus_LV_4042-1_0_6_node_145 | 0.4 | n |  | TRUE
156 | bus_LV_4042-1_0_6_node_171 | 0.4 | n |  | TRUE
157 | bus_LV_4042-1_0_6_node_146 | 0.4 | n |  | TRUE
158 | bus_LV_4042-1_0_6_node_170 | 0.4 | n |  | TRUE
159 | bus_LV_4042-1_0_6_node_175 | 0.4 | n |  | TRUE
160 | bus_LV_4042-1_0_6_node_151 | 0.4 | n |  | TRUE
161 | bus_LV_4042-1_0_6_node_165 | 0.4 | n |  | TRUE
162 | bus_LV_4042-1_0_6_node_152 | 0.4 | n |  | TRUE
163 | bus_LV_4042-1_0_6_node_150 | 0.4 | n |  | TRUE
164 | bus_LV_4042-1_0_6_node_166 | 0.4 | n |  | TRUE
165 | bus_LV_4042-1_0_6_node_160 | 0.4 | n |  | TRUE
166 | bus_LV_4042-1_0_6_node_153 | 0.4 | n |  | TRUE
167 | bus_LV_4042-1_0_6_node_172 | 0.4 | n |  | TRUE
168 | bus_LV_4042-1_0_6_node_173 | 0.4 | n |  | TRUE
169 | bus_LV_4042-1_0_6_node_174 | 0.4 | n |  | TRUE
170 | bus_LV_4042-1_0_6_node_161 | 0.4 | n |  | TRUE
171 | bus_LV_4042-1_0_6_node_176 | 0.4 | n |  | TRUE
172 | bus_LV_4042-1_0_6_node_177 | 0.4 | n |  | TRUE
173 | bus_LV_4042-1_0_6_node_159 | 0.4 | n |  | TRUE
174 | bus_MV_421_0_node_60 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4042-1_0_6_load_0 | 0 | 0.0079761 | 0.001999 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4042-1_0_6_load_4 | 5 | 0.010112 | 0.0025344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4042-1_0_6_load_154 | 6 | 0.01222 | 0.0030625 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4042-1_0_6_load_139 | 7 | 0.0030405 | 0.00076202 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4042-1_0_6_load_169 | 8 | 0.0016479 | 0.00041299 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4042-1_0_6_load_168 | 9 | 0.0030905 | 0.00077455 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4042-1_0_6_load_5 | 10 | 0.0021343 | 0.00053489 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4042-1_0_6_load_6 | 11 | 0.0061693 | 0.0015462 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4042-1_0_6_load_70 | 13 | 0.0092353 | 0.0023146 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4042-1_0_6_load_68 | 14 | 0.0057906 | 0.0014513 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4042-1_0_6_load_8 | 15 | 0.0031921 | 0.00080001 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4042-1_0_6_load_9 | 16 | 0.003192 | 0.00079998 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4042-1_0_6_load_12 | 18 | 0.00097974 | 0.00024555 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4042-1_0_6_load_36 | 20 | 0.0017297 | 0.0004335 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4042-1_0_6_load_33 | 21 | 0.00078886 | 0.00019771 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4042-1_0_6_load_67 | 22 | 0.0083248 | 0.0020864 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4042-1_0_6_load_34 | 23 | 0.0016064 | 0.0004026 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4042-1_0_6_load_44 | 24 | 0.00086011 | 0.00021556 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4042-1_0_6_load_13 | 25 | 0.012506 | 0.0031344 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4042-1_0_6_load_14 | 26 | 0.0016552 | 0.00041484 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4042-1_0_6_load_16 | 28 | 0.0016137 | 0.00040443 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4042-1_0_6_load_18 | 30 | 0.001778 | 0.00044561 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4042-1_0_6_load_63 | 31 | 0.0045553 | 0.0011417 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4042-1_0_6_load_72 | 32 | 0.0022186 | 0.00055603 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4042-1_0_6_load_64 | 33 | 0.024317 | 0.0060944 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4042-1_0_6_load_48 | 35 | 0.0027023 | 0.00067725 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4042-1_0_6_load_66 | 36 | 0.00093338 | 0.00023393 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4042-1_0_6_load_19 | 37 | 0.0027288 | 0.0006839 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4042-1_0_6_load_53 | 40 | 0.010197 | 0.0025557 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4042-1_0_6_load_52 | 41 | 0.0012304 | 0.00030838 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4042-1_0_6_load_55 | 42 | 0.024135 | 0.0060489 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4042-1_0_6_load_133 | 43 | 0.017165 | 0.004302 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4042-1_0_6_load_54 | 45 | 0.009058 | 0.0022702 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4042-1_0_6_load_23 | 46 | 0.00076517 | 0.00019177 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4042-1_0_6_load_24 | 47 | 0.0019015 | 0.00047655 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4042-1_0_6_load_25 | 48 | 0.0010507 | 0.00026333 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4042-1_0_6_load_42 | 51 | 0.003242 | 0.00081251 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4042-1_0_6_load_43 | 52 | 0.0079222 | 0.0019855 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4042-1_0_6_load_31 | 53 | 0.00099367 | 0.00024904 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4042-1_0_6_load_41 | 54 | 0.016986 | 0.0042571 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4042-1_0_6_load_104 | 56 | 0.0017522 | 0.00043915 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4042-1_0_6_load_29 | 57 | 0.0011135 | 0.00027907 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4042-1_0_6_load_28 | 58 | 0.00089028 | 0.00022312 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4042-1_0_6_load_30 | 59 | 0.00098865 | 0.00024778 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4042-1_0_6_load_65 | 61 | 0.0016972 | 0.00042535 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4042-1_0_6_load_35 | 62 | 0.00095668 | 0.00023977 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4042-1_0_6_load_37 | 63 | 0.0011051 | 0.00027697 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4042-1_0_6_load_74 | 66 | 0.0068014 | 0.0017046 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4042-1_0_6_load_73 | 69 | 0.011401 | 0.0028575 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4042-1_0_6_load_105 | 71 | 0.0016123 | 0.00040409 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4042-1_0_6_load_45 | 72 | 0.0015626 | 0.00039162 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4042-1_0_6_load_51 | 74 | 0.0032784 | 0.00082165 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4042-1_0_6_load_56 | 75 | 0.015917 | 0.0039891 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4042-1_0_6_load_57 | 76 | 0.0020482 | 0.00051333 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4042-1_0_6_load_58 | 77 | 0.0020241 | 0.00050728 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4042-1_0_6_load_59 | 78 | 0.0019571 | 0.00049051 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4042-1_0_6_load_60 | 79 | 0.0020402 | 0.00051133 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4042-1_0_6_load_136 | 82 | 0.016111 | 0.0040377 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4042-1_0_6_load_101 | 83 | 0.0023845 | 0.00059762 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4042-1_0_6_load_75 | 84 | 0.0019316 | 0.00048412 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4042-1_0_6_load_76 | 85 | 0.0017166 | 0.00043022 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4042-1_0_6_load_78 | 87 | 0.003941 | 0.0009877 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4042-1_0_6_load_79 | 88 | 0.007306 | 0.0018311 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4042-1_0_6_load_80 | 89 | 0.0015806 | 0.00039615 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4042-1_0_6_load_90 | 90 | 0.0013389 | 0.00033555 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4042-1_0_6_load_88 | 91 | 0.0053336 | 0.0013367 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4042-1_0_6_load_91 | 92 | 0.0035147 | 0.00088086 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4042-1_0_6_load_89 | 93 | 0.0046083 | 0.0011549 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4042-1_0_6_load_81 | 94 | 0.0020255 | 0.00050763 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4042-1_0_6_load_84 | 97 | 0.0018237 | 0.00045705 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4042-1_0_6_load_85 | 98 | 0.0012379 | 0.00031025 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4042-1_0_6_load_98 | 101 | 0.0012858 | 0.00032225 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4042-1_0_6_load_125 | 102 | 0.0045884 | 0.00115 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4042-1_0_6_load_155 | 103 | 0.01089 | 0.0027293 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4042-1_0_6_load_103 | 106 | 0.0010497 | 0.00026308 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4042-1_0_6_load_116 | 107 | 0.001018 | 0.00025513 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4042-1_0_6_load_117 | 108 | 0.0041645 | 0.0010437 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4042-1_0_6_load_99 | 109 | 0.0018622 | 0.0004667 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4042-1_0_6_load_126 | 110 | 0.0029053 | 0.00072813 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4042-1_0_6_load_134 | 111 | 0.0016972 | 0.00042536 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4042-1_0_6_load_107 | 112 | 0.001282 | 0.00032129 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4042-1_0_6_load_102 | 113 | 0.0023894 | 0.00059884 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4042-1_0_6_load_115 | 114 | 0.0022759 | 0.00057039 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4042-1_0_6_load_118 | 115 | 0.0014865 | 0.00037256 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4042-1_0_6_load_123 | 118 | 0.0055145 | 0.0013821 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4042-1_0_6_load_92 | 119 | 0.0113 | 0.0028321 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4042-1_0_6_load_93 | 120 | 0.0052048 | 0.0013045 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4042-1_0_6_load_95 | 122 | 0.013914 | 0.0034872 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4042-1_0_6_load_96 | 123 | 0.028191 | 0.0070654 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4042-1_0_6_load_113 | 125 | 0.013816 | 0.0034625 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4042-1_0_6_load_121 | 126 | 0.0015558 | 0.00038993 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4042-1_0_6_load_131 | 127 | 0.0053777 | 0.0013478 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4042-1_0_6_load_127 | 129 | 0.00064419 | 0.00016145 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4042-1_0_6_load_128 | 130 | 0.0031968 | 0.00080119 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4042-1_0_6_load_148 | 131 | 0.00074651 | 0.00018709 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4042-1_0_6_load_164 | 132 | 0.0019395 | 0.00048609 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4042-1_0_6_load_106 | 133 | 0.00076246 | 0.00019109 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4042-1_0_6_load_110 | 135 | 0.0034272 | 0.00085894 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4042-1_0_6_load_111 | 136 | 0.0014283 | 0.00035796 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4042-1_0_6_load_114 | 137 | 0.0017481 | 0.00043813 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4042-1_0_6_load_124 | 139 | 0.0051212 | 0.0012835 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4042-1_0_6_load_129 | 140 | 0.0031247 | 0.00078313 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4042-1_0_6_load_132 | 141 | 0.0023256 | 0.00058286 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4042-1_0_6_load_130 | 142 | 0.0053735 | 0.0013467 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4042-1_0_6_load_149 | 143 | 0.00067445 | 0.00016903 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4042-1_0_6_load_138 | 145 | 0.0035303 | 0.00088478 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4042-1_0_6_load_143 | 148 | 0.0087359 | 0.0021894 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4042-1_0_6_load_167 | 149 | 0.0028404 | 0.00071187 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4042-1_0_6_load_158 | 150 | 0.0013951 | 0.00034964 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4042-1_0_6_load_162 | 151 | 0.0086291 | 0.0021627 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4042-1_0_6_load_157 | 152 | 0.0018893 | 0.00047351 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4042-1_0_6_load_163 | 153 | 0.0081505 | 0.0020427 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4042-1_0_6_load_144 | 154 | 0.00039198 | 9.8239e-05 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4042-1_0_6_load_146 | 157 | 0.00040623 | 0.00010181 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4042-1_0_6_load_170 | 158 | 0.00080138 | 0.00020084 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4042-1_0_6_load_151 | 160 | 0.0015035 | 0.0003768 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4042-1_0_6_load_165 | 161 | 0.0018961 | 0.0004752 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4042-1_0_6_load_152 | 162 | 0.0022548 | 0.0005651 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4042-1_0_6_load_150 | 163 | 0.001351 | 0.00033859 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4042-1_0_6_load_166 | 164 | 0.0023413 | 0.00058678 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4042-1_0_6_load_160 | 165 | 0.0010962 | 0.00027475 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4042-1_0_6_load_172 | 167 | 0.00046323 | 0.0001161 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4042-1_0_6_load_161 | 170 | 0.0037556 | 0.00094125 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4042-1_0_6_load_176 | 171 | 0.0037178 | 0.00093177 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4042-1_0_6_load_177 | 172 | 0.0010205 | 0.00025577 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4042-1_0_6_load_159 | 173 | 0.0028164 | 0.00070585 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 120 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4042-1_0_6_line_0 |  | 0 | 1 | 0.053139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4042-1_0_6_line_1 |  | 1 | 2 | 0.035739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4042-1_0_6_line_2 |  | 2 | 3 | 0.060121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4042-1_0_6_line_3 |  | 2 | 4 | 0.041478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4042-1_0_6_line_4 |  | 3 | 5 | 0.050005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4042-1_0_6_line_5 |  | 4 | 6 | 0.042263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4042-1_0_6_line_6 |  | 4 | 7 | 0.023453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4042-1_0_6_line_7 |  | 7 | 145 | 0.021456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4042-1_0_6_line_8 |  | 8 | 9 | 0.012689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4042-1_0_6_line_9 |  | 9 | 158 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4042-1_0_6_line_10 |  | 10 | 11 | 0.042449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4042-1_0_6_line_11 |  | 11 | 12 | 0.029359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4042-1_0_6_line_12 |  | 12 | 13 | 0.074989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4042-1_0_6_line_13 |  | 13 | 14 | 0.0026373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4042-1_0_6_line_14 |  | 14 | 70 | 0.049644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4042-1_0_6_line_15 |  | 15 | 16 | 0.0031443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4042-1_0_6_line_16 |  | 16 | 17 | 0.013625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4042-1_0_6_line_17 |  | 17 | 18 | 0.011391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4042-1_0_6_line_18 |  | 18 | 22 | 0.020252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4042-1_0_6_line_19 |  | 19 | 20 | 0.012252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4042-1_0_6_line_20 |  | 19 | 21 | 0.011962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4042-1_0_6_line_21 |  | 21 | 23 | 0.017997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4042-1_0_6_line_22 |  | 22 | 24 | 0.0024604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4042-1_0_6_line_23 |  | 23 | 62 | 0.0059506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4042-1_0_6_line_24 |  | 24 | 50 | 0.034656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4042-1_0_6_line_25 |  | 25 | 26 | 0.0014295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4042-1_0_6_line_26 |  | 25 | 27 | 0.0311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4042-1_0_6_line_27 |  | 26 | 28 | 0.015348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4042-1_0_6_line_28 |  | 27 | 29 | 0.015651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_4042-1_0_6_line_29 |  | 27 | 30 | 0.0081646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_4042-1_0_6_line_30 |  | 29 | 31 | 0.017348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_4042-1_0_6_line_31 |  | 30 | 32 | 0.0036157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_4042-1_0_6_line_32 |  | 31 | 35 | 0.011906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_4042-1_0_6_line_33 |  | 32 | 36 | 0.014679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_4042-1_0_6_line_34 |  | 33 | 34 | 0.015954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4042-1_0_6_line_35 |  | 34 | 42 | 0.0046776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4042-1_0_6_line_36 |  | 34 | 38 | 0.023497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4042-1_0_6_line_37 |  | 35 | 68 | 0.016724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_4042-1_0_6_line_38 |  | 36 | 60 | 0.013777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_4042-1_0_6_line_39 |  | 37 | 38 | 0.014139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4042-1_0_6_line_40 |  | 38 | 39 | 0.009907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4042-1_0_6_line_41 |  | 39 | 40 | 0.01822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4042-1_0_6_line_42 |  | 39 | 41 | 0.011433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_4042-1_0_6_line_43 |  | 40 | 43 | 0.025163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4042-1_0_6_line_44 |  | 41 | 44 | 0.011735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
45 | LV_4042-1_0_6_line_45 |  | 42 | 45 | 0.018423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4042-1_0_6_line_46 |  | 44 | 73 | 0.007662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_4042-1_0_6_line_47 |  | 45 | 54 | 0.01664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4042-1_0_6_line_48 |  | 46 | 47 | 0.02731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
49 | LV_4042-1_0_6_line_49 |  | 46 | 48 | 0.0033072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_4042-1_0_6_line_50 |  | 47 | 49 | 0.018432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_4042-1_0_6_line_51 |  | 48 | 50 | 0.0079154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_4042-1_0_6_line_52 |  | 49 | 51 | 0.020883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4042-1_0_6_line_53 |  | 49 | 52 | 0.020592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_4042-1_0_6_line_54 |  | 50 | 53 | 0.013981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_4042-1_0_6_line_55 |  | 51 | 55 | 0.01629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4042-1_0_6_line_56 |  | 52 | 56 | 0.041829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_4042-1_0_6_line_57 |  | 53 | 57 | 0.015203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
58 | LV_4042-1_0_6_line_58 |  | 55 | 69 | 0.029293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4042-1_0_6_line_59 |  | 55 | 70 | 0.00593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4042-1_0_6_line_60 |  | 56 | 71 | 0.019601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_4042-1_0_6_line_61 |  | 57 | 58 | 0.0038663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_4042-1_0_6_line_62 |  | 58 | 59 | 0.013609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_4042-1_0_6_line_63 |  | 59 | 60 | 0.0020887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_4042-1_0_6_line_64 |  | 60 | 61 | 0.011456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4042-1_0_6_line_65 |  | 61 | 62 | 0.018444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4042-1_0_6_line_66 |  | 63 | 64 | 0.016064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4042-1_0_6_line_67 |  | 64 | 65 | 0.009222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4042-1_0_6_line_68 |  | 65 | 66 | 0.027138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4042-1_0_6_line_69 |  | 66 | 67 | 0.0041957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4042-1_0_6_line_70 |  | 67 | 68 | 0.030888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4042-1_0_6_line_71 |  | 68 | 72 | 0.033837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_4042-1_0_6_line_72 |  | 69 | 83 | 0.0017623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4042-1_0_6_line_73 |  | 70 | 79 | 0.015709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4042-1_0_6_line_74 |  | 71 | 124 | 0.011085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
75 | LV_4042-1_0_6_line_75 |  | 72 | 73 | 0.030537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_4042-1_0_6_line_76 |  | 73 | 74 | 0.0232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4042-1_0_6_line_77 |  | 75 | 76 | 0.020292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4042-1_0_6_line_78 |  | 75 | 77 | 0.0019782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4042-1_0_6_line_79 |  | 76 | 78 | 0.0088787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4042-1_0_6_line_80 |  | 77 | 79 | 0.010097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4042-1_0_6_line_81 |  | 78 | 80 | 0.035375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4042-1_0_6_line_82 |  | 80 | 81 | 0.074627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4042-1_0_6_line_83 |  | 81 | 82 | 0.043111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4042-1_0_6_line_84 |  | 84 | 85 | 0.022501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4042-1_0_6_line_85 |  | 84 | 86 | 0.010887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4042-1_0_6_line_86 |  | 85 | 87 | 0.015795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4042-1_0_6_line_87 |  | 86 | 88 | 0.038812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4042-1_0_6_line_88 |  | 86 | 89 | 0.015156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4042-1_0_6_line_89 |  | 87 | 90 | 0.027341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4042-1_0_6_line_90 |  | 88 | 91 | 0.048147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4042-1_0_6_line_91 |  | 90 | 92 | 0.012033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4042-1_0_6_line_92 |  | 91 | 93 | 0.0021424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4042-1_0_6_line_93 |  | 93 | 116 | 0.031956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4042-1_0_6_line_94 |  | 94 | 95 | 0.016304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
95 | LV_4042-1_0_6_line_95 |  | 94 | 96 | 0.018719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_4042-1_0_6_line_96 |  | 95 | 97 | 0.0093572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_4042-1_0_6_line_97 |  | 95 | 98 | 0.042079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4042-1_0_6_line_98 |  | 96 | 99 | 0.022062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4042-1_0_6_line_99 |  | 96 | 100 | 0.030484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
100 | LV_4042-1_0_6_line_100 |  | 97 | 101 | 0.0066672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
101 | LV_4042-1_0_6_line_101 |  | 98 | 102 | 0.0075598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4042-1_0_6_line_102 |  | 99 | 105 | 0.018187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4042-1_0_6_line_103 |  | 99 | 106 | 0.028397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4042-1_0_6_line_104 |  | 100 | 107 | 0.013475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4042-1_0_6_line_105 |  | 100 | 108 | 0.0074686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_4042-1_0_6_line_106 |  | 101 | 109 | 0.016754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_4042-1_0_6_line_107 |  | 102 | 110 | 0.021943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4042-1_0_6_line_108 |  | 103 | 104 | 0.036496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4042-1_0_6_line_109 |  | 104 | 170 | 0.064612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4042-1_0_6_line_110 |  | 105 | 111 | 0.024955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4042-1_0_6_line_111 |  | 105 | 112 | 0.0087336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4042-1_0_6_line_112 |  | 106 | 113 | 0.043005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4042-1_0_6_line_113 |  | 107 | 114 | 0.010043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4042-1_0_6_line_114 |  | 108 | 115 | 0.011708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
115 | LV_4042-1_0_6_line_115 |  | 109 | 128 | 0.063445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
116 | LV_4042-1_0_6_line_116 |  | 112 | 133 | 0.014404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4042-1_0_6_line_117 |  | 114 | 137 | 0.0064627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4042-1_0_6_line_118 |  | 115 | 138 | 0.01951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
119 | LV_4042-1_0_6_line_119 |  | 116 | 117 | 0.008793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4042-1_0_6_line_120 |  | 116 | 118 | 0.014816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4042-1_0_6_line_121 |  | 117 | 140 | 0.022507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4042-1_0_6_line_122 |  | 117 | 138 | 0.004274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4042-1_0_6_line_123 |  | 119 | 120 | 0.034094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_4042-1_0_6_line_124 |  | 119 | 121 | 0.029027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_4042-1_0_6_line_125 |  | 120 | 122 | 0.01273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4042-1_0_6_line_126 |  | 121 | 123 | 0.0088537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4042-1_0_6_line_127 |  | 121 | 124 | 0.066812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_4042-1_0_6_line_128 |  | 123 | 125 | 0.019975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4042-1_0_6_line_129 |  | 124 | 126 | 0.0061551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
130 | LV_4042-1_0_6_line_130 |  | 126 | 127 | 0.01511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_4042-1_0_6_line_131 |  | 127 | 141 | 0.0025355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_4042-1_0_6_line_132 |  | 128 | 129 | 0.022068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_4042-1_0_6_line_133 |  | 128 | 130 | 0.061761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4042-1_0_6_line_134 |  | 129 | 131 | 0.017338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_4042-1_0_6_line_135 |  | 130 | 132 | 0.026184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4042-1_0_6_line_136 |  | 131 | 143 | 0.023363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
137 | LV_4042-1_0_6_line_137 |  | 132 | 144 | 0.022881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4042-1_0_6_line_138 |  | 133 | 134 | 0.017614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4042-1_0_6_line_139 |  | 134 | 135 | 0.01895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4042-1_0_6_line_140 |  | 134 | 136 | 0.01359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4042-1_0_6_line_141 |  | 138 | 139 | 0.026789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
142 | LV_4042-1_0_6_line_142 |  | 139 | 141 | 0.031863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
143 | LV_4042-1_0_6_line_143 |  | 140 | 142 | 0.012119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4042-1_0_6_line_144 |  | 143 | 163 | 0.019167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
145 | LV_4042-1_0_6_line_145 |  | 144 | 161 | 0.017867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4042-1_0_6_line_146 |  | 144 | 155 | 0.033079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4042-1_0_6_line_147 |  | 145 | 146 | 0.011592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4042-1_0_6_line_148 |  | 146 | 147 | 0.004412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4042-1_0_6_line_149 |  | 146 | 148 | 0.034418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4042-1_0_6_line_150 |  | 147 | 149 | 0.037698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4042-1_0_6_line_151 |  | 147 | 150 | 0.019051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4042-1_0_6_line_152 |  | 148 | 151 | 0.022499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4042-1_0_6_line_153 |  | 150 | 152 | 0.026439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4042-1_0_6_line_154 |  | 151 | 153 | 0.020439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4042-1_0_6_line_155 |  | 152 | 173 | 0.0095061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4042-1_0_6_line_156 |  | 154 | 155 | 0.015624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4042-1_0_6_line_157 |  | 154 | 156 | 0.060319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4042-1_0_6_line_158 |  | 155 | 157 | 0.014697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4042-1_0_6_line_159 |  | 156 | 159 | 0.055136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4042-1_0_6_line_160 |  | 156 | 158 | 0.035151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4042-1_0_6_line_161 |  | 157 | 160 | 0.022586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4042-1_0_6_line_162 |  | 159 | 168 | 0.008012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4042-1_0_6_line_163 |  | 160 | 162 | 0.0022318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4042-1_0_6_line_164 |  | 162 | 166 | 0.053763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4042-1_0_6_line_165 |  | 163 | 164 | 0.011246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
166 | LV_4042-1_0_6_line_166 |  | 164 | 165 | 0.010826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
167 | LV_4042-1_0_6_line_167 |  | 165 | 173 | 0.021417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
168 | LV_4042-1_0_6_line_168 |  | 166 | 170 | 0.05752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4042-1_0_6_line_169 |  | 167 | 168 | 0.011049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4042-1_0_6_line_170 |  | 168 | 169 | 0.049081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4042-1_0_6_line_171 |  | 169 | 171 | 0.035159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4042-1_0_6_line_172 |  | 171 | 172 | 0.019689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4042-1_0_6_trafo_93 | 0.63 MVA 20/0.4 kV | 174 | 120 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2662528.6528 | 1259728.7839 | 2662497.0233 | 1259754.7688 | 2662488.2572 | 1259763.2598
1 | 2662528.9384 | 1259703.1904 | 2662533.2229 | 1259705.7264 | 2662538.1936 | 1259706.1014 | 2662539.3158 | 1259709.7493 | 2662537.548 | 1259715.1234 | 2662528.6528 | 1259728.7839
2 | 2662528.9384 | 1259703.1904 | 2662533.2229 | 1259705.7264 | 2662538.1936 | 1259706.1014 | 2662541.4303 | 1259705.0793 | 2662544.2022 | 1259703.1183 | 2662546.2359 | 1259700.3934 | 2662551.82 | 1259702.6318 | 2662572.6044 | 1259713.6483 | 2662579.6229 | 1259721.3615
3 | 2662528.9384 | 1259703.1904 | 2662525.9683 | 1259698.2332 | 2662525.9389 | 1259692.462 | 2662528.8633 | 1259687.4782 | 2662514.2854 | 1259678.9847 | 2662507.8467 | 1259675.592
4 | 2662579.6229 | 1259721.3615 | 2662582.3168 | 1259728.195 | 2662583.7065 | 1259735.048 | 2662582.164 | 1259743.3488 | 2662568.9854 | 1259767.1705
5 | 2662507.8467 | 1259675.592 | 2662509.8316 | 1259668.2187 | 2662515.2987 | 1259667.2646 | 2662522.7941 | 1259666.243 | 2662535.6415 | 1259655.1929 | 2662537.9938 | 1259651.2783
6 | 2662507.8467 | 1259675.592 | 2662498.5179 | 1259678.2177 | 2662488.4296 | 1259687.5781
7 | 2662472.7013 | 1259702.1717 | 2662488.4296 | 1259687.5781
8 | 2662547.8589 | 1259873.369 | 2662557.1283 | 1259882.0342
9 | 2662547.8589 | 1259873.369 | 2662539.6792 | 1259865.7225
10 | 2661871.9258 | 1259844.4994 | 2661848.9954 | 1259849.2651 | 2661830.3605 | 1259853.1155
11 | 2661899.3296 | 1259833.9912 | 2661872.6303 | 1259844.3529 | 2661871.9258 | 1259844.4994
12 | 2661935.9834 | 1259899.4111 | 2661899.3296 | 1259833.9912
13 | 2661935.9834 | 1259899.4111 | 2661938.3926 | 1259898.3381
14 | 2661983.7424 | 1259878.1399 | 2661938.3926 | 1259898.3381
15 | 2661872.5614 | 1259975.7063 | 2661875.5148 | 1259974.6275
16 | 2661888.3124 | 1259969.9528 | 2661875.5148 | 1259974.6275
17 | 2661888.3124 | 1259969.9528 | 2661892.7082 | 1259968.3421 | 2661898.7752 | 1259965.4775
18 | 2661917.0889 | 1259956.8307 | 2661898.7752 | 1259965.4775
19 | 2661905.0397 | 1260010.7241 | 2661909.6884 | 1260022.0599
20 | 2661905.0397 | 1260010.7241 | 2661915.6135 | 1260005.1316
21 | 2661931.5226 | 1259996.7172 | 2661915.6135 | 1260005.1316
22 | 2661917.0889 | 1259956.8307 | 2661919.3138 | 1259955.7803
23 | 2661931.5226 | 1259996.7172 | 2661936.7828 | 1259993.935
24 | 2661950.6523 | 1259940.9838 | 2661919.3138 | 1259955.7803
25 | 2661948.6692 | 1260040.6151 | 2661949.9415 | 1260039.9633
26 | 2661977.6204 | 1260025.7835 | 2661949.9415 | 1260039.9633
27 | 2661948.6692 | 1260040.6151 | 2661935.0092 | 1260047.613
28 | 2661991.0644 | 1260033.8635 | 2661977.6204 | 1260025.7835
29 | 2661977.6204 | 1260025.7835 | 2661975.1464 | 1260018.0028
30 | 2661991.0644 | 1260033.8635 | 2661997.8558 | 1260049.8271
31 | 2661974.0508 | 1260014.5571 | 2661975.1464 | 1260018.0028
32 | 2661997.8558 | 1260049.8271 | 2662002.5165 | 1260060.7824
33 | 2661974.0508 | 1260014.5571 | 2661969.6028 | 1260000.5685
34 | 2662035.1799 | 1259985.5015 | 2662025.1284 | 1259991.7007 | 2662022.3649 | 1259994.7899
35 | 2662035.1799 | 1259985.5015 | 2662033.1568 | 1259981.2839
36 | 2662045.654 | 1260006.5488 | 2662035.1799 | 1259985.5015
37 | 2662009.0636 | 1260076.1718 | 2662002.5165 | 1260060.7824
38 | 2661965.428 | 1259987.439 | 2661969.6028 | 1260000.5685
39 | 2662045.654 | 1260006.5488 | 2662032.6233 | 1260012.0365
40 | 2662050.0679 | 1260015.4238 | 2662045.654 | 1260006.5488
41 | 2662050.0679 | 1260015.4238 | 2662064.6606 | 1260004.5141
42 | 2662050.0679 | 1260015.4238 | 2662055.2012 | 1260025.6397
43 | 2662084.8143 | 1259989.4469 | 2662064.6606 | 1260004.5141
44 | 2662060.4702 | 1260036.1257 | 2662055.2012 | 1260025.6397
45 | 2662033.1568 | 1259981.2839 | 2662025.1888 | 1259964.6727
46 | 2662060.4702 | 1260036.1257 | 2662063.8196 | 1260043.0214
47 | 2662017.9919 | 1259949.669 | 2662025.1888 | 1259964.6727
48 | 2661985.6127 | 1259924.7804 | 2661960.8343 | 1259936.2646
49 | 2661957.8338 | 1259937.6553 | 2661960.8343 | 1259936.2646
50 | 2662002.3357 | 1259917.0297 | 2661985.6127 | 1259924.7804
51 | 2661950.6523 | 1259940.9838 | 2661957.8338 | 1259937.6553
52 | 2662002.3357 | 1259917.0297 | 2661993.3282 | 1259898.1896
53 | 2662002.3357 | 1259917.0297 | 2662020.964 | 1259908.2539
54 | 2661950.6523 | 1259940.9838 | 2661954.89 | 1259954.3073
55 | 2661986.3016 | 1259883.4929 | 2661993.3282 | 1259898.1896
56 | 2662020.964 | 1259908.2539 | 2662058.8039 | 1259890.4277
57 | 2661954.89 | 1259954.3073 | 2661959.4982 | 1259968.7956
58 | 2661986.3016 | 1259883.4929 | 2662013.0651 | 1259871.5861
59 | 2661986.3016 | 1259883.4929 | 2661983.7424 | 1259878.1399
60 | 2662076.536 | 1259882.0742 | 2662058.8039 | 1259890.4277
61 | 2661959.4982 | 1259968.7956 | 2661960.6701 | 1259972.48
62 | 2661964.7949 | 1259985.4486 | 2661960.6701 | 1259972.48
63 | 2661965.428 | 1259987.439 | 2661964.7949 | 1259985.4486
64 | 2661965.428 | 1259987.439 | 2661953.9781 | 1259987.812
65 | 2661953.9781 | 1259987.812 | 2661951.4799 | 1259987.8933 | 2661942.7446 | 1259990.7818 | 2661936.7828 | 1259993.935
66 | 2661944.5051 | 1260106.9516 | 2661938.4091 | 1260092.0889
67 | 2661944.5051 | 1260106.9516 | 2661953.0657 | 1260103.4609
68 | 2661953.0657 | 1260103.4609 | 2661977.5174 | 1260091.6888
69 | 2661981.2977 | 1260089.8687 | 2661977.5174 | 1260091.6888
70 | 2661981.2977 | 1260089.8687 | 2661993.1465 | 1260084.0219 | 2662000.5709 | 1260080.3636 | 2662009.0636 | 1260076.1718
71 | 2662009.0636 | 1260076.1718 | 2662039.3271 | 1260061.0371
72 | 2662014.6753 | 1259870.8697 | 2662013.0651 | 1259871.5861
73 | 2661983.7424 | 1259878.1399 | 2661978.9262 | 1259863.1879
74 | 2662086.5636 | 1259877.3502 | 2662076.536 | 1259882.0742
75 | 2662063.8196 | 1260043.0214 | 2662045.628 | 1260057.886 | 2662039.3271 | 1260061.0371
76 | 2662063.8196 | 1260043.0214 | 2662079.645 | 1260026.0568
77 | 2661977.7606 | 1259851.4098 | 2661979.5477 | 1259831.1971
78 | 2661977.7606 | 1259851.4098 | 2661977.5864 | 1259853.3804
79 | 2661980.3296 | 1259822.3529 | 2661979.5477 | 1259831.1971
80 | 2661978.9262 | 1259863.1879 | 2661977.1946 | 1259857.8121 | 2661977.5864 | 1259853.3804
81 | 2661983.445 | 1259787.1149 | 2661980.3296 | 1259822.3529
82 | 2662053.209 | 1259766.2862 | 2662044.8419 | 1259766.3541 | 2662018.0737 | 1259768.8643 | 2661990.6817 | 1259781.2642 | 2661983.445 | 1259787.1149
83 | 2662053.209 | 1259766.2862 | 2662060.1142 | 1259764.7352 | 2662081.4165 | 1259754.4733 | 2662091.8779 | 1259747.8376
84 | 2662052.916 | 1259840.1118 | 2662042.4206 | 1259820.2081
85 | 2662057.9939 | 1259849.7416 | 2662052.916 | 1259840.1118
86 | 2662035.0532 | 1259806.2363 | 2662042.4206 | 1259820.2081
87 | 2662057.9939 | 1259849.7416 | 2662092.5639 | 1259832.0975
88 | 2662057.9939 | 1259849.7416 | 2662045.1745 | 1259857.8264
89 | 2662035.0532 | 1259806.2363 | 2662027.9604 | 1259792.7853 | 2662016.9993 | 1259797.9909
90 | 2662092.5639 | 1259832.0975 | 2662121.586 | 1259817.2849 | 2662136.8841 | 1259814.426
91 | 2662006.1296 | 1259803.1531 | 2662016.9993 | 1259797.9909
92 | 2662136.8841 | 1259814.426 | 2662138.9901 | 1259814.0325
93 | 2662159.8364 | 1259831.6858 | 2662152.2534 | 1259815.2498 | 2662145.8656 | 1259812.7476 | 2662138.9901 | 1259814.0325
94 | 2662251.9374 | 1259891.375 | 2662240.3532 | 1259879.9015
95 | 2662227.0531 | 1259866.7287 | 2662240.3532 | 1259879.9015
96 | 2662251.9374 | 1259891.375 | 2662258.6858 | 1259884.8929
97 | 2662251.9374 | 1259891.375 | 2662222.0286 | 1259920.9741
98 | 2662227.0531 | 1259866.7287 | 2662236.2784 | 1259846.6777
99 | 2662198.2872 | 1259856.3966 | 2662227.0531 | 1259866.7287
100 | 2662263.4942 | 1259880.2743 | 2662258.6858 | 1259884.8929
101 | 2662222.0286 | 1259920.9741 | 2662216.6553 | 1259926.2918
102 | 2662242.4129 | 1259829.5519 | 2662236.2784 | 1259846.6777
103 | 2662236.2784 | 1259846.6777 | 2662244.3324 | 1259846.2621 | 2662262.1808 | 1259836.5227
104 | 2662198.2872 | 1259856.3966 | 2662203.6055 | 1259845.1999 | 2662204.4327 | 1259844.507
105 | 2662198.2872 | 1259856.3966 | 2662191.2403 | 1259853.9227
106 | 2662263.4942 | 1259880.2743 | 2662272.6171 | 1259871.5113 | 2662275.9153 | 1259869.0684
107 | 2662216.6553 | 1259926.2918 | 2662215.6837 | 1259927.2533 | 2662199.0644 | 1259939.3856
108 | 2662327.1873 | 1259937.8674 | 2662295.1435 | 1259955.3355
109 | 2662346.5632 | 1259876.2291 | 2662327.1873 | 1259937.8674
110 | 2662265.5907 | 1259820.1333 | 2662242.4129 | 1259829.5519
111 | 2662242.4129 | 1259829.5519 | 2662245.3572 | 1259821.3296
112 | 2662295.1664 | 1259813.0339 | 2662285.6888 | 1259816.164 | 2662282.736 | 1259825.3063 | 2662262.1808 | 1259836.5227
113 | 2662204.4327 | 1259844.507 | 2662212.1317 | 1259838.0578
114 | 2662191.2403 | 1259853.9227 | 2662180.1928 | 1259850.0443
115 | 2662329.0949 | 1259834.79 | 2662319.4958 | 1259839.5035 | 2662303.952 | 1259848.3019 | 2662275.9153 | 1259869.0684
116 | 2662250.2132 | 1259807.7686 | 2662245.3572 | 1259821.3296
117 | 2662217.0858 | 1259833.9077 | 2662212.1317 | 1259838.0578
118 | 2662161.7841 | 1259843.5816 | 2662180.1928 | 1259850.0443
119 | 2662159.8364 | 1259831.6858 | 2662163.521 | 1259839.6748
120 | 2662173.3548 | 1259825.5344 | 2662159.8364 | 1259831.6858
121 | 2662163.521 | 1259839.6748 | 2662184.3536 | 1259831.1557
122 | 2662163.521 | 1259839.6748 | 2662161.7841 | 1259843.5816
123 | 2662137.7056 | 1259926.5194 | 2662168.3152 | 1259911.5047
124 | 2662111.6446 | 1259939.3029 | 2662137.7056 | 1259926.5194
125 | 2662175.518 | 1259918.0357 | 2662171.6317 | 1259909.8778 | 2662168.3152 | 1259911.5047
126 | 2662111.6446 | 1259939.3029 | 2662114.9652 | 1259947.5104 | 2662114.9652 | 1259947.5104
127 | 2662111.6446 | 1259939.3029 | 2662086.5636 | 1259877.3502
128 | 2662132.9829 | 1259938.8864 | 2662114.9652 | 1259947.5104
129 | 2662086.5636 | 1259877.3502 | 2662092.1789 | 1259874.8293
130 | 2662092.1789 | 1259874.8293 | 2662105.9634 | 1259868.6411
131 | 2662108.2766 | 1259867.6026 | 2662105.9634 | 1259868.6411
132 | 2662329.0949 | 1259834.79 | 2662331.8067 | 1259829.9373 | 2662338.8801 | 1259821.728 | 2662342.9803 | 1259817.8084
133 | 2662329.0949 | 1259834.79 | 2662354.1821 | 1259824.4356 | 2662376.7258 | 1259815.1329 | 2662386.0001 | 1259810.8074
134 | 2662356.2367 | 1259806.7196 | 2662350.3846 | 1259810.73 | 2662342.9803 | 1259817.8084
135 | 2662409.5989 | 1259799.4859 | 2662406.6599 | 1259801.1716 | 2662386.0001 | 1259810.8074
136 | 2662373.8851 | 1259791.5405 | 2662363.5036 | 1259801.7394 | 2662356.2367 | 1259806.7196
137 | 2662429.447 | 1259788.1023 | 2662409.5989 | 1259799.4859
138 | 2662260.0608 | 1259793.4112 | 2662251.7624 | 1259803.4423 | 2662250.2132 | 1259807.7686
139 | 2662260.0608 | 1259793.4112 | 2662252.2731 | 1259776.1356
140 | 2662260.0608 | 1259793.4112 | 2662271.1977 | 1259785.6233
141 | 2662161.7841 | 1259843.5816 | 2662137.3445 | 1259854.5532
142 | 2662108.2766 | 1259867.6026 | 2662137.3445 | 1259854.5532
143 | 2662195.5709 | 1259826.5686 | 2662184.3536 | 1259831.1557
144 | 2662387.5578 | 1259778.1083 | 2662373.8851 | 1259791.5405
145 | 2662429.447 | 1259788.1023 | 2662443.891 | 1259777.5855
146 | 2662429.447 | 1259788.1023 | 2662443.6126 | 1259811.3576 | 2662444.6294 | 1259817.1392
147 | 2662464.2035 | 1259710.0565 | 2662472.7013 | 1259702.1717
148 | 2662464.2035 | 1259710.0565 | 2662460.7375 | 1259712.7997
149 | 2662464.2035 | 1259710.0565 | 2662453.5294 | 1259686.6157 | 2662460.6114 | 1259681.629
150 | 2662456.8326 | 1259743.5587 | 2662467.5747 | 1259736.9895 | 2662460.7375 | 1259712.7997
151 | 2662460.7375 | 1259712.7997 | 2662444.5824 | 1259722.8968
152 | 2662460.6114 | 1259681.629 | 2662474.5794 | 1259671.7936 | 2662474.4956 | 1259668.3124 | 2662476.0867 | 1259667.2142
153 | 2662425.3621 | 1259740.969 | 2662442.3155 | 1259724.3137 | 2662444.5824 | 1259722.8968
154 | 2662492.908 | 1259655.6038 | 2662476.0867 | 1259667.2142
155 | 2662425.3621 | 1259740.969 | 2662418.5808 | 1259747.6309
156 | 2662444.6294 | 1259817.1392 | 2662459.9065 | 1259813.8674
157 | 2662459.9065 | 1259813.8674 | 2662508.3117 | 1259849.8574
158 | 2662444.6294 | 1259817.1392 | 2662443.6465 | 1259823.8559 | 2662440.3772 | 1259830.1038 | 2662439.7393 | 1259830.677
159 | 2662481.2357 | 1259897.9177 | 2662489.8983 | 1259883.4097 | 2662508.3117 | 1259849.8574
160 | 2662508.3117 | 1259849.8574 | 2662539.6792 | 1259865.7225 | 2662539.6792 | 1259865.7225
161 | 2662422.9389 | 1259845.7725 | 2662439.7393 | 1259830.677
162 | 2662477.2956 | 1259904.8923 | 2662478.1743 | 1259903.0447 | 2662481.2357 | 1259897.9177
163 | 2662421.2788 | 1259847.2641 | 2662422.9389 | 1259845.7725
164 | 2662385.7293 | 1259885.4903 | 2662386.5343 | 1259878.4825 | 2662421.2788 | 1259847.2641
165 | 2662387.5578 | 1259778.1083 | 2662395.5802 | 1259770.227
166 | 2662395.5802 | 1259770.227 | 2662403.3028 | 1259762.6402
167 | 2662403.3028 | 1259762.6402 | 2662418.5808 | 1259747.6309
168 | 2662385.7293 | 1259885.4903 | 2662360.5766 | 1259900.6474 | 2662346.5632 | 1259876.2291
169 | 2662477.2956 | 1259904.8923 | 2662485.594 | 1259912.1878
170 | 2662477.2956 | 1259904.8923 | 2662472.1771 | 1259915.6795 | 2662471.1815 | 1259930.0128 | 2662474.8852 | 1259946.1414 | 2662478.8288 | 1259950.9755
171 | 2662478.8288 | 1259950.9755 | 2662455.1822 | 1259976.994
172 | 2662455.1822 | 1259976.994 | 2662441.0711 | 1259963.2626

## bus_geodata
| x | y | coords
0 | 2662488.2572 | 1259763.2598
1 | 2662528.6528 | 1259728.7839
2 | 2662528.9384 | 1259703.1904
3 | 2662579.6229 | 1259721.3615
4 | 2662507.8467 | 1259675.592
5 | 2662568.9854 | 1259767.1705
6 | 2662537.9938 | 1259651.2783
7 | 2662488.4296 | 1259687.5781
8 | 2662557.1283 | 1259882.0342
9 | 2662547.8589 | 1259873.369
10 | 2661830.3605 | 1259853.1155
11 | 2661871.9258 | 1259844.4994
12 | 2661899.3296 | 1259833.9912
13 | 2661935.9834 | 1259899.4111
14 | 2661938.3926 | 1259898.3381
15 | 2661872.5614 | 1259975.7063
16 | 2661875.5148 | 1259974.6275
17 | 2661888.3124 | 1259969.9528
18 | 2661898.7752 | 1259965.4775
19 | 2661905.0397 | 1260010.7241
20 | 2661909.6884 | 1260022.0599
21 | 2661915.6135 | 1260005.1316
22 | 2661917.0889 | 1259956.8307
23 | 2661931.5226 | 1259996.7172
24 | 2661919.3138 | 1259955.7803
25 | 2661949.9415 | 1260039.9633
26 | 2661948.6692 | 1260040.6151
27 | 2661977.6204 | 1260025.7835
28 | 2661935.0092 | 1260047.613
29 | 2661991.0644 | 1260033.8635
30 | 2661975.1464 | 1260018.0028
31 | 2661997.8558 | 1260049.8271
32 | 2661974.0508 | 1260014.5571
33 | 2662022.3649 | 1259994.7899
34 | 2662035.1799 | 1259985.5015
35 | 2662002.5165 | 1260060.7824
36 | 2661969.6028 | 1260000.5685
37 | 2662032.6233 | 1260012.0365
38 | 2662045.654 | 1260006.5488
39 | 2662050.0679 | 1260015.4238
40 | 2662064.6606 | 1260004.5141
41 | 2662055.2012 | 1260025.6397
42 | 2662033.1568 | 1259981.2839
43 | 2662084.8143 | 1259989.4469
44 | 2662060.4702 | 1260036.1257
45 | 2662025.1888 | 1259964.6727
46 | 2661960.8343 | 1259936.2646
47 | 2661985.6127 | 1259924.7804
48 | 2661957.8338 | 1259937.6553
49 | 2662002.3357 | 1259917.0297
50 | 2661950.6523 | 1259940.9838
51 | 2661993.3282 | 1259898.1896
52 | 2662020.964 | 1259908.2539
53 | 2661954.89 | 1259954.3073
54 | 2662017.9919 | 1259949.669
55 | 2661986.3016 | 1259883.4929
56 | 2662058.8039 | 1259890.4277
57 | 2661959.4982 | 1259968.7956
58 | 2661960.6701 | 1259972.48
59 | 2661964.7949 | 1259985.4486
60 | 2661965.428 | 1259987.439
61 | 2661953.9781 | 1259987.812
62 | 2661936.7828 | 1259993.935
63 | 2661938.4091 | 1260092.0889
64 | 2661944.5051 | 1260106.9516
65 | 2661953.0657 | 1260103.4609
66 | 2661977.5174 | 1260091.6888
67 | 2661981.2977 | 1260089.8687
68 | 2662009.0636 | 1260076.1718
69 | 2662013.0651 | 1259871.5861
70 | 2661983.7424 | 1259878.1399
71 | 2662076.536 | 1259882.0742
72 | 2662039.3271 | 1260061.0371
73 | 2662063.8196 | 1260043.0214
74 | 2662079.645 | 1260026.0568
75 | 2661977.7606 | 1259851.4098
76 | 2661979.5477 | 1259831.1971
77 | 2661977.5864 | 1259853.3804
78 | 2661980.3296 | 1259822.3529
79 | 2661978.9262 | 1259863.1879
80 | 2661983.445 | 1259787.1149
81 | 2662053.209 | 1259766.2862
82 | 2662091.8779 | 1259747.8376
83 | 2662014.6753 | 1259870.8697
84 | 2662052.916 | 1259840.1118
85 | 2662042.4206 | 1259820.2081
86 | 2662057.9939 | 1259849.7416
87 | 2662035.0532 | 1259806.2363
88 | 2662092.5639 | 1259832.0974
89 | 2662045.1745 | 1259857.8264
90 | 2662016.9993 | 1259797.9909
91 | 2662136.8841 | 1259814.426
92 | 2662006.1296 | 1259803.1531
93 | 2662138.9901 | 1259814.0325
94 | 2662240.3532 | 1259879.9015
95 | 2662251.9374 | 1259891.375
96 | 2662227.0531 | 1259866.7287
97 | 2662258.6858 | 1259884.8929
98 | 2662222.0286 | 1259920.9741
99 | 2662236.2784 | 1259846.6777
100 | 2662198.2872 | 1259856.3966
101 | 2662263.4941 | 1259880.2743
102 | 2662216.6553 | 1259926.2918
103 | 2662295.1435 | 1259955.3355
104 | 2662327.1873 | 1259937.8674
105 | 2662242.4129 | 1259829.5519
106 | 2662262.1808 | 1259836.5227
107 | 2662204.4327 | 1259844.507
108 | 2662191.2403 | 1259853.9227
109 | 2662275.9153 | 1259869.0684
110 | 2662199.0644 | 1259939.3856
111 | 2662265.5907 | 1259820.1333
112 | 2662245.3572 | 1259821.3296
113 | 2662295.1664 | 1259813.0339
114 | 2662212.1317 | 1259838.0578
115 | 2662180.1928 | 1259850.0443
116 | 2662159.8364 | 1259831.6858
117 | 2662163.521 | 1259839.6748
118 | 2662173.3548 | 1259825.5344
119 | 2662137.7056 | 1259926.5194
120 | 2662168.3152 | 1259911.5047
121 | 2662111.6446 | 1259939.3029
122 | 2662175.518 | 1259918.0357
123 | 2662114.9652 | 1259947.5104
124 | 2662086.5636 | 1259877.3502
125 | 2662132.9829 | 1259938.8864
126 | 2662092.1789 | 1259874.8293
127 | 2662105.9634 | 1259868.6411
128 | 2662329.0949 | 1259834.79
129 | 2662342.9803 | 1259817.8084
130 | 2662386.0001 | 1259810.8074
131 | 2662356.2367 | 1259806.7196
132 | 2662409.5989 | 1259799.4859
133 | 2662250.2132 | 1259807.7686
134 | 2662260.0608 | 1259793.4112
135 | 2662252.2731 | 1259776.1356
136 | 2662271.1977 | 1259785.6233
137 | 2662217.0858 | 1259833.9077
138 | 2662161.7841 | 1259843.5816
139 | 2662137.3445 | 1259854.5532
140 | 2662184.3536 | 1259831.1557
141 | 2662108.2766 | 1259867.6026
142 | 2662195.5709 | 1259826.5686
143 | 2662373.8851 | 1259791.5405
144 | 2662429.447 | 1259788.1023
145 | 2662472.7013 | 1259702.1717
146 | 2662464.2035 | 1259710.0565
147 | 2662460.7375 | 1259712.7997
148 | 2662460.6114 | 1259681.629
149 | 2662456.8326 | 1259743.5587
150 | 2662444.5824 | 1259722.8968
151 | 2662476.0867 | 1259667.2142
152 | 2662425.3621 | 1259740.969
153 | 2662492.908 | 1259655.6038
154 | 2662459.9065 | 1259813.8674
155 | 2662444.6294 | 1259817.1392
156 | 2662508.3117 | 1259849.8574
157 | 2662439.7393 | 1259830.677
158 | 2662539.6792 | 1259865.7225
159 | 2662481.2358 | 1259897.9177
160 | 2662422.9389 | 1259845.7725
161 | 2662443.891 | 1259777.5855
162 | 2662421.2788 | 1259847.2641
163 | 2662387.5578 | 1259778.1083
164 | 2662395.5802 | 1259770.227
165 | 2662403.3028 | 1259762.6402
166 | 2662385.7293 | 1259885.4903
167 | 2662485.594 | 1259912.1878
168 | 2662477.2956 | 1259904.8923
169 | 2662478.8288 | 1259950.9755
170 | 2662346.5632 | 1259876.2291
171 | 2662455.1822 | 1259976.994
172 | 2662441.0711 | 1259963.2626
173 | 2662418.5808 | 1259747.6309
174 | 2662175.518 | 1259918.0357

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1