## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4042-4_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4042-4_0_7_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_4042-4_0_7_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4042-4_0_7_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_4042-4_0_7_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_4042-4_0_7_node_111 | 0.4 | n |  | TRUE
6 | bus_LV_4042-4_0_7_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4042-4_0_7_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4042-4_0_7_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_4042-4_0_7_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4042-4_0_7_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4042-4_0_7_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_4042-4_0_7_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_4042-4_0_7_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_4042-4_0_7_node_67 | 0.4 | n |  | TRUE
15 | bus_LV_4042-4_0_7_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_4042-4_0_7_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_4042-4_0_7_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_4042-4_0_7_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_4042-4_0_7_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_4042-4_0_7_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_4042-4_0_7_node_34 | 0.4 | n |  | TRUE
22 | bus_LV_4042-4_0_7_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_4042-4_0_7_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_4042-4_0_7_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_4042-4_0_7_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_4042-4_0_7_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_4042-4_0_7_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_4042-4_0_7_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_4042-4_0_7_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_4042-4_0_7_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_4042-4_0_7_node_45 | 0.4 | n |  | TRUE
32 | bus_LV_4042-4_0_7_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_4042-4_0_7_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_4042-4_0_7_node_22 | 0.4 | n |  | TRUE
35 | bus_LV_4042-4_0_7_node_63 | 0.4 | n |  | TRUE
36 | bus_LV_4042-4_0_7_node_64 | 0.4 | n |  | TRUE
37 | bus_LV_4042-4_0_7_node_53 | 0.4 | n |  | TRUE
38 | bus_LV_4042-4_0_7_node_65 | 0.4 | n |  | TRUE
39 | bus_LV_4042-4_0_7_node_39 | 0.4 | n |  | TRUE
40 | bus_LV_4042-4_0_7_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_4042-4_0_7_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_4042-4_0_7_node_94 | 0.4 | n |  | TRUE
43 | bus_LV_4042-4_0_7_node_91 | 0.4 | n |  | TRUE
44 | bus_LV_4042-4_0_7_node_28 | 0.4 | n |  | TRUE
45 | bus_LV_4042-4_0_7_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_4042-4_0_7_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_4042-4_0_7_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_4042-4_0_7_node_90 | 0.4 | n |  | TRUE
49 | bus_LV_4042-4_0_7_node_108 | 0.4 | n |  | TRUE
50 | bus_LV_4042-4_0_7_node_89 | 0.4 | n |  | TRUE
51 | bus_LV_4042-4_0_7_node_96 | 0.4 | n |  | TRUE
52 | bus_LV_4042-4_0_7_node_97 | 0.4 | n |  | TRUE
53 | bus_LV_4042-4_0_7_node_92 | 0.4 | n |  | TRUE
54 | bus_LV_4042-4_0_7_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_4042-4_0_7_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_4042-4_0_7_node_99 | 0.4 | n |  | TRUE
57 | bus_LV_4042-4_0_7_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_4042-4_0_7_node_103 | 0.4 | n |  | TRUE
59 | bus_LV_4042-4_0_7_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_4042-4_0_7_node_59 | 0.4 | n |  | TRUE
61 | bus_LV_4042-4_0_7_node_98 | 0.4 | n |  | TRUE
62 | bus_LV_4042-4_0_7_node_40 | 0.4 | n |  | TRUE
63 | bus_LV_4042-4_0_7_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_4042-4_0_7_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_4042-4_0_7_node_52 | 0.4 | n |  | TRUE
66 | bus_LV_4042-4_0_7_node_43 | 0.4 | n |  | TRUE
67 | bus_LV_4042-4_0_7_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_4042-4_0_7_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_4042-4_0_7_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_4042-4_0_7_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_4042-4_0_7_node_110 | 0.4 | n |  | TRUE
72 | bus_LV_4042-4_0_7_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_4042-4_0_7_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_4042-4_0_7_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_4042-4_0_7_node_51 | 0.4 | n |  | TRUE
76 | bus_LV_4042-4_0_7_node_54 | 0.4 | n |  | TRUE
77 | bus_LV_4042-4_0_7_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_4042-4_0_7_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_4042-4_0_7_node_107 | 0.4 | n |  | TRUE
80 | bus_LV_4042-4_0_7_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_4042-4_0_7_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_4042-4_0_7_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_4042-4_0_7_node_88 | 0.4 | n |  | TRUE
84 | bus_LV_4042-4_0_7_node_101 | 0.4 | n |  | TRUE
85 | bus_LV_4042-4_0_7_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_4042-4_0_7_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_4042-4_0_7_node_106 | 0.4 | n |  | TRUE
88 | bus_LV_4042-4_0_7_node_86 | 0.4 | n |  | TRUE
89 | bus_LV_4042-4_0_7_node_72 | 0.4 | n |  | TRUE
90 | bus_LV_4042-4_0_7_node_73 | 0.4 | n |  | TRUE
91 | bus_LV_4042-4_0_7_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_4042-4_0_7_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_4042-4_0_7_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_4042-4_0_7_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_4042-4_0_7_node_105 | 0.4 | n |  | TRUE
96 | bus_LV_4042-4_0_7_node_104 | 0.4 | n |  | TRUE
97 | bus_LV_4042-4_0_7_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_4042-4_0_7_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_4042-4_0_7_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_4042-4_0_7_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_4042-4_0_7_node_85 | 0.4 | n |  | TRUE
102 | bus_LV_4042-4_0_7_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_4042-4_0_7_node_109 | 0.4 | n |  | TRUE
104 | bus_LV_4042-4_0_7_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_4042-4_0_7_node_84 | 0.4 | n |  | TRUE
106 | bus_LV_4042-4_0_7_node_93 | 0.4 | n |  | TRUE
107 | bus_LV_4042-4_0_7_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_4042-4_0_7_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_4042-4_0_7_node_102 | 0.4 | n |  | TRUE
110 | bus_MV_421_0_node_156 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4042-4_0_7_load_0 | 0 | 0.0016087 | 0.00040317 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4042-4_0_7_load_41 | 4 | 0.007683 | 0.0019255 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4042-4_0_7_load_111 | 5 | 0.00070102 | 0.00017569 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4042-4_0_7_load_4 | 6 | 0.0036136 | 0.00090565 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4042-4_0_7_load_5 | 7 | 0.0020518 | 0.00051423 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4042-4_0_7_load_6 | 8 | 0.0029814 | 0.00074721 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4042-4_0_7_load_7 | 9 | 0.0038462 | 0.00096394 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4042-4_0_7_load_18 | 12 | 0.0010764 | 0.00026978 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4042-4_0_7_load_12 | 13 | 0.0049964 | 0.0012522 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4042-4_0_7_load_67 | 14 | 0.01471 | 0.0036867 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4042-4_0_7_load_47 | 15 | 0.0041794 | 0.0010475 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4042-4_0_7_load_10 | 16 | 0.008697 | 0.0021797 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4042-4_0_7_load_9 | 17 | 0.0096488 | 0.0024182 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4042-4_0_7_load_13 | 19 | 0.0037343 | 0.00093591 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4042-4_0_7_load_14 | 20 | 0.011883 | 0.0029783 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4042-4_0_7_load_25 | 22 | 0.0090698 | 0.0022731 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4042-4_0_7_load_32 | 25 | 0.0045019 | 0.0011283 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4042-4_0_7_load_15 | 26 | 0.0045759 | 0.0011468 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4042-4_0_7_load_16 | 27 | 0.0065393 | 0.0016389 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4042-4_0_7_load_17 | 28 | 0.0018949 | 0.00047491 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4042-4_0_7_load_35 | 29 | 0.0089876 | 0.0022525 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4042-4_0_7_load_36 | 30 | 0.0053502 | 0.0013409 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4042-4_0_7_load_19 | 32 | 0.0089999 | 0.0022556 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4042-4_0_7_load_20 | 33 | 0.011734 | 0.0029407 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4042-4_0_7_load_22 | 34 | 0.0022113 | 0.0005542 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4042-4_0_7_load_63 | 35 | 0.0077883 | 0.0019519 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4042-4_0_7_load_64 | 36 | 0.012288 | 0.0030796 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4042-4_0_7_load_53 | 37 | 0.0093742 | 0.0023494 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4042-4_0_7_load_65 | 38 | 0.0015113 | 0.00037876 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4042-4_0_7_load_39 | 39 | 0.0085166 | 0.0021345 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4042-4_0_7_load_27 | 41 | 0.029432 | 0.0073764 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4042-4_0_7_load_94 | 42 | 0.0025308 | 0.00063427 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4042-4_0_7_load_91 | 43 | 0.0075327 | 0.0018879 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4042-4_0_7_load_29 | 45 | 0.0078524 | 0.001968 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4042-4_0_7_load_108 | 49 | 0.002936 | 0.00073583 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4042-4_0_7_load_89 | 50 | 0.00071103 | 0.0001782 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4042-4_0_7_load_96 | 51 | 0.0040823 | 0.0010231 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4042-4_0_7_load_97 | 52 | 0.0022738 | 0.00056988 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4042-4_0_7_load_92 | 53 | 0.017286 | 0.0043323 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4042-4_0_7_load_38 | 55 | 0.0022711 | 0.0005692 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4042-4_0_7_load_99 | 56 | 0.0096055 | 0.0024074 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4042-4_0_7_load_103 | 58 | 0.0094712 | 0.0023737 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4042-4_0_7_load_48 | 59 | 0.0031814 | 0.00079735 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4042-4_0_7_load_59 | 60 | 0.0036944 | 0.0009259 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4042-4_0_7_load_98 | 61 | 0.0039426 | 0.00098811 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4042-4_0_7_load_40 | 62 | 0.0019878 | 0.00049818 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4042-4_0_7_load_42 | 63 | 0.0029017 | 0.00072725 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4042-4_0_7_load_68 | 64 | 0.0026392 | 0.00066144 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4042-4_0_7_load_52 | 65 | 0.023844 | 0.0059759 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4042-4_0_7_load_43 | 66 | 0.0024793 | 0.00062138 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4042-4_0_7_load_44 | 67 | 0.0028505 | 0.00071441 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4042-4_0_7_load_57 | 69 | 0.001903 | 0.00047693 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4042-4_0_7_load_55 | 70 | 0.03792 | 0.0095036 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4042-4_0_7_load_56 | 72 | 0.0046023 | 0.0011534 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4042-4_0_7_load_49 | 73 | 0.010093 | 0.0025296 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4042-4_0_7_load_50 | 74 | 0.011572 | 0.0029001 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4042-4_0_7_load_54 | 76 | 0.0079636 | 0.0019959 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4042-4_0_7_load_70 | 77 | 0.0092373 | 0.0023151 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4042-4_0_7_load_107 | 79 | 0.0169 | 0.0042355 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4042-4_0_7_load_58 | 80 | 0.028724 | 0.007199 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4042-4_0_7_load_60 | 81 | 0.0072679 | 0.0018215 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4042-4_0_7_load_62 | 82 | 0.0085877 | 0.0021523 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4042-4_0_7_load_88 | 83 | 0.0081622 | 0.0020456 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4042-4_0_7_load_101 | 84 | 0.0053699 | 0.0013458 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4042-4_0_7_load_87 | 85 | 0.002748 | 0.00068871 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4042-4_0_7_load_71 | 86 | 0.0096294 | 0.0024134 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4042-4_0_7_load_86 | 88 | 0.019849 | 0.0049746 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4042-4_0_7_load_72 | 89 | 0.0027314 | 0.00068455 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4042-4_0_7_load_73 | 90 | 0.0061743 | 0.0015474 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4042-4_0_7_load_75 | 92 | 0.0050127 | 0.0012563 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4042-4_0_7_load_76 | 93 | 0.0012455 | 0.00031216 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4042-4_0_7_load_105 | 95 | 0.0011701 | 0.00029327 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4042-4_0_7_load_104 | 96 | 0.0012985 | 0.00032543 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4042-4_0_7_load_78 | 97 | 0.0013826 | 0.00034652 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4042-4_0_7_load_80 | 99 | 0.0011579 | 0.00029021 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4042-4_0_7_load_85 | 101 | 0.0019288 | 0.0004834 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4042-4_0_7_load_83 | 102 | 0.0013602 | 0.0003409 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4042-4_0_7_load_109 | 103 | 0.0014987 | 0.00037561 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4042-4_0_7_load_82 | 104 | 0.0019833 | 0.00049705 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4042-4_0_7_load_84 | 105 | 0.0017635 | 0.00044198 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4042-4_0_7_load_93 | 106 | 0.012616 | 0.0031619 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4042-4_0_7_load_95 | 107 | 0.0047762 | 0.001197 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4042-4_0_7_load_102 | 109 | 0.0055001 | 0.0013784 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 10 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4042-4_0_7_line_0 |  | 0 | 1 | 0.0043413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4042-4_0_7_line_1 |  | 1 | 2 | 0.015577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4042-4_0_7_line_2 |  | 2 | 5 | 0.014541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4042-4_0_7_line_3 |  | 3 | 4 | 0.011968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4042-4_0_7_line_4 |  | 3 | 5 | 0.054965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4042-4_0_7_line_5 |  | 4 | 39 | 0.0094461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4042-4_0_7_line_6 |  | 6 | 7 | 0.022884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_4042-4_0_7_line_7 |  | 6 | 8 | 0.00088736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_4042-4_0_7_line_8 |  | 7 | 9 | 0.0034913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_4042-4_0_7_line_9 |  | 8 | 10 | 0.017351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_4042-4_0_7_line_10 |  | 9 | 11 | 0.024898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_4042-4_0_7_line_11 |  | 10 | 12 | 0.026225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4042-4_0_7_line_12 |  | 10 | 13 | 0.0075556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_4042-4_0_7_line_13 |  | 11 | 14 | 0.010193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_4042-4_0_7_line_14 |  | 12 | 15 | 0.001724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4042-4_0_7_line_15 |  | 13 | 16 | 0.038711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_4042-4_0_7_line_16 |  | 14 | 78 | 0.013082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_4042-4_0_7_line_17 |  | 15 | 31 | 0.019073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4042-4_0_7_line_18 |  | 16 | 17 | 0.0051998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_4042-4_0_7_line_19 |  | 17 | 18 | 0.016144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_4042-4_0_7_line_20 |  | 18 | 19 | 0.013006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4042-4_0_7_line_21 |  | 18 | 20 | 0.024886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_4042-4_0_7_line_22 |  | 20 | 21 | 0.024595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_4042-4_0_7_line_23 |  | 21 | 24 | 0.026622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4042-4_0_7_line_24 |  | 21 | 25 | 0.012526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_4042-4_0_7_line_25 |  | 22 | 23 | 0.026285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4042-4_0_7_line_26 |  | 23 | 40 | 0.024155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_4042-4_0_7_line_27 |  | 23 | 41 | 0.02486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_4042-4_0_7_line_28 |  | 24 | 36 | 0.019834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4042-4_0_7_line_29 |  | 25 | 46 | 0.020937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_4042-4_0_7_line_30 |  | 26 | 27 | 0.019368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4042-4_0_7_line_31 |  | 27 | 28 | 0.0053432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4042-4_0_7_line_32 |  | 28 | 29 | 0.014349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4042-4_0_7_line_33 |  | 29 | 30 | 0.019362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4042-4_0_7_line_34 |  | 30 | 54 | 0.017495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_4042-4_0_7_line_35 |  | 30 | 55 | 0.016611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_4042-4_0_7_line_36 |  | 31 | 66 | 0.0092162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4042-4_0_7_line_37 |  | 32 | 33 | 0.0045767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4042-4_0_7_line_38 |  | 33 | 34 | 0.018814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4042-4_0_7_line_39 |  | 34 | 35 | 0.024144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4042-4_0_7_line_40 |  | 35 | 37 | 0.021677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4042-4_0_7_line_41 |  | 36 | 38 | 0.030593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4042-4_0_7_line_42 |  | 37 | 75 | 0.01529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4042-4_0_7_line_43 |  | 39 | 62 | 0.015853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4042-4_0_7_line_44 |  | 40 | 42 | 0.0048021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_4042-4_0_7_line_45 |  | 40 | 43 | 0.015309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4042-4_0_7_line_46 |  | 41 | 44 | 0.025133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_4042-4_0_7_line_47 |  | 42 | 52 | 0.0043752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_4042-4_0_7_line_48 |  | 43 | 53 | 0.022345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4042-4_0_7_line_49 |  | 44 | 45 | 0.042642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_4042-4_0_7_line_50 |  | 45 | 46 | 0.004051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_4042-4_0_7_line_51 |  | 47 | 48 | 0.047482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4042-4_0_7_line_52 |  | 47 | 49 | 0.0096213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4042-4_0_7_line_53 |  | 48 | 50 | 0.014939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4042-4_0_7_line_54 |  | 49 | 51 | 0.0018716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4042-4_0_7_line_55 |  | 51 | 107 | 0.011159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4042-4_0_7_line_56 |  | 52 | 55 | 0.0074163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
57 | LV_4042-4_0_7_line_57 |  | 53 | 106 | 0.0092311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4042-4_0_7_line_58 |  | 54 | 56 | 0.012224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_4042-4_0_7_line_59 |  | 56 | 61 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_4042-4_0_7_line_60 |  | 57 | 58 | 0.022001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
61 | LV_4042-4_0_7_line_61 |  | 57 | 59 | 0.015975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4042-4_0_7_line_62 |  | 57 | 60 | 0.039761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_4042-4_0_7_line_63 |  | 58 | 84 | 0.0058945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_4042-4_0_7_line_64 |  | 60 | 80 | 0.012495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_4042-4_0_7_line_65 |  | 61 | 108 | 0.0082031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_4042-4_0_7_line_66 |  | 62 | 63 | 0.0079747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4042-4_0_7_line_67 |  | 63 | 64 | 0.004593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4042-4_0_7_line_68 |  | 64 | 65 | 0.0058493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4042-4_0_7_line_69 |  | 65 | 74 | 0.0087833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4042-4_0_7_line_70 |  | 67 | 68 | 0.0057093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4042-4_0_7_line_71 |  | 68 | 69 | 0.0079635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4042-4_0_7_line_72 |  | 68 | 70 | 0.062972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4042-4_0_7_line_73 |  | 69 | 71 | 0.01155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4042-4_0_7_line_74 |  | 70 | 72 | 0.0096207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4042-4_0_7_line_75 |  | 71 | 79 | 0.022166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4042-4_0_7_line_76 |  | 73 | 74 | 0.0079853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4042-4_0_7_line_77 |  | 73 | 75 | 0.010307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4042-4_0_7_line_78 |  | 75 | 76 | 0.0083792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4042-4_0_7_line_79 |  | 76 | 77 | 0.0164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4042-4_0_7_line_80 |  | 77 | 78 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4042-4_0_7_line_81 |  | 78 | 86 | 0.0037531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4042-4_0_7_line_82 |  | 79 | 87 | 0.027025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4042-4_0_7_line_83 |  | 80 | 81 | 0.0086786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_4042-4_0_7_line_84 |  | 81 | 82 | 0.02661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_4042-4_0_7_line_85 |  | 82 | 83 | 0.010466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_4042-4_0_7_line_86 |  | 83 | 85 | 0.013382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_4042-4_0_7_line_87 |  | 84 | 108 | 0.013007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_4042-4_0_7_line_88 |  | 85 | 93 | 0.022469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_4042-4_0_7_line_89 |  | 86 | 87 | 0.012801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4042-4_0_7_line_90 |  | 87 | 88 | 0.0051129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4042-4_0_7_line_91 |  | 88 | 101 | 0.083533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4042-4_0_7_line_92 |  | 89 | 90 | 0.028895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4042-4_0_7_line_93 |  | 89 | 91 | 0.014591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4042-4_0_7_line_94 |  | 90 | 92 | 0.029755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4042-4_0_7_line_95 |  | 91 | 93 | 0.0098764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4042-4_0_7_line_96 |  | 91 | 94 | 0.037298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4042-4_0_7_line_97 |  | 94 | 95 | 0.066226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4042-4_0_7_line_98 |  | 94 | 96 | 0.010595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4042-4_0_7_line_99 |  | 97 | 98 | 0.04589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4042-4_0_7_line_100 |  | 98 | 99 | 0.040418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4042-4_0_7_line_101 |  | 98 | 100 | 0.006018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4042-4_0_7_line_102 |  | 99 | 101 | 0.049935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4042-4_0_7_line_103 |  | 100 | 102 | 0.021885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4042-4_0_7_line_104 |  | 100 | 103 | 0.024117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4042-4_0_7_line_105 |  | 102 | 104 | 0.020496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4042-4_0_7_line_106 |  | 104 | 105 | 0.0035038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4042-4_0_7_line_107 |  | 106 | 107 | 0.0086982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4042-4_0_7_line_108 |  | 108 | 109 | 0.057978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4042-4_0_7_trafo_8 | 0.63 MVA 20/0.4 kV | 110 | 10 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2661367.8841 | 1260447.5496 | 2661370.9362 | 1260446.1135 | 2661371.8126 | 1260445.7018
1 | 2661367.8841 | 1260447.5496 | 2661374.4978 | 1260461.6618
2 | 2661374.4978 | 1260461.6618 | 2661372.4229 | 1260462.6188 | 2661362.2454 | 1260467.3167 | 2661361.2987 | 1260467.7627
3 | 2661357.3236 | 1260522.5838 | 2661346.048 | 1260526.5962
4 | 2661357.3236 | 1260522.5838 | 2661361.2987 | 1260467.7627
5 | 2661337.1486 | 1260529.763 | 2661346.048 | 1260526.5962
6 | 2661243.3097 | 1260634.2493 | 2661243.8739 | 1260611.3725
7 | 2661243.3097 | 1260634.2493 | 2661243.2878 | 1260635.1364
8 | 2661243.8739 | 1260611.3725 | 2661243.96 | 1260607.8823
9 | 2661242.8601 | 1260652.482 | 2661243.2878 | 1260635.1364
10 | 2661242.1998 | 1260583.0579 | 2661244.0162 | 1260605.6042 | 2661243.96 | 1260607.8823
11 | 2661242.8601 | 1260652.482 | 2661217.2248 | 1260646.95
12 | 2661242.8601 | 1260652.482 | 2661250.1828 | 1260654.3435
13 | 2661242.1998 | 1260583.0579 | 2661241.7309 | 1260572.8757
14 | 2661215.5396 | 1260646.5863 | 2661217.2248 | 1260646.95
15 | 2661286.2054 | 1260650.0485 | 2661275.1684 | 1260647.9909 | 2661270.9904 | 1260649.7378 | 2661266.9446 | 1260653.9991 | 2661259.0962 | 1260655.7858 | 2661250.3838 | 1260654.3946 | 2661250.1828 | 1260654.3435
16 | 2661241.1292 | 1260559.8076 | 2661241.7309 | 1260572.8757
17 | 2661196.9895 | 1260642.1556 | 2661213.3094 | 1260646.105 | 2661215.5396 | 1260646.5863
18 | 2661291.3171 | 1260651.0015 | 2661286.2054 | 1260650.0485
19 | 2661307.1875 | 1260653.9602 | 2661291.3171 | 1260651.0015
20 | 2661307.1875 | 1260653.9602 | 2661305.2675 | 1260666.8234
21 | 2661307.1875 | 1260653.9602 | 2661331.7843 | 1260657.7439
22 | 2661356.0938 | 1260661.4835 | 2661331.7843 | 1260657.7439
23 | 2661358.8553 | 1260635.015 | 2661358.5063 | 1260641.0492 | 2661356.0938 | 1260661.4835
24 | 2661356.0938 | 1260661.4835 | 2661354.8192 | 1260673.9446
25 | 2661298.9762 | 1260743.8407 | 2661298.8421 | 1260735.689 | 2661300.9811 | 1260717.6839
26 | 2661279.2718 | 1260757.4578 | 2661290.6147 | 1260751.5153 | 2661294.4112 | 1260748.0299 | 2661298.9762 | 1260743.8407
27 | 2661298.9762 | 1260743.8407 | 2661323.8041 | 1260742.5832
28 | 2661358.8553 | 1260635.015 | 2661339.4159 | 1260631.0804
29 | 2661352.6888 | 1260694.7725 | 2661354.8192 | 1260673.9446
30 | 2661252.4342 | 1260710.7756 | 2661254.9037 | 1260691.5657
31 | 2661252.4342 | 1260710.7756 | 2661251.7529 | 1260716.0751
32 | 2661249.9233 | 1260730.3074 | 2661251.7529 | 1260716.0751
33 | 2661247.4546 | 1260749.5115 | 2661249.9233 | 1260730.3074
34 | 2661247.4546 | 1260749.5115 | 2661230.7424 | 1260744.1792
35 | 2661247.4546 | 1260749.5115 | 2661263.2818 | 1260754.5527
36 | 2661196.9895 | 1260642.1556 | 2661195.3476 | 1260633.0868
37 | 2661344.181 | 1260583.9363 | 2661339.6413 | 1260583.3556
38 | 2661320.9791 | 1260580.9687 | 2661339.6413 | 1260583.3556
39 | 2661297.0302 | 1260577.9055 | 2661320.9791 | 1260580.9687
40 | 2661282.756 | 1260565.2358 | 2661284.4497 | 1260572.6542 | 2661290.5458 | 1260577.0761 | 2661297.0302 | 1260577.9055
41 | 2661314.7022 | 1260620.4024 | 2661314.4143 | 1260624.1799 | 2661315.3128 | 1260626.2018 | 2661339.4159 | 1260631.0804
42 | 2661279.3529 | 1260550.3296 | 2661282.756 | 1260565.2358
43 | 2661337.1486 | 1260529.763 | 2661322.213 | 1260535.0778
44 | 2661279.2718 | 1260757.4578 | 2661274.5172 | 1260758.1313 | 2661274.5172 | 1260758.1313
45 | 2661279.2718 | 1260757.4578 | 2661291.9487 | 1260766.0397
46 | 2661348.9054 | 1260741.3118 | 2661323.8041 | 1260742.5832
47 | 2661270.3484 | 1260756.8035 | 2661274.5172 | 1260758.1313
48 | 2661291.9487 | 1260766.0397 | 2661313.9668 | 1260769.8483
49 | 2661348.9054 | 1260741.3118 | 2661350.5815 | 1260722.1151 | 2661352.3776 | 1260698.8115
50 | 2661352.6888 | 1260694.7725 | 2661352.3776 | 1260698.8115
51 | 2661344.9947 | 1260779.7771 | 2661338.4932 | 1260826.8107
52 | 2661344.9947 | 1260779.7771 | 2661335.3758 | 1260779.5613
53 | 2661338.4932 | 1260826.8107 | 2661323.5541 | 1260826.8213
54 | 2661333.5047 | 1260779.5194 | 2661335.3758 | 1260779.5613
55 | 2661322.3486 | 1260779.2691 | 2661333.5047 | 1260779.5194
56 | 2661263.2818 | 1260754.5527 | 2661270.3484 | 1260756.8035
57 | 2661313.6527 | 1260779.0741 | 2661313.9668 | 1260769.8483 | 2661313.9668 | 1260769.8483
58 | 2661230.7424 | 1260744.1792 | 2661218.7009 | 1260742.0761
59 | 2661202.2797 | 1260739.208 | 2661218.7009 | 1260742.0761
60 | 2661213.0377 | 1260704.4003 | 2661201.1616 | 1260715.2632 | 2661196.631 | 1260719.0525
61 | 2661213.0377 | 1260704.4003 | 2661206.5815 | 1260689.7875
62 | 2661213.0377 | 1260704.4003 | 2661193.7492 | 1260703.3223 | 2661175.2834 | 1260694.5534
63 | 2661196.631 | 1260719.0525 | 2661196.631 | 1260719.0525 | 2661195.8725 | 1260724.898
64 | 2661163.9968 | 1260689.1938 | 2661175.2834 | 1260694.5534
65 | 2661194.1988 | 1260737.7966 | 2661202.2797 | 1260739.208
66 | 2661314.6998 | 1260537.7514 | 2661322.213 | 1260535.0778
67 | 2661310.3726 | 1260539.2913 | 2661314.6998 | 1260537.7514
68 | 2661310.3726 | 1260539.2913 | 2661304.8618 | 1260541.2523
69 | 2661304.8618 | 1260541.2523 | 2661296.5868 | 1260544.1969
70 | 2661187.8385 | 1260595.0155 | 2661189.1505 | 1260600.572
71 | 2661187.8385 | 1260595.0155 | 2661185.7375 | 1260587.3342
72 | 2661187.8385 | 1260595.0155 | 2661153.919 | 1260594.2311 | 2661153.0435 | 1260623.2614
73 | 2661182.6901 | 1260576.193 | 2661185.7375 | 1260587.3342
74 | 2661153.0435 | 1260623.2614 | 2661152.7535 | 1260632.8778
75 | 2661182.6901 | 1260576.193 | 2661194.9999 | 1260574.419 | 2661204.6458 | 1260573.1461
76 | 2661289.0636 | 1260546.8741 | 2661296.5868 | 1260544.1969
77 | 2661279.3529 | 1260550.3296 | 2661289.0636 | 1260546.8741
78 | 2661279.3529 | 1260550.3296 | 2661271.22 | 1260552.3463
79 | 2661271.22 | 1260552.3463 | 2661255.3021 | 1260556.2933
80 | 2661241.1292 | 1260559.8076 | 2661255.3021 | 1260556.2933
81 | 2661241.1292 | 1260559.8076 | 2661237.4176 | 1260560.3641
82 | 2661224.7579 | 1260562.2623 | 2661224.72 | 1260567.3767 | 2661224.0626 | 1260569.0044 | 2661222.4515 | 1260570.2998 | 2661220.6277 | 1260571.037 | 2661204.6458 | 1260573.1461
83 | 2661163.9968 | 1260689.1938 | 2661156.1572 | 1260685.471
84 | 2661156.1572 | 1260685.471 | 2661141.2325 | 1260678.3836 | 2661132.3853 | 1260674.0002 | 2661132.192 | 1260673.9066
85 | 2661132.192 | 1260673.9066 | 2661122.7717 | 1260669.3469
86 | 2661110.7267 | 1260663.5167 | 2661122.7717 | 1260669.3469
87 | 2661194.1988 | 1260737.7966 | 2661195.8725 | 1260724.898
88 | 2661110.7267 | 1260663.5167 | 2661090.5025 | 1260653.7276
89 | 2661224.7579 | 1260562.2623 | 2661237.4176 | 1260560.3641
90 | 2661224.7579 | 1260562.2623 | 2661219.6895 | 1260562.9357
91 | 2661137.0753 | 1260575.0902 | 2661141.0739 | 1260574.1615 | 2661156.5901 | 1260571.3197 | 2661219.6895 | 1260562.9357
92 | 2661088.9713 | 1260636.8257 | 2661092.3608 | 1260631.0222 | 2661100.4522 | 1260619.5752 | 2661105.5558 | 1260613.2135
93 | 2661081.6127 | 1260649.4247 | 2661088.9713 | 1260636.8257
94 | 2661105.5558 | 1260613.2135 | 2661111.148 | 1260606.2425 | 2661124.5006 | 1260590.2704
95 | 2661081.6127 | 1260649.4247 | 2661090.5025 | 1260653.7276
96 | 2661079.596 | 1260682.706 | 2661075.2508 | 1260678.0355 | 2661073.3859 | 1260673.9911 | 2661072.8519 | 1260669.5157 | 2661074.0814 | 1260665.0251 | 2661081.6127 | 1260649.4247
97 | 2661079.596 | 1260682.706 | 2661074.8351 | 1260683.9911 | 2661035.5171 | 1260668.1851 | 2661017.2583 | 1260663.2326
98 | 2661079.596 | 1260682.706 | 2661089.0468 | 1260687.4943
99 | 2661050.122 | 1260599.5412 | 2661052.1649 | 1260604.5993 | 2661071.905 | 1260601.3784 | 2661082.4074 | 1260602.3986 | 2661083.2914 | 1260612.2413
100 | 2661050.122 | 1260599.5412 | 2661063.4619 | 1260595.7983 | 2661088.8762 | 1260588.0709
101 | 2661044.2304 | 1260600.8481 | 2661050.122 | 1260599.5412
102 | 2661088.8762 | 1260588.0709 | 2661100.5279 | 1260584.5282 | 2661120.0806 | 1260579.0371 | 2661137.0753 | 1260575.0902
103 | 2661044.2304 | 1260600.8481 | 2661046.0951 | 1260622.6534
104 | 2661044.2304 | 1260600.8481 | 2661020.6296 | 1260605.8127
105 | 2661050.4249 | 1260642.3742 | 2661047.2026 | 1260635.6041 | 2661046.0951 | 1260622.6534
106 | 2661051.9307 | 1260645.5379 | 2661050.4249 | 1260642.3742
107 | 2661313.6527 | 1260779.0741 | 2661313.6527 | 1260779.0741 | 2661322.3486 | 1260779.2691
108 | 2661194.1988 | 1260737.7966 | 2661172.2555 | 1260729.6527 | 2661141.416 | 1260714.0276

## bus_geodata
| x | y | coords
0 | 2661371.8126 | 1260445.7018
1 | 2661367.8841 | 1260447.5496
2 | 2661374.4978 | 1260461.6618
3 | 2661357.3236 | 1260522.5838
4 | 2661346.048 | 1260526.5962
5 | 2661361.2987 | 1260467.7627
6 | 2661243.3097 | 1260634.2493
7 | 2661243.8739 | 1260611.3725
8 | 2661243.2878 | 1260635.1364
9 | 2661243.96 | 1260607.8823
10 | 2661242.8601 | 1260652.482
11 | 2661242.1998 | 1260583.0579
12 | 2661217.2248 | 1260646.95
13 | 2661250.1828 | 1260654.3435
14 | 2661241.7309 | 1260572.8757
15 | 2661215.5396 | 1260646.5863
16 | 2661286.2054 | 1260650.0485
17 | 2661291.3171 | 1260651.0015
18 | 2661307.1875 | 1260653.9602
19 | 2661305.2675 | 1260666.8234
20 | 2661331.7843 | 1260657.7439
21 | 2661356.0938 | 1260661.4835
22 | 2661300.9811 | 1260717.6839
23 | 2661298.9762 | 1260743.8407
24 | 2661358.8553 | 1260635.015
25 | 2661354.8192 | 1260673.9446
26 | 2661254.9037 | 1260691.5657
27 | 2661252.4342 | 1260710.7756
28 | 2661251.7529 | 1260716.0751
29 | 2661249.9233 | 1260730.3074
30 | 2661247.4546 | 1260749.5115
31 | 2661196.9895 | 1260642.1556
32 | 2661344.181 | 1260583.9363
33 | 2661339.6413 | 1260583.3556
34 | 2661320.9791 | 1260580.9687
35 | 2661297.0302 | 1260577.9055
36 | 2661339.4159 | 1260631.0804
37 | 2661282.756 | 1260565.2358
38 | 2661314.7022 | 1260620.4024
39 | 2661337.1486 | 1260529.763
40 | 2661279.2718 | 1260757.4578
41 | 2661323.8041 | 1260742.5832
42 | 2661274.5172 | 1260758.1313
43 | 2661291.9487 | 1260766.0397
44 | 2661348.9054 | 1260741.3118
45 | 2661352.3776 | 1260698.8115
46 | 2661352.6888 | 1260694.7725
47 | 2661344.9947 | 1260779.7771
48 | 2661338.4932 | 1260826.8107
49 | 2661335.3758 | 1260779.5613
50 | 2661323.5541 | 1260826.8213
51 | 2661333.5047 | 1260779.5194
52 | 2661270.3484 | 1260756.8035
53 | 2661313.9668 | 1260769.8483
54 | 2661230.7424 | 1260744.1792
55 | 2661263.2819 | 1260754.5527
56 | 2661218.7009 | 1260742.0761
57 | 2661213.0377 | 1260704.4003
58 | 2661196.631 | 1260719.0525
59 | 2661206.5815 | 1260689.7875
60 | 2661175.2834 | 1260694.5534
61 | 2661202.2797 | 1260739.208
62 | 2661322.213 | 1260535.0778
63 | 2661314.6998 | 1260537.7514
64 | 2661310.3726 | 1260539.2913
65 | 2661304.8618 | 1260541.2523
66 | 2661195.3476 | 1260633.0868
67 | 2661189.1505 | 1260600.572
68 | 2661187.8385 | 1260595.0155
69 | 2661185.7375 | 1260587.3342
70 | 2661153.0435 | 1260623.2614
71 | 2661182.6901 | 1260576.193
72 | 2661152.7535 | 1260632.8778
73 | 2661289.0636 | 1260546.8741
74 | 2661296.5868 | 1260544.1969
75 | 2661279.3529 | 1260550.3296
76 | 2661271.22 | 1260552.3463
77 | 2661255.3021 | 1260556.2933
78 | 2661241.1292 | 1260559.8076
79 | 2661204.6458 | 1260573.1461
80 | 2661163.9968 | 1260689.1938
81 | 2661156.1572 | 1260685.471
82 | 2661132.192 | 1260673.9066
83 | 2661122.7717 | 1260669.3469
84 | 2661195.8725 | 1260724.898
85 | 2661110.7267 | 1260663.5167
86 | 2661237.4176 | 1260560.3641
87 | 2661224.7579 | 1260562.2623
88 | 2661219.6895 | 1260562.9357
89 | 2661088.9713 | 1260636.8257
90 | 2661105.5558 | 1260613.2135
91 | 2661081.6127 | 1260649.4247
92 | 2661124.5006 | 1260590.2704
93 | 2661090.5025 | 1260653.7276
94 | 2661079.596 | 1260682.706
95 | 2661017.2583 | 1260663.2326
96 | 2661089.0468 | 1260687.4943
97 | 2661083.2914 | 1260612.2413
98 | 2661050.122 | 1260599.5412
99 | 2661088.8762 | 1260588.0709
100 | 2661044.2304 | 1260600.8481
101 | 2661137.0753 | 1260575.0902
102 | 2661046.0951 | 1260622.6534
103 | 2661020.6296 | 1260605.8127
104 | 2661050.4249 | 1260642.3742
105 | 2661051.9307 | 1260645.5379
106 | 2661313.6527 | 1260779.0741
107 | 2661322.3486 | 1260779.2691
108 | 2661194.1988 | 1260737.7966
109 | 2661141.416 | 1260714.0276
110 | 2661196.9895 | 1260642.1556

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1