## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4048-8_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4048-8_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4048-8_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4048-8_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4048-8_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4048-8_0_7_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4048-8_0_7_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4048-8_0_7_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_4048-8_0_7_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_4048-8_0_7_node_131 | 0.4 | n |  | TRUE
10 | bus_LV_4048-8_0_7_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4048-8_0_7_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_4048-8_0_7_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_4048-8_0_7_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_4048-8_0_7_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_4048-8_0_7_node_129 | 0.4 | n |  | TRUE
16 | bus_LV_4048-8_0_7_node_130 | 0.4 | n |  | TRUE
17 | bus_LV_4048-8_0_7_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_4048-8_0_7_node_42 | 0.4 | n |  | TRUE
19 | bus_LV_4048-8_0_7_node_43 | 0.4 | n |  | TRUE
20 | bus_LV_4048-8_0_7_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_4048-8_0_7_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_4048-8_0_7_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_4048-8_0_7_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_4048-8_0_7_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_4048-8_0_7_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_4048-8_0_7_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_4048-8_0_7_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_4048-8_0_7_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_4048-8_0_7_node_45 | 0.4 | n |  | TRUE
30 | bus_LV_4048-8_0_7_node_46 | 0.4 | n |  | TRUE
31 | bus_LV_4048-8_0_7_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_4048-8_0_7_node_52 | 0.4 | n |  | TRUE
33 | bus_LV_4048-8_0_7_node_54 | 0.4 | n |  | TRUE
34 | bus_LV_4048-8_0_7_node_128 | 0.4 | n |  | TRUE
35 | bus_LV_4048-8_0_7_node_126 | 0.4 | n |  | TRUE
36 | bus_LV_4048-8_0_7_node_127 | 0.4 | n |  | TRUE
37 | bus_LV_4048-8_0_7_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_4048-8_0_7_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_4048-8_0_7_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_4048-8_0_7_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_4048-8_0_7_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_4048-8_0_7_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_4048-8_0_7_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_4048-8_0_7_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_4048-8_0_7_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_4048-8_0_7_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_4048-8_0_7_node_36 | 0.4 | n |  | TRUE
48 | bus_LV_4048-8_0_7_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_4048-8_0_7_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_4048-8_0_7_node_103 | 0.4 | n |  | TRUE
51 | bus_LV_4048-8_0_7_node_56 | 0.4 | n |  | TRUE
52 | bus_LV_4048-8_0_7_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_4048-8_0_7_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_4048-8_0_7_node_102 | 0.4 | n |  | TRUE
55 | bus_LV_4048-8_0_7_node_98 | 0.4 | n |  | TRUE
56 | bus_LV_4048-8_0_7_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_4048-8_0_7_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_4048-8_0_7_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_4048-8_0_7_node_48 | 0.4 | n |  | TRUE
60 | bus_LV_4048-8_0_7_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_4048-8_0_7_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_4048-8_0_7_node_51 | 0.4 | n |  | TRUE
63 | bus_LV_4048-8_0_7_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_4048-8_0_7_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_4048-8_0_7_node_87 | 0.4 | n |  | TRUE
66 | bus_LV_4048-8_0_7_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_4048-8_0_7_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_4048-8_0_7_node_80 | 0.4 | n |  | TRUE
69 | bus_LV_4048-8_0_7_node_77 | 0.4 | n |  | TRUE
70 | bus_LV_4048-8_0_7_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_4048-8_0_7_node_73 | 0.4 | n |  | TRUE
72 | bus_LV_4048-8_0_7_node_75 | 0.4 | n |  | TRUE
73 | bus_LV_4048-8_0_7_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_4048-8_0_7_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_4048-8_0_7_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_4048-8_0_7_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_4048-8_0_7_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_4048-8_0_7_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_4048-8_0_7_node_66 | 0.4 | n |  | TRUE
80 | bus_LV_4048-8_0_7_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_4048-8_0_7_node_69 | 0.4 | n |  | TRUE
82 | bus_LV_4048-8_0_7_node_67 | 0.4 | n |  | TRUE
83 | bus_LV_4048-8_0_7_node_91 | 0.4 | n |  | TRUE
84 | bus_LV_4048-8_0_7_node_88 | 0.4 | n |  | TRUE
85 | bus_LV_4048-8_0_7_node_85 | 0.4 | n |  | TRUE
86 | bus_LV_4048-8_0_7_node_94 | 0.4 | n |  | TRUE
87 | bus_LV_4048-8_0_7_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_4048-8_0_7_node_90 | 0.4 | n |  | TRUE
89 | bus_LV_4048-8_0_7_node_92 | 0.4 | n |  | TRUE
90 | bus_LV_4048-8_0_7_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_4048-8_0_7_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_4048-8_0_7_node_104 | 0.4 | n |  | TRUE
93 | bus_LV_4048-8_0_7_node_78 | 0.4 | n |  | TRUE
94 | bus_LV_4048-8_0_7_node_72 | 0.4 | n |  | TRUE
95 | bus_LV_4048-8_0_7_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_4048-8_0_7_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_4048-8_0_7_node_76 | 0.4 | n |  | TRUE
98 | bus_LV_4048-8_0_7_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_4048-8_0_7_node_81 | 0.4 | n |  | TRUE
100 | bus_LV_4048-8_0_7_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_4048-8_0_7_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_4048-8_0_7_node_95 | 0.4 | n |  | TRUE
103 | bus_LV_4048-8_0_7_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_4048-8_0_7_node_96 | 0.4 | n |  | TRUE
105 | bus_LV_4048-8_0_7_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_4048-8_0_7_node_108 | 0.4 | n |  | TRUE
107 | bus_LV_4048-8_0_7_node_117 | 0.4 | n |  | TRUE
108 | bus_LV_4048-8_0_7_node_124 | 0.4 | n |  | TRUE
109 | bus_LV_4048-8_0_7_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_4048-8_0_7_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_4048-8_0_7_node_123 | 0.4 | n |  | TRUE
112 | bus_LV_4048-8_0_7_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_4048-8_0_7_node_125 | 0.4 | n |  | TRUE
114 | bus_LV_4048-8_0_7_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_4048-8_0_7_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_4048-8_0_7_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_4048-8_0_7_node_105 | 0.4 | n |  | TRUE
118 | bus_LV_4048-8_0_7_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_4048-8_0_7_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_4048-8_0_7_node_121 | 0.4 | n |  | TRUE
121 | bus_LV_4048-8_0_7_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_4048-8_0_7_node_115 | 0.4 | n |  | TRUE
123 | bus_LV_4048-8_0_7_node_118 | 0.4 | n |  | TRUE
124 | bus_LV_4048-8_0_7_node_119 | 0.4 | n |  | TRUE
125 | bus_LV_4048-8_0_7_node_120 | 0.4 | n |  | TRUE
126 | bus_MV_519_0_node_155 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4048-8_0_7_load_0 | 0 | 0.0022311 | 0.00055917 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4048-8_0_7_load_3 | 3 | 0.0050954 | 0.001277 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4048-8_0_7_load_4 | 4 | 0.0075939 | 0.0019032 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4048-8_0_7_load_5 | 5 | 0.0052067 | 0.0013049 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4048-8_0_7_load_6 | 6 | 0.0007557 | 0.0001894 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4048-8_0_7_load_7 | 7 | 0.0020258 | 0.00050772 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4048-8_0_7_load_15 | 8 | 0.0024932 | 0.00062484 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4048-8_0_7_load_8 | 10 | 0.0049381 | 0.0012376 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4048-8_0_7_load_14 | 11 | 0.0017613 | 0.00044143 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4048-8_0_7_load_129 | 15 | 0.0020734 | 0.00051964 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4048-8_0_7_load_130 | 16 | 0.0030522 | 0.00076495 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4048-8_0_7_load_9 | 17 | 0.0015612 | 0.00039127 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4048-8_0_7_load_43 | 19 | 0.0032066 | 0.00080365 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4048-8_0_7_load_10 | 20 | 0.003718 | 0.00093182 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4048-8_0_7_load_11 | 21 | 0.0038656 | 0.0009688 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4048-8_0_7_load_12 | 22 | 0.013676 | 0.0034275 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4048-8_0_7_load_13 | 23 | 0.003619 | 0.00090702 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4048-8_0_7_load_17 | 27 | 0.0057259 | 0.001435 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4048-8_0_7_load_18 | 28 | 0.0033042 | 0.00082812 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4048-8_0_7_load_45 | 29 | 0.0044277 | 0.0011097 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4048-8_0_7_load_46 | 30 | 0.0033038 | 0.00082802 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4048-8_0_7_load_53 | 31 | 0.003765 | 0.00094361 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4048-8_0_7_load_54 | 33 | 0.0035101 | 0.00087972 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4048-8_0_7_load_128 | 34 | 0.0014439 | 0.00036188 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4048-8_0_7_load_126 | 35 | 0.0030261 | 0.0007584 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4048-8_0_7_load_127 | 36 | 0.0013934 | 0.00034922 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4048-8_0_7_load_26 | 37 | 0.011244 | 0.0028181 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4048-8_0_7_load_27 | 38 | 0.012448 | 0.0031198 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4048-8_0_7_load_28 | 39 | 0.014675 | 0.0036779 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4048-8_0_7_load_34 | 42 | 0.010644 | 0.0026677 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4048-8_0_7_load_44 | 44 | 0.0038125 | 0.0009555 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4048-8_0_7_load_41 | 45 | 0.018547 | 0.0046484 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4048-8_0_7_load_36 | 47 | 0.010151 | 0.0025441 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4048-8_0_7_load_39 | 49 | 0.013268 | 0.0033253 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4048-8_0_7_load_37 | 52 | 0.011976 | 0.0030014 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4048-8_0_7_load_38 | 53 | 0.01076 | 0.0026967 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4048-8_0_7_load_102 | 54 | 0.012586 | 0.0031543 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4048-8_0_7_load_47 | 57 | 0.0051005 | 0.0012783 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4048-8_0_7_load_55 | 58 | 0.0041296 | 0.001035 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4048-8_0_7_load_48 | 59 | 0.0015062 | 0.0003775 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4048-8_0_7_load_50 | 61 | 0.0015888 | 0.0003982 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4048-8_0_7_load_61 | 63 | 0.00091722 | 0.00022988 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4048-8_0_7_load_58 | 64 | 0.025913 | 0.0064943 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4048-8_0_7_load_87 | 65 | 0.0026469 | 0.00066339 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4048-8_0_7_load_59 | 66 | 0.011656 | 0.0029214 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4048-8_0_7_load_86 | 67 | 0.01074 | 0.0026918 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4048-8_0_7_load_80 | 68 | 0.0053143 | 0.0013319 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4048-8_0_7_load_60 | 70 | 0.015342 | 0.003845 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4048-8_0_7_load_75 | 72 | 0.01217 | 0.0030501 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4048-8_0_7_load_71 | 73 | 0.0060034 | 0.0015046 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4048-8_0_7_load_62 | 74 | 0.0062885 | 0.0015761 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4048-8_0_7_load_65 | 77 | 0.0049877 | 0.00125 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4048-8_0_7_load_91 | 83 | 0.00049306 | 0.00012357 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4048-8_0_7_load_88 | 84 | 0.0091415 | 0.0022911 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4048-8_0_7_load_85 | 85 | 0.0047585 | 0.0011926 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4048-8_0_7_load_94 | 86 | 0.0071308 | 0.0017871 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4048-8_0_7_load_90 | 88 | 0.016396 | 0.0041093 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4048-8_0_7_load_92 | 89 | 0.011209 | 0.0028093 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4048-8_0_7_load_84 | 90 | 0.0028001 | 0.00070178 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4048-8_0_7_load_93 | 91 | 0.00061015 | 0.00015292 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4048-8_0_7_load_104 | 92 | 0.0026387 | 0.00066131 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4048-8_0_7_load_72 | 94 | 0.015621 | 0.0039151 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4048-8_0_7_load_74 | 95 | 0.0037288 | 0.00093453 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4048-8_0_7_load_83 | 96 | 0.0075006 | 0.0018798 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4048-8_0_7_load_76 | 97 | 0.0013023 | 0.00032638 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4048-8_0_7_load_79 | 98 | 0.0050599 | 0.0012681 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4048-8_0_7_load_101 | 101 | 0.011608 | 0.0029092 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4048-8_0_7_load_95 | 102 | 0.018044 | 0.0045224 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4048-8_0_7_load_89 | 103 | 0.00064831 | 0.00016248 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4048-8_0_7_load_108 | 106 | 0.010095 | 0.00253 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4048-8_0_7_load_117 | 107 | 0.0034996 | 0.00087709 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4048-8_0_7_load_124 | 108 | 0.0089266 | 0.0022372 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4048-8_0_7_load_106 | 109 | 0.0072828 | 0.0018253 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4048-8_0_7_load_112 | 110 | 0.0030933 | 0.00077526 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4048-8_0_7_load_116 | 114 | 0.0047864 | 0.0011996 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4048-8_0_7_load_110 | 115 | 0.010563 | 0.0026474 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4048-8_0_7_load_111 | 116 | 0.0022731 | 0.0005697 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4048-8_0_7_load_105 | 117 | 0.0041834 | 0.0010485 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4048-8_0_7_load_107 | 118 | 0.01523 | 0.0038171 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4048-8_0_7_load_122 | 119 | 0.0025196 | 0.00063146 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4048-8_0_7_load_121 | 120 | 0.0029826 | 0.00074751 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4048-8_0_7_load_114 | 121 | 0.0036151 | 0.00090604 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4048-8_0_7_load_115 | 122 | 0.0037997 | 0.00095231 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4048-8_0_7_load_118 | 123 | 0.0022712 | 0.00056922 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4048-8_0_7_load_119 | 124 | 0.0023347 | 0.00058514 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4048-8_0_7_load_120 | 125 | 0.0019162 | 0.00048025 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 56 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4048-8_0_7_line_0 |  | 0 | 1 | 0.026655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4048-8_0_7_line_1 |  | 0 | 2 | 0.017608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4048-8_0_7_line_2 |  | 1 | 3 | 0.012822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_4048-8_0_7_line_3 |  | 1 | 4 | 0.011828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_4048-8_0_7_line_4 |  | 2 | 5 | 0.0061901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4048-8_0_7_line_5 |  | 2 | 6 | 0.014891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4048-8_0_7_line_6 |  | 3 | 7 | 0.018172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_4048-8_0_7_line_7 |  | 4 | 8 | 0.0070053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_4048-8_0_7_line_8 |  | 6 | 9 | 0.034999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4048-8_0_7_line_9 |  | 7 | 10 | 0.0050239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_4048-8_0_7_line_10 |  | 8 | 11 | 0.029114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
11 | LV_4048-8_0_7_line_11 |  | 9 | 15 | 0.00604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4048-8_0_7_line_12 |  | 9 | 16 | 0.024387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4048-8_0_7_line_13 |  | 10 | 17 | 0.017876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
14 | LV_4048-8_0_7_line_14 |  | 11 | 26 | 0.0071092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_4048-8_0_7_line_15 |  | 12 | 13 | 0.03137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4048-8_0_7_line_16 |  | 12 | 14 | 0.023652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4048-8_0_7_line_17 |  | 13 | 15 | 0.023373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4048-8_0_7_line_18 |  | 13 | 34 | 0.01669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4048-8_0_7_line_19 |  | 14 | 35 | 0.020731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4048-8_0_7_line_20 |  | 17 | 18 | 0.0072975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_4048-8_0_7_line_21 |  | 18 | 19 | 0.0027354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
22 | LV_4048-8_0_7_line_22 |  | 19 | 44 | 0.010693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_4048-8_0_7_line_23 |  | 20 | 21 | 0.010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4048-8_0_7_line_24 |  | 20 | 22 | 0.00081358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4048-8_0_7_line_25 |  | 21 | 23 | 0.016779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4048-8_0_7_line_26 |  | 23 | 24 | 0.011083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4048-8_0_7_line_27 |  | 24 | 25 | 0.031595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4048-8_0_7_line_28 |  | 25 | 31 | 0.0090996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_4048-8_0_7_line_29 |  | 25 | 28 | 0.0061954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_4048-8_0_7_line_30 |  | 26 | 27 | 0.015114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4048-8_0_7_line_31 |  | 26 | 28 | 0.034424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_4048-8_0_7_line_32 |  | 27 | 29 | 0.012978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4048-8_0_7_line_33 |  | 29 | 30 | 0.014777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4048-8_0_7_line_34 |  | 30 | 57 | 0.0076336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4048-8_0_7_line_35 |  | 31 | 32 | 0.019519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_4048-8_0_7_line_36 |  | 32 | 33 | 0.024649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4048-8_0_7_line_37 |  | 32 | 61 | 0.0074241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_4048-8_0_7_line_38 |  | 35 | 36 | 0.023439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4048-8_0_7_line_39 |  | 37 | 38 | 0.015638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4048-8_0_7_line_40 |  | 37 | 39 | 0.0010329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4048-8_0_7_line_41 |  | 39 | 40 | 0.018219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4048-8_0_7_line_42 |  | 40 | 41 | 0.022057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4048-8_0_7_line_43 |  | 40 | 42 | 0.023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4048-8_0_7_line_44 |  | 41 | 48 | 0.006483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4048-8_0_7_line_45 |  | 42 | 46 | 0.014284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4048-8_0_7_line_46 |  | 43 | 44 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
47 | LV_4048-8_0_7_line_47 |  | 43 | 45 | 0.045381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_4048-8_0_7_line_48 |  | 45 | 49 | 0.0081003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4048-8_0_7_line_49 |  | 46 | 47 | 0.020579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4048-8_0_7_line_50 |  | 47 | 50 | 0.00097559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4048-8_0_7_line_51 |  | 48 | 51 | 0.005604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4048-8_0_7_line_52 |  | 49 | 53 | 0.014246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4048-8_0_7_line_53 |  | 50 | 54 | 0.025316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4048-8_0_7_line_54 |  | 50 | 55 | 0.046934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4048-8_0_7_line_55 |  | 51 | 56 | 0.028111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4048-8_0_7_line_56 |  | 52 | 53 | 0.018574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4048-8_0_7_line_57 |  | 55 | 106 | 0.018082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4048-8_0_7_line_58 |  | 56 | 67 | 0.057872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4048-8_0_7_line_59 |  | 56 | 68 | 0.025811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_4048-8_0_7_line_60 |  | 57 | 58 | 0.026226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4048-8_0_7_line_61 |  | 59 | 60 | 0.028833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4048-8_0_7_line_62 |  | 60 | 61 | 0.0092435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_4048-8_0_7_line_63 |  | 60 | 62 | 0.012998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_4048-8_0_7_line_64 |  | 62 | 63 | 0.016391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4048-8_0_7_line_65 |  | 62 | 64 | 0.028432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_4048-8_0_7_line_66 |  | 63 | 65 | 0.0070661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4048-8_0_7_line_67 |  | 64 | 66 | 0.024137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_4048-8_0_7_line_68 |  | 66 | 70 | 0.010812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_4048-8_0_7_line_69 |  | 68 | 69 | 0.038961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
70 | LV_4048-8_0_7_line_70 |  | 69 | 98 | 0.019218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4048-8_0_7_line_71 |  | 69 | 97 | 0.00069985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_4048-8_0_7_line_72 |  | 70 | 71 | 0.0017921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
73 | LV_4048-8_0_7_line_73 |  | 71 | 72 | 0.015293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
74 | LV_4048-8_0_7_line_74 |  | 71 | 73 | 0.010798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4048-8_0_7_line_75 |  | 72 | 82 | 0.019592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
76 | LV_4048-8_0_7_line_76 |  | 73 | 94 | 0.021933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4048-8_0_7_line_77 |  | 74 | 75 | 0.035756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
78 | LV_4048-8_0_7_line_78 |  | 74 | 76 | 0.025296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
79 | LV_4048-8_0_7_line_79 |  | 75 | 77 | 0.02372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
80 | LV_4048-8_0_7_line_80 |  | 75 | 78 | 0.095833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4048-8_0_7_line_81 |  | 76 | 79 | 0.03445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
82 | LV_4048-8_0_7_line_82 |  | 77 | 80 | 0.021905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_4048-8_0_7_line_83 |  | 78 | 85 | 0.043965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4048-8_0_7_line_84 |  | 79 | 81 | 0.020486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4048-8_0_7_line_85 |  | 79 | 82 | 0.029466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
86 | LV_4048-8_0_7_line_86 |  | 79 | 83 | 0.017694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4048-8_0_7_line_87 |  | 80 | 87 | 0.012905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_4048-8_0_7_line_88 |  | 81 | 86 | 0.010265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4048-8_0_7_line_89 |  | 82 | 84 | 0.039458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4048-8_0_7_line_90 |  | 83 | 88 | 0.002781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4048-8_0_7_line_91 |  | 84 | 89 | 0.011868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4048-8_0_7_line_92 |  | 85 | 90 | 0.013988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4048-8_0_7_line_93 |  | 86 | 91 | 0.013637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4048-8_0_7_line_94 |  | 87 | 92 | 0.011467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4048-8_0_7_line_95 |  | 87 | 93 | 0.014958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_4048-8_0_7_line_96 |  | 88 | 103 | 0.019748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4048-8_0_7_line_97 |  | 92 | 99 | 0.0054537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4048-8_0_7_line_98 |  | 93 | 97 | 0.009665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_4048-8_0_7_line_99 |  | 94 | 95 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4048-8_0_7_line_100 |  | 95 | 96 | 0.011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4048-8_0_7_line_101 |  | 99 | 100 | 0.024877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4048-8_0_7_line_102 |  | 100 | 101 | 0.023446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4048-8_0_7_line_103 |  | 100 | 102 | 0.027168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4048-8_0_7_line_104 |  | 102 | 104 | 0.0068107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4048-8_0_7_line_105 |  | 104 | 105 | 0.01929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4048-8_0_7_line_106 |  | 105 | 107 | 0.016986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4048-8_0_7_line_107 |  | 105 | 108 | 0.03777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4048-8_0_7_line_108 |  | 106 | 109 | 0.010934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4048-8_0_7_line_109 |  | 107 | 110 | 0.012057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4048-8_0_7_line_110 |  | 108 | 111 | 0.0081396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4048-8_0_7_line_111 |  | 109 | 117 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4048-8_0_7_line_112 |  | 110 | 116 | 0.01109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4048-8_0_7_line_113 |  | 111 | 119 | 0.036547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4048-8_0_7_line_114 |  | 112 | 113 | 0.11832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4048-8_0_7_line_115 |  | 112 | 114 | 0.02536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4048-8_0_7_line_116 |  | 113 | 120 | 0.031738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4048-8_0_7_line_117 |  | 114 | 121 | 0.015718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4048-8_0_7_line_118 |  | 115 | 116 | 0.021677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4048-8_0_7_line_119 |  | 117 | 118 | 0.0049665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4048-8_0_7_line_120 |  | 119 | 125 | 0.0064589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4048-8_0_7_line_121 |  | 120 | 124 | 0.0003488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4048-8_0_7_line_122 |  | 121 | 122 | 0.0038443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4048-8_0_7_line_123 |  | 123 | 124 | 0.013428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4048-8_0_7_line_124 |  | 123 | 125 | 0.0015104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4048-8_0_7_trafo_57 | 0.63 MVA 20/0.4 kV | 126 | 56 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2669712.7064 | 1255297.4562 | 2669710.2408 | 1255323.9965
1 | 2669708.612 | 1255341.529 | 2669710.2408 | 1255323.9965
2 | 2669712.7064 | 1255297.4562 | 2669707.5152 | 1255296.9503 | 2669700.3853 | 1255294.3024
3 | 2669712.7064 | 1255297.4562 | 2669720.5648 | 1255296.9483 | 2669724.3319 | 1255295.7499
4 | 2669708.612 | 1255341.529 | 2669708.1703 | 1255347.7033
5 | 2669708.612 | 1255341.529 | 2669693.7627 | 1255340.4145
6 | 2669684.5231 | 1255285.6389 | 2669687.4135 | 1255287.9183 | 2669696.1672 | 1255292.7359 | 2669700.3853 | 1255294.3024
7 | 2669724.3319 | 1255295.7499 | 2669731.0075 | 1255293.6263
8 | 2669676.2144 | 1255358.2045 | 2669677.8634 | 1255339.2211 | 2669693.7627 | 1255340.4145
9 | 2669680.5782 | 1255282.528 | 2669684.5231 | 1255285.6389
10 | 2669757.813 | 1255282.2911 | 2669733.1032 | 1255292.9596 | 2669731.0075 | 1255293.6263
11 | 2669676.2144 | 1255358.2045 | 2669675.6912 | 1255364.2218
12 | 2669676.2144 | 1255358.2045 | 2669651.939 | 1255355.8702
13 | 2669667.6621 | 1255270.2004 | 2669677.6229 | 1255280.1975 | 2669680.5782 | 1255282.528
14 | 2669764.3398 | 1255279.4731 | 2669757.813 | 1255282.2911
15 | 2669705.0316 | 1255389.9889 | 2669673.6669 | 1255387.507
16 | 2669703.2528 | 1255413.5741 | 2669703.3508 | 1255412.2965 | 2669705.0316 | 1255389.9889
17 | 2669673.6669 | 1255387.507 | 2669675.6912 | 1255364.2218
18 | 2669673.6669 | 1255387.507 | 2669657.029 | 1255386.1923
19 | 2669703.2528 | 1255413.5741 | 2669723.2186 | 1255419.1531
20 | 2669662.5114 | 1255265.0309 | 2669667.6621 | 1255270.2004
21 | 2669662.5114 | 1255265.0309 | 2669660.8559 | 1255262.8534
22 | 2669654.384 | 1255254.3413 | 2669660.8559 | 1255262.8534
23 | 2669799.2594 | 1255298.738 | 2669809.0933 | 1255296.7352
24 | 2669798.4622 | 1255298.9004 | 2669799.2594 | 1255298.738
25 | 2669822.8302 | 1255287.2776 | 2669819.5116 | 1255290.2421 | 2669814.8758 | 1255293.8012 | 2669809.0933 | 1255296.7352 | 2669809.0933 | 1255296.7352
26 | 2669829.2531 | 1255278.4484 | 2669826.1211 | 1255284.338 | 2669822.8302 | 1255287.2776
27 | 2669829.2531 | 1255278.4484 | 2669805.9089 | 1255267.4207 | 2669801.649 | 1255263.4121
28 | 2669801.649 | 1255263.4121 | 2669809.3332 | 1255258.5381
29 | 2669801.649 | 1255263.4121 | 2669795.9581 | 1255265.8608
30 | 2669764.3398 | 1255279.4731 | 2669758.8836 | 1255265.3789
31 | 2669764.3398 | 1255279.4731 | 2669773.0511 | 1255275.7174 | 2669795.9581 | 1255265.8608
32 | 2669754.1984 | 1255253.2764 | 2669758.8836 | 1255265.3789
33 | 2669754.1984 | 1255253.2764 | 2669750.8265 | 1255244.5663 | 2669748.8658 | 1255239.4952
34 | 2669746.2183 | 1255232.3394 | 2669746.6028 | 1255233.642 | 2669748.8658 | 1255239.4952
35 | 2669823.2139 | 1255244.9527 | 2669821.2717 | 1255247.1759 | 2669819.5234 | 1255248.9455 | 2669812.3194 | 1255256.644 | 2669809.3332 | 1255258.5381
36 | 2669823.2139 | 1255244.9527 | 2669833.2322 | 1255252.543 | 2669844.2921 | 1255257.401
37 | 2669823.2139 | 1255244.9527 | 2669827.3584 | 1255238.7932
38 | 2669723.2186 | 1255419.1531 | 2669741.9716 | 1255424.3933 | 2669745.8053 | 1255425.417
39 | 2669665.9433 | 1255137.8909 | 2669672.5556 | 1255123.7198
40 | 2669672.9923 | 1255122.7838 | 2669672.5556 | 1255123.7198
41 | 2669680.6961 | 1255106.2735 | 2669672.9923 | 1255122.7838
42 | 2669702.3529 | 1255110.776 | 2669688.9058 | 1255107.9824 | 2669680.6961 | 1255106.2735
43 | 2669680.6961 | 1255106.2735 | 2669682.8712 | 1255101.5623 | 2669677.7237 | 1255093.4847 | 2669673.6905 | 1255091.9918 | 2669669.0473 | 1255092.3263
44 | 2669705.3174 | 1255105.0066 | 2669702.3529 | 1255110.776
45 | 2669656.3843 | 1255085.717 | 2669669.0473 | 1255092.3263
46 | 2669642.9303 | 1255243.7963 | 2669651.9337 | 1255251.1186 | 2669654.384 | 1255254.3413
47 | 2669642.9303 | 1255243.7963 | 2669646.9194 | 1255235.5705 | 2669656.5749 | 1255207.9861 | 2669659.5353 | 1255201.628
48 | 2669662.9545 | 1255194.2847 | 2669659.5353 | 1255201.628
49 | 2669656.3843 | 1255085.717 | 2669669.0491 | 1255069.4962
50 | 2669669.0491 | 1255069.4962 | 2669669.6494 | 1255068.7273
51 | 2669705.3174 | 1255105.0066 | 2669707.9521 | 1255105.4713 | 2669710.7684 | 1255104.6149
52 | 2669662.9545 | 1255194.2847 | 2669668.9677 | 1255181.3701
53 | 2669669.6494 | 1255068.7273 | 2669687.2112 | 1255086.961
54 | 2669698.8081 | 1255031.9212 | 2669693.2305 | 1255039.8614 | 2669674.5348 | 1255063.1918 | 2669669.6494 | 1255068.7273
55 | 2669710.7684 | 1255104.6149 | 2669732.4856 | 1255086.6908
56 | 2669676.8572 | 1255164.5547 | 2669673.4998 | 1255171.6365 | 2669668.9677 | 1255181.3701
57 | 2669698.8081 | 1255031.9212 | 2669683.9061 | 1255021.6793
58 | 2669723.4058 | 1255045.4984 | 2669707.6099 | 1255059.5894 | 2669732.4856 | 1255086.6908
59 | 2669732.4856 | 1255086.6908 | 2669744.6092 | 1255077.6158 | 2669753.2475 | 1255071.3571
60 | 2669739.2843 | 1255207.0521 | 2669741.0718 | 1255213.3064 | 2669743.6288 | 1255223.5663 | 2669746.2183 | 1255232.3394
61 | 2669831.1468 | 1255230.4579 | 2669812.2848 | 1255208.6504
62 | 2669831.1468 | 1255230.4579 | 2669829.4713 | 1255235.653 | 2669827.3584 | 1255238.7932
63 | 2669834.1846 | 1255217.8512 | 2669832.9552 | 1255224.8751 | 2669831.1468 | 1255230.4579
64 | 2669834.1846 | 1255217.8512 | 2669846.2056 | 1255217.4593 | 2669850.4799 | 1255216.5812
65 | 2669834.1846 | 1255217.8512 | 2669834.2108 | 1255189.4196
66 | 2669850.4799 | 1255216.5812 | 2669855.9827 | 1255215.4509 | 2669857.3347 | 1255214.9312
67 | 2669834.2108 | 1255189.4196 | 2669835.2283 | 1255174.1427 | 2669836.7479 | 1255165.4485
68 | 2669836.7479 | 1255165.4485 | 2669837.4043 | 1255161.6926 | 2669840.4096 | 1255155.372
69 | 2669785.3085 | 1255049.23 | 2669772.2165 | 1255057.9043 | 2669767.4398 | 1255061.2505 | 2669762.5193 | 1255064.6395 | 2669753.2475 | 1255071.3571
70 | 2669785.3085 | 1255049.23 | 2669799.2384 | 1255062.4695
71 | 2669784.9102 | 1255048.6546 | 2669785.3085 | 1255049.23
72 | 2669841.1791 | 1255153.7535 | 2669840.4096 | 1255155.372
73 | 2669841.1791 | 1255153.7535 | 2669850.063 | 1255141.3061
74 | 2669841.1791 | 1255153.7535 | 2669836.6572 | 1255150.2088 | 2669835.0434 | 1255145.4214
75 | 2669861.922 | 1255125.7333 | 2669857.5165 | 1255130.8628 | 2669850.063 | 1255141.3061
76 | 2669835.0434 | 1255145.4214 | 2669828.0373 | 1255124.6373
77 | 2669843.478 | 1255040.1089 | 2669836.2783 | 1255053.1669 | 2669836.188 | 1255060.8269 | 2669844.4979 | 1255071.0625
78 | 2669860.442 | 1255090.7014 | 2669844.4979 | 1255071.0625
79 | 2669843.478 | 1255040.1089 | 2669825.7505 | 1255038.2208 | 2669819.8648 | 1255037.951
80 | 2669843.478 | 1255040.1089 | 2669845.7997 | 1255038.335 | 2669879.3994 | 1255012.6681 | 2669870.5512 | 1255002.4229 | 2669860.8899 | 1254992.0347 | 2669848.1091 | 1254973.0257
81 | 2669860.442 | 1255090.7014 | 2669861.8176 | 1255092.3966 | 2669878.5329 | 1255110.9962 | 2669884.4142 | 1255106.7403
82 | 2669797.983 | 1255036.9481 | 2669819.8648 | 1255037.951
83 | 2669848.1091 | 1254973.0257 | 2669831.3173 | 1254989.0061 | 2669820.2561 | 1255006.6023
84 | 2669884.4142 | 1255106.7403 | 2669890.5978 | 1255102.4323 | 2669901.491 | 1255095.3557
85 | 2669861.922 | 1255125.7333 | 2669878.5329 | 1255110.9962 | 2669884.4142 | 1255106.7403
86 | 2669884.4142 | 1255106.7403 | 2669893.958 | 1255121.6391
87 | 2669797.983 | 1255036.9481 | 2669788.1472 | 1255028.5595
88 | 2669901.491 | 1255095.3557 | 2669906.5593 | 1255104.2826
89 | 2669861.922 | 1255125.7333 | 2669881.0072 | 1255146.1288 | 2669882.4596 | 1255151.5388 | 2669879.5033 | 1255156.6719
90 | 2669895.4581 | 1255123.9809 | 2669893.958 | 1255121.6391
91 | 2669873.5802 | 1255166.9564 | 2669879.5033 | 1255156.6719
92 | 2669819.9538 | 1255019.5877 | 2669817.7254 | 1255010.6283 | 2669820.2561 | 1255006.6023
93 | 2669915.9618 | 1255112.7272 | 2669910.4842 | 1255111.1956 | 2669906.5593 | 1255104.2826
94 | 2669788.1472 | 1255028.5595 | 2669778.9571 | 1255021.7018
95 | 2669788.1472 | 1255028.5595 | 2669782.6199 | 1255038.6239 | 2669779.6932 | 1255040.5242
96 | 2669906.763 | 1255140.1544 | 2669900.6055 | 1255132.0164 | 2669895.4581 | 1255123.9809
97 | 2669773.8649 | 1255023.6543 | 2669778.9571 | 1255021.7018
98 | 2669779.6932 | 1255040.5242 | 2669782.4604 | 1255045.1157 | 2669784.9102 | 1255048.6546
99 | 2669823.1572 | 1255110.16 | 2669828.0373 | 1255124.6373
100 | 2669819.632 | 1255099.7022 | 2669823.1572 | 1255110.16
101 | 2669753.4905 | 1255009.5263 | 2669770.2508 | 1255019.8757 | 2669773.8649 | 1255023.6543
102 | 2669753.4905 | 1255009.5263 | 2669764.6641 | 1254988.8984
103 | 2669753.4905 | 1255009.5263 | 2669750.395 | 1255007.8331 | 2669730.4457 | 1254995.1504
104 | 2669724.6982 | 1254991.4964 | 2669730.4457 | 1254995.1504
105 | 2669724.6982 | 1254991.4964 | 2669716.4915 | 1254986.3183 | 2669707.9198 | 1254982.0254
106 | 2669707.9198 | 1254982.0254 | 2669709.6656 | 1254978.5434 | 2669711.8419 | 1254978.8693 | 2669714.4789 | 1254977.8551 | 2669716.6066 | 1254975.901 | 2669718.8117 | 1254971.2179
107 | 2669707.9198 | 1254982.0254 | 2669691.2927 | 1254973.1567 | 2669676.0806 | 1254961.898
108 | 2669683.9061 | 1255021.6793 | 2669674.8954 | 1255015.4863
109 | 2669723.9158 | 1254960.302 | 2669723.0718 | 1254961.7779 | 2669719.361 | 1254970.0513 | 2669718.8117 | 1254971.2179
110 | 2669669.538 | 1254957.0557 | 2669676.0806 | 1254961.898
111 | 2669659.0432 | 1255004.5913 | 2669674.8954 | 1255015.4863
112 | 2669729.8572 | 1254950.9498 | 2669726.4762 | 1254955.8247 | 2669723.9158 | 1254960.302
113 | 2669669.538 | 1254957.0557 | 2669667.2532 | 1254954.4158 | 2669660.5688 | 1254946.7983 | 2669657.3736 | 1254936.898 | 2669656.8282 | 1254925.55 | 2669656.8648 | 1254924.3936
114 | 2669735.2681 | 1254871.6224 | 2669711.7737 | 1254836.6871 | 2669708.8485 | 1254832.0493 | 2669705.8933 | 1254828.045 | 2669662.4938 | 1254866.5514 | 2669656.2838 | 1254871.1706
115 | 2669735.2681 | 1254871.6224 | 2669726.2263 | 1254877.1311 | 2669722.0798 | 1254881.3965 | 2669721.2043 | 1254885.9229 | 2669723.3985 | 1254889.5196
116 | 2669656.2838 | 1254871.1706 | 2669657.3918 | 1254874.4527 | 2669658.4467 | 1254889.2982 | 2669657.6088 | 1254900.8856 | 2669657.5527 | 1254902.6582
117 | 2669731.2565 | 1254903.1306 | 2669725.2969 | 1254892.6315 | 2669723.3985 | 1254889.5196
118 | 2669744.7786 | 1254935.2933 | 2669740.386 | 1254939.2208 | 2669731.28 | 1254948.8984 | 2669729.8572 | 1254950.9498
119 | 2669659.0432 | 1255004.5913 | 2669654.9502 | 1255001.7783
120 | 2669656.8648 | 1254924.3936 | 2669657.0691 | 1254917.9379
121 | 2669657.5527 | 1254902.6582 | 2669657.5417 | 1254903.0068
122 | 2669731.2565 | 1254903.1306 | 2669733.1541 | 1254906.4738
123 | 2669657.1169 | 1254916.4282 | 2669657.5417 | 1254903.0068
124 | 2669657.1169 | 1254916.4282 | 2669657.0691 | 1254917.9379

## bus_geodata
| x | y | coords
0 | 2669710.2408 | 1255323.9965
1 | 2669712.7064 | 1255297.4562
2 | 2669708.612 | 1255341.529
3 | 2669700.3853 | 1255294.3024
4 | 2669724.3319 | 1255295.7499
5 | 2669708.1703 | 1255347.7033
6 | 2669693.7627 | 1255340.4145
7 | 2669684.5231 | 1255285.6389
8 | 2669731.0075 | 1255293.6263
9 | 2669676.2144 | 1255358.2045
10 | 2669680.5782 | 1255282.528
11 | 2669757.813 | 1255282.2911
12 | 2669705.0316 | 1255389.9889
13 | 2669673.6669 | 1255387.507
14 | 2669703.2528 | 1255413.5741
15 | 2669675.6912 | 1255364.2218
16 | 2669651.939 | 1255355.8702
17 | 2669667.6621 | 1255270.2004
18 | 2669662.5114 | 1255265.0309
19 | 2669660.8559 | 1255262.8534
20 | 2669799.2594 | 1255298.738
21 | 2669809.0933 | 1255296.7352
22 | 2669798.4622 | 1255298.9004
23 | 2669822.8302 | 1255287.2776
24 | 2669829.2531 | 1255278.4484
25 | 2669801.649 | 1255263.4121
26 | 2669764.3398 | 1255279.4731
27 | 2669758.8836 | 1255265.3789
28 | 2669795.9581 | 1255265.8608
29 | 2669754.1984 | 1255253.2764
30 | 2669748.8658 | 1255239.4952
31 | 2669809.3332 | 1255258.5381
32 | 2669823.2139 | 1255244.9527
33 | 2669844.2921 | 1255257.401
34 | 2669657.029 | 1255386.1923
35 | 2669723.2186 | 1255419.1531
36 | 2669745.8053 | 1255425.417
37 | 2669672.5556 | 1255123.7198
38 | 2669665.9433 | 1255137.8909
39 | 2669672.9923 | 1255122.7838
40 | 2669680.6961 | 1255106.2735
41 | 2669702.3529 | 1255110.776
42 | 2669669.0473 | 1255092.3263
43 | 2669642.9303 | 1255243.7963
44 | 2669654.384 | 1255254.3413
45 | 2669659.5353 | 1255201.628
46 | 2669656.3843 | 1255085.717
47 | 2669669.0491 | 1255069.4962
48 | 2669705.3174 | 1255105.0066
49 | 2669662.9545 | 1255194.2847
50 | 2669669.6494 | 1255068.7273
51 | 2669710.7684 | 1255104.6149
52 | 2669676.8572 | 1255164.5547
53 | 2669668.9677 | 1255181.3701
54 | 2669687.2112 | 1255086.961
55 | 2669698.8081 | 1255031.9212
56 | 2669732.4856 | 1255086.6908
57 | 2669746.2183 | 1255232.3394
58 | 2669739.2843 | 1255207.0521
59 | 2669812.2848 | 1255208.6504
60 | 2669831.1468 | 1255230.4579
61 | 2669827.3584 | 1255238.7932
62 | 2669834.1846 | 1255217.8512
63 | 2669850.4799 | 1255216.5812
64 | 2669834.2108 | 1255189.4196
65 | 2669857.3347 | 1255214.9312
66 | 2669836.7479 | 1255165.4485
67 | 2669723.4058 | 1255045.4984
68 | 2669753.2475 | 1255071.3571
69 | 2669785.3085 | 1255049.23
70 | 2669840.4096 | 1255155.372
71 | 2669841.1791 | 1255153.7535
72 | 2669850.063 | 1255141.3061
73 | 2669835.0434 | 1255145.4214
74 | 2669844.4979 | 1255071.0625
75 | 2669843.478 | 1255040.1089
76 | 2669860.442 | 1255090.7014
77 | 2669819.8648 | 1255037.951
78 | 2669848.1091 | 1254973.0257
79 | 2669884.4142 | 1255106.7403
80 | 2669797.983 | 1255036.9481
81 | 2669901.491 | 1255095.3557
82 | 2669861.922 | 1255125.7333
83 | 2669893.958 | 1255121.6391
84 | 2669879.5033 | 1255156.6719
85 | 2669820.2561 | 1255006.6023
86 | 2669906.5593 | 1255104.2826
87 | 2669788.1472 | 1255028.5595
88 | 2669895.4581 | 1255123.9809
89 | 2669873.5802 | 1255166.9564
90 | 2669819.9538 | 1255019.5877
91 | 2669915.9618 | 1255112.7272
92 | 2669778.9571 | 1255021.7018
93 | 2669779.6932 | 1255040.5242
94 | 2669828.0373 | 1255124.6373
95 | 2669823.1572 | 1255110.16
96 | 2669819.632 | 1255099.7022
97 | 2669784.9102 | 1255048.6546
98 | 2669799.2384 | 1255062.4695
99 | 2669773.8649 | 1255023.6543
100 | 2669753.4905 | 1255009.5263
101 | 2669764.6641 | 1254988.8984
102 | 2669730.4457 | 1254995.1504
103 | 2669906.763 | 1255140.1544
104 | 2669724.6982 | 1254991.4964
105 | 2669707.9198 | 1254982.0254
106 | 2669683.9061 | 1255021.6792
107 | 2669718.8117 | 1254971.2179
108 | 2669676.0806 | 1254961.898
109 | 2669674.8954 | 1255015.4863
110 | 2669723.9158 | 1254960.302
111 | 2669669.538 | 1254957.0557
112 | 2669735.2681 | 1254871.6224
113 | 2669656.2838 | 1254871.1706
114 | 2669723.3985 | 1254889.5196
115 | 2669744.7786 | 1254935.2933
116 | 2669729.8572 | 1254950.9498
117 | 2669659.0432 | 1255004.5913
118 | 2669654.9502 | 1255001.7783
119 | 2669656.8648 | 1254924.3936
120 | 2669657.5527 | 1254902.6582
121 | 2669731.2565 | 1254903.1306
122 | 2669733.1541 | 1254906.4738
123 | 2669657.1169 | 1254916.4282
124 | 2669657.5417 | 1254903.0068
125 | 2669657.0691 | 1254917.9379
126 | 2669710.7684 | 1255104.6149

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1