## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4075-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4075-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4075-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4075-8_0_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_4075-8_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_4075-8_0_4_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_4075-8_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4075-8_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4075-8_0_4_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_4075-8_0_4_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_4075-8_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4075-8_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_4075-8_0_4_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_4075-8_0_4_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_4075-8_0_4_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_4075-8_0_4_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_4075-8_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_4075-8_0_4_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_4075-8_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_4075-8_0_4_node_119 | 0.4 | n |  | TRUE
20 | bus_LV_4075-8_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_4075-8_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_4075-8_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_4075-8_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_4075-8_0_4_node_79 | 0.4 | n |  | TRUE
25 | bus_LV_4075-8_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_4075-8_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_4075-8_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_4075-8_0_4_node_99 | 0.4 | n |  | TRUE
29 | bus_LV_4075-8_0_4_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_4075-8_0_4_node_100 | 0.4 | n |  | TRUE
31 | bus_LV_4075-8_0_4_node_98 | 0.4 | n |  | TRUE
32 | bus_LV_4075-8_0_4_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_4075-8_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_4075-8_0_4_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_4075-8_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_4075-8_0_4_node_74 | 0.4 | n |  | TRUE
37 | bus_LV_4075-8_0_4_node_95 | 0.4 | n |  | TRUE
38 | bus_LV_4075-8_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_4075-8_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_4075-8_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_4075-8_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_4075-8_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_4075-8_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_4075-8_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_4075-8_0_4_node_72 | 0.4 | n |  | TRUE
46 | bus_LV_4075-8_0_4_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_4075-8_0_4_node_93 | 0.4 | n |  | TRUE
48 | bus_LV_4075-8_0_4_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_4075-8_0_4_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_4075-8_0_4_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_4075-8_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_4075-8_0_4_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_4075-8_0_4_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_4075-8_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_4075-8_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_4075-8_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_4075-8_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_4075-8_0_4_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_4075-8_0_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_4075-8_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_4075-8_0_4_node_90 | 0.4 | n |  | TRUE
62 | bus_LV_4075-8_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_4075-8_0_4_node_86 | 0.4 | n |  | TRUE
64 | bus_LV_4075-8_0_4_node_51 | 0.4 | n |  | TRUE
65 | bus_LV_4075-8_0_4_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_4075-8_0_4_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_4075-8_0_4_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_4075-8_0_4_node_56 | 0.4 | n |  | TRUE
69 | bus_LV_4075-8_0_4_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_4075-8_0_4_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_4075-8_0_4_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_4075-8_0_4_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_4075-8_0_4_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_4075-8_0_4_node_62 | 0.4 | n |  | TRUE
75 | bus_LV_4075-8_0_4_node_63 | 0.4 | n |  | TRUE
76 | bus_LV_4075-8_0_4_node_64 | 0.4 | n |  | TRUE
77 | bus_LV_4075-8_0_4_node_65 | 0.4 | n |  | TRUE
78 | bus_LV_4075-8_0_4_node_66 | 0.4 | n |  | TRUE
79 | bus_LV_4075-8_0_4_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_4075-8_0_4_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_4075-8_0_4_node_69 | 0.4 | n |  | TRUE
82 | bus_LV_4075-8_0_4_node_70 | 0.4 | n |  | TRUE
83 | bus_LV_4075-8_0_4_node_71 | 0.4 | n |  | TRUE
84 | bus_LV_4075-8_0_4_node_73 | 0.4 | n |  | TRUE
85 | bus_LV_4075-8_0_4_node_75 | 0.4 | n |  | TRUE
86 | bus_LV_4075-8_0_4_node_182 | 0.4 | n |  | TRUE
87 | bus_LV_4075-8_0_4_node_180 | 0.4 | n |  | TRUE
88 | bus_LV_4075-8_0_4_node_177 | 0.4 | n |  | TRUE
89 | bus_LV_4075-8_0_4_node_181 | 0.4 | n |  | TRUE
90 | bus_LV_4075-8_0_4_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_4075-8_0_4_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_4075-8_0_4_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_4075-8_0_4_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_4075-8_0_4_node_81 | 0.4 | n |  | TRUE
95 | bus_LV_4075-8_0_4_node_117 | 0.4 | n |  | TRUE
96 | bus_LV_4075-8_0_4_node_118 | 0.4 | n |  | TRUE
97 | bus_LV_4075-8_0_4_node_114 | 0.4 | n |  | TRUE
98 | bus_LV_4075-8_0_4_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_4075-8_0_4_node_83 | 0.4 | n |  | TRUE
100 | bus_LV_4075-8_0_4_node_146 | 0.4 | n |  | TRUE
101 | bus_LV_4075-8_0_4_node_147 | 0.4 | n |  | TRUE
102 | bus_LV_4075-8_0_4_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_4075-8_0_4_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_4075-8_0_4_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_4075-8_0_4_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_4075-8_0_4_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_4075-8_0_4_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_4075-8_0_4_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_4075-8_0_4_node_94 | 0.4 | n |  | TRUE
110 | bus_LV_4075-8_0_4_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_4075-8_0_4_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_4075-8_0_4_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_4075-8_0_4_node_106 | 0.4 | n |  | TRUE
114 | bus_LV_4075-8_0_4_node_108 | 0.4 | n |  | TRUE
115 | bus_LV_4075-8_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_4075-8_0_4_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_4075-8_0_4_node_112 | 0.4 | n |  | TRUE
118 | bus_LV_4075-8_0_4_node_107 | 0.4 | n |  | TRUE
119 | bus_LV_4075-8_0_4_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_4075-8_0_4_node_102 | 0.4 | n |  | TRUE
121 | bus_LV_4075-8_0_4_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_4075-8_0_4_node_111 | 0.4 | n |  | TRUE
123 | bus_LV_4075-8_0_4_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_4075-8_0_4_node_109 | 0.4 | n |  | TRUE
125 | bus_LV_4075-8_0_4_node_162 | 0.4 | n |  | TRUE
126 | bus_LV_4075-8_0_4_node_154 | 0.4 | n |  | TRUE
127 | bus_LV_4075-8_0_4_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_4075-8_0_4_node_166 | 0.4 | n |  | TRUE
129 | bus_LV_4075-8_0_4_node_164 | 0.4 | n |  | TRUE
130 | bus_LV_4075-8_0_4_node_152 | 0.4 | n |  | TRUE
131 | bus_LV_4075-8_0_4_node_165 | 0.4 | n |  | TRUE
132 | bus_LV_4075-8_0_4_node_160 | 0.4 | n |  | TRUE
133 | bus_LV_4075-8_0_4_node_144 | 0.4 | n |  | TRUE
134 | bus_LV_4075-8_0_4_node_148 | 0.4 | n |  | TRUE
135 | bus_LV_4075-8_0_4_node_141 | 0.4 | n |  | TRUE
136 | bus_LV_4075-8_0_4_node_155 | 0.4 | n |  | TRUE
137 | bus_LV_4075-8_0_4_node_140 | 0.4 | n |  | TRUE
138 | bus_LV_4075-8_0_4_node_120 | 0.4 | n |  | TRUE
139 | bus_LV_4075-8_0_4_node_121 | 0.4 | n |  | TRUE
140 | bus_LV_4075-8_0_4_node_122 | 0.4 | n |  | TRUE
141 | bus_LV_4075-8_0_4_node_123 | 0.4 | n |  | TRUE
142 | bus_LV_4075-8_0_4_node_124 | 0.4 | n |  | TRUE
143 | bus_LV_4075-8_0_4_node_127 | 0.4 | n |  | TRUE
144 | bus_LV_4075-8_0_4_node_125 | 0.4 | n |  | TRUE
145 | bus_LV_4075-8_0_4_node_126 | 0.4 | n |  | TRUE
146 | bus_LV_4075-8_0_4_node_128 | 0.4 | n |  | TRUE
147 | bus_LV_4075-8_0_4_node_129 | 0.4 | n |  | TRUE
148 | bus_LV_4075-8_0_4_node_151 | 0.4 | n |  | TRUE
149 | bus_LV_4075-8_0_4_node_158 | 0.4 | n |  | TRUE
150 | bus_LV_4075-8_0_4_node_130 | 0.4 | n |  | TRUE
151 | bus_LV_4075-8_0_4_node_131 | 0.4 | n |  | TRUE
152 | bus_LV_4075-8_0_4_node_132 | 0.4 | n |  | TRUE
153 | bus_LV_4075-8_0_4_node_133 | 0.4 | n |  | TRUE
154 | bus_LV_4075-8_0_4_node_134 | 0.4 | n |  | TRUE
155 | bus_LV_4075-8_0_4_node_157 | 0.4 | n |  | TRUE
156 | bus_LV_4075-8_0_4_node_153 | 0.4 | n |  | TRUE
157 | bus_LV_4075-8_0_4_node_156 | 0.4 | n |  | TRUE
158 | bus_LV_4075-8_0_4_node_135 | 0.4 | n |  | TRUE
159 | bus_LV_4075-8_0_4_node_136 | 0.4 | n |  | TRUE
160 | bus_LV_4075-8_0_4_node_137 | 0.4 | n |  | TRUE
161 | bus_LV_4075-8_0_4_node_138 | 0.4 | n |  | TRUE
162 | bus_LV_4075-8_0_4_node_139 | 0.4 | n |  | TRUE
163 | bus_LV_4075-8_0_4_node_145 | 0.4 | n |  | TRUE
164 | bus_LV_4075-8_0_4_node_187 | 0.4 | n |  | TRUE
165 | bus_LV_4075-8_0_4_node_143 | 0.4 | n |  | TRUE
166 | bus_LV_4075-8_0_4_node_142 | 0.4 | n |  | TRUE
167 | bus_LV_4075-8_0_4_node_150 | 0.4 | n |  | TRUE
168 | bus_LV_4075-8_0_4_node_168 | 0.4 | n |  | TRUE
169 | bus_LV_4075-8_0_4_node_167 | 0.4 | n |  | TRUE
170 | bus_LV_4075-8_0_4_node_159 | 0.4 | n |  | TRUE
171 | bus_LV_4075-8_0_4_node_161 | 0.4 | n |  | TRUE
172 | bus_LV_4075-8_0_4_node_163 | 0.4 | n |  | TRUE
173 | bus_LV_4075-8_0_4_node_169 | 0.4 | n |  | TRUE
174 | bus_LV_4075-8_0_4_node_170 | 0.4 | n |  | TRUE
175 | bus_LV_4075-8_0_4_node_171 | 0.4 | n |  | TRUE
176 | bus_LV_4075-8_0_4_node_172 | 0.4 | n |  | TRUE
177 | bus_LV_4075-8_0_4_node_178 | 0.4 | n |  | TRUE
178 | bus_LV_4075-8_0_4_node_179 | 0.4 | n |  | TRUE
179 | bus_LV_4075-8_0_4_node_173 | 0.4 | n |  | TRUE
180 | bus_LV_4075-8_0_4_node_174 | 0.4 | n |  | TRUE
181 | bus_LV_4075-8_0_4_node_175 | 0.4 | n |  | TRUE
182 | bus_LV_4075-8_0_4_node_176 | 0.4 | n |  | TRUE
183 | bus_LV_4075-8_0_4_node_186 | 0.4 | n |  | TRUE
184 | bus_LV_4075-8_0_4_node_184 | 0.4 | n |  | TRUE
185 | bus_LV_4075-8_0_4_node_183 | 0.4 | n |  | TRUE
186 | bus_LV_4075-8_0_4_node_185 | 0.4 | n |  | TRUE
187 | bus_MV_420_0_node_126 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4075-8_0_4_load_0 | 0 | 0.011736 | 0.0029413 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4075-8_0_4_load_1 | 1 | 0.0028118 | 0.00070471 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4075-8_0_4_load_2 | 2 | 0.0071482 | 0.0017915 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4075-8_0_4_load_6 | 3 | 0.0021803 | 0.00054642 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4075-8_0_4_load_7 | 4 | 0.006861 | 0.0017195 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4075-8_0_4_load_3 | 5 | 0.0057295 | 0.0014359 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4075-8_0_4_load_4 | 6 | 0.0037199 | 0.0009323 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4075-8_0_4_load_5 | 7 | 0.0025134 | 0.00062992 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4075-8_0_4_load_12 | 8 | 0.0041348 | 0.0010363 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4075-8_0_4_load_13 | 9 | 0.0023479 | 0.00058844 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4075-8_0_4_load_8 | 10 | 0.0037531 | 0.00094062 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4075-8_0_4_load_9 | 11 | 0.0074839 | 0.0018756 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4075-8_0_4_load_10 | 12 | 0.0059014 | 0.001479 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4075-8_0_4_load_11 | 13 | 0.0036105 | 0.00090489 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4075-8_0_4_load_34 | 14 | 0.0020037 | 0.00050218 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4075-8_0_4_load_18 | 17 | 0.002578 | 0.00064612 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4075-8_0_4_load_15 | 18 | 0.0029877 | 0.00074878 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4075-8_0_4_load_119 | 19 | 0.0021958 | 0.00055032 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4075-8_0_4_load_16 | 20 | 0.0049167 | 0.0012322 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4075-8_0_4_load_17 | 21 | 0.0053572 | 0.0013426 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4075-8_0_4_load_19 | 22 | 0.0052064 | 0.0013048 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4075-8_0_4_load_21 | 25 | 0.0041863 | 0.0010492 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4075-8_0_4_load_22 | 26 | 0.013593 | 0.0034067 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4075-8_0_4_load_23 | 27 | 0.0036424 | 0.00091286 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4075-8_0_4_load_24 | 29 | 0.0014754 | 0.00036977 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4075-8_0_4_load_98 | 31 | 0.0036769 | 0.00092152 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4075-8_0_4_load_29 | 34 | 0.0022597 | 0.00056635 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4075-8_0_4_load_74 | 36 | 0.0041038 | 0.0010285 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4075-8_0_4_load_26 | 38 | 0.00213 | 0.00053383 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4075-8_0_4_load_30 | 40 | 0.0057861 | 0.0014501 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4075-8_0_4_load_31 | 41 | 0.0035582 | 0.00089177 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4075-8_0_4_load_32 | 42 | 0.0040145 | 0.0010061 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4075-8_0_4_load_43 | 44 | 0.0020376 | 0.00051068 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4075-8_0_4_load_101 | 46 | 0.0025676 | 0.00064351 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4075-8_0_4_load_93 | 47 | 0.0024021 | 0.00060202 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4075-8_0_4_load_40 | 48 | 0.0084336 | 0.0021136 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4075-8_0_4_load_37 | 51 | 0.0032256 | 0.0008084 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4075-8_0_4_load_35 | 52 | 0.0059236 | 0.0014846 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4075-8_0_4_load_36 | 53 | 0.0057779 | 0.0014481 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4075-8_0_4_load_46 | 54 | 0.010864 | 0.0027229 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4075-8_0_4_load_42 | 55 | 0.0087448 | 0.0021916 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4075-8_0_4_load_45 | 57 | 0.0016156 | 0.00040491 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4075-8_0_4_load_52 | 58 | 0.0017465 | 0.00043772 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4075-8_0_4_load_50 | 59 | 0.0030745 | 0.00077055 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4075-8_0_4_load_47 | 60 | 0.0099118 | 0.0024841 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4075-8_0_4_load_90 | 61 | 0.0040901 | 0.0010251 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4075-8_0_4_load_49 | 62 | 0.0045725 | 0.001146 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4075-8_0_4_load_51 | 64 | 0.0017243 | 0.00043215 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4075-8_0_4_load_53 | 65 | 0.003531 | 0.00088496 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4075-8_0_4_load_54 | 66 | 0.0012915 | 0.00032367 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4075-8_0_4_load_55 | 67 | 0.0034237 | 0.00085805 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4075-8_0_4_load_56 | 68 | 0.002862 | 0.00071729 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4075-8_0_4_load_57 | 69 | 0.0022627 | 0.00056709 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4075-8_0_4_load_58 | 70 | 0.0028657 | 0.00071822 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4075-8_0_4_load_59 | 71 | 0.00195 | 0.00048871 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4075-8_0_4_load_60 | 72 | 0.0016114 | 0.00040385 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4075-8_0_4_load_61 | 73 | 0.0021012 | 0.00052661 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4075-8_0_4_load_62 | 74 | 0.0016107 | 0.00040369 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4075-8_0_4_load_63 | 75 | 0.0011204 | 0.00028079 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4075-8_0_4_load_64 | 76 | 0.0016098 | 0.00040346 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4075-8_0_4_load_65 | 77 | 0.0021521 | 0.00053937 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4075-8_0_4_load_66 | 78 | 0.0022668 | 0.00056811 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4075-8_0_4_load_67 | 79 | 0.0024986 | 0.00062621 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4075-8_0_4_load_68 | 80 | 0.0019141 | 0.00047973 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4075-8_0_4_load_69 | 81 | 0.0014209 | 0.0003561 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4075-8_0_4_load_70 | 82 | 0.0031276 | 0.00078386 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4075-8_0_4_load_73 | 84 | 0.0033637 | 0.00084302 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4075-8_0_4_load_75 | 85 | 0.0028828 | 0.0007225 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4075-8_0_4_load_182 | 86 | 0.0019405 | 0.00048633 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4075-8_0_4_load_180 | 87 | 0.0026843 | 0.00067274 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4075-8_0_4_load_181 | 89 | 0.0023117 | 0.00057936 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4075-8_0_4_load_76 | 90 | 0.0025012 | 0.00062686 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4075-8_0_4_load_77 | 91 | 0.0012156 | 0.00030465 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4075-8_0_4_load_78 | 92 | 0.0035934 | 0.0009006 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4075-8_0_4_load_80 | 93 | 0.0019959 | 0.00050021 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4075-8_0_4_load_81 | 94 | 0.0019572 | 0.00049053 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4075-8_0_4_load_114 | 97 | 0.0037112 | 0.0009301 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4075-8_0_4_load_83 | 99 | 0.0020095 | 0.00050364 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4075-8_0_4_load_146 | 100 | 0.0033129 | 0.00083028 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4075-8_0_4_load_147 | 101 | 0.0020589 | 0.00051602 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4075-8_0_4_load_84 | 102 | 0.0070541 | 0.0017679 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4075-8_0_4_load_85 | 103 | 0.0045067 | 0.0011295 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4075-8_0_4_load_89 | 104 | 0.0039751 | 0.00099625 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4075-8_0_4_load_87 | 106 | 0.0022751 | 0.0005702 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4075-8_0_4_load_91 | 107 | 0.0022435 | 0.00056229 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4075-8_0_4_load_92 | 108 | 0.001271 | 0.00031854 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4075-8_0_4_load_94 | 109 | 0.0011486 | 0.00028787 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4075-8_0_4_load_96 | 110 | 0.0036358 | 0.00091121 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4075-8_0_4_load_97 | 111 | 0.0012532 | 0.00031409 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4075-8_0_4_load_106 | 113 | 0.0012334 | 0.00030911 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4075-8_0_4_load_115 | 115 | 0.0025721 | 0.00064463 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4075-8_0_4_load_116 | 116 | 0.0016112 | 0.00040381 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4075-8_0_4_load_112 | 117 | 0.0016208 | 0.00040621 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4075-8_0_4_load_107 | 118 | 0.0012506 | 0.00031344 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4075-8_0_4_load_105 | 119 | 0.0022673 | 0.00056823 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4075-8_0_4_load_102 | 120 | 0.0012423 | 0.00031136 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4075-8_0_4_load_103 | 121 | 0.0011788 | 0.00029544 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4075-8_0_4_load_109 | 124 | 0.0019533 | 0.00048955 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4075-8_0_4_load_162 | 125 | 0.0012339 | 0.00030925 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4075-8_0_4_load_154 | 126 | 0.0016125 | 0.00040412 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4075-8_0_4_load_110 | 127 | 0.0022512 | 0.00056421 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4075-8_0_4_load_166 | 128 | 0.0020954 | 0.00052515 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4075-8_0_4_load_164 | 129 | 0.0019613 | 0.00049154 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4075-8_0_4_load_152 | 130 | 0.0026829 | 0.0006724 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4075-8_0_4_load_165 | 131 | 0.0019622 | 0.00049178 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4075-8_0_4_load_160 | 132 | 0.0019616 | 0.00049161 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4075-8_0_4_load_148 | 134 | 0.0020927 | 0.00052448 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4075-8_0_4_load_141 | 135 | 0.0020555 | 0.00051516 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4075-8_0_4_load_155 | 136 | 0.00071398 | 0.00017894 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4075-8_0_4_load_140 | 137 | 0.0049819 | 0.0012486 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4075-8_0_4_load_120 | 138 | 0.0034109 | 0.00085484 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4075-8_0_4_load_121 | 139 | 0.0030696 | 0.00076932 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4075-8_0_4_load_122 | 140 | 0.0027618 | 0.00069217 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4075-8_0_4_load_123 | 141 | 0.0034113 | 0.00085495 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4075-8_0_4_load_124 | 142 | 0.0026021 | 0.00065214 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4075-8_0_4_load_127 | 143 | 0.0029908 | 0.00074955 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4075-8_0_4_load_125 | 144 | 0.0026868 | 0.00067337 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4075-8_0_4_load_126 | 145 | 0.0026013 | 0.00065196 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4075-8_0_4_load_128 | 146 | 0.0028439 | 0.00071276 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4075-8_0_4_load_158 | 149 | 0.0038905 | 0.00097506 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4075-8_0_4_load_130 | 150 | 0.0035992 | 0.00090204 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4075-8_0_4_load_131 | 151 | 0.0051029 | 0.0012789 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4075-8_0_4_load_133 | 153 | 0.0023886 | 0.00059864 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4075-8_0_4_load_134 | 154 | 0.001502 | 0.00037643 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4075-8_0_4_load_157 | 155 | 0.0046444 | 0.001164 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4075-8_0_4_load_153 | 156 | 0.0035285 | 0.00088434 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4075-8_0_4_load_156 | 157 | 0.0025599 | 0.00064157 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4075-8_0_4_load_135 | 158 | 0.01032 | 0.0025864 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4075-8_0_4_load_136 | 159 | 0.010325 | 0.0025876 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4075-8_0_4_load_138 | 161 | 0.010326 | 0.0025879 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4075-8_0_4_load_145 | 163 | 0.0077936 | 0.0019533 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4075-8_0_4_load_187 | 164 | 0.00049686 | 0.00012452 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4075-8_0_4_load_143 | 165 | 0.0023376 | 0.00058586 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4075-8_0_4_load_150 | 167 | 0.0012935 | 0.00032419 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4075-8_0_4_load_167 | 169 | 0.0034462 | 0.00086369 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4075-8_0_4_load_159 | 170 | 0.001235 | 0.00030952 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4075-8_0_4_load_161 | 171 | 0.0019624 | 0.00049183 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4075-8_0_4_load_163 | 172 | 0.0012347 | 0.00030946 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4075-8_0_4_load_169 | 173 | 0.0052484 | 0.0013154 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4075-8_0_4_load_170 | 174 | 0.0035059 | 0.00087865 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4075-8_0_4_load_171 | 175 | 0.0034201 | 0.00085716 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4075-8_0_4_load_172 | 176 | 0.0035075 | 0.00087907 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4075-8_0_4_load_178 | 177 | 0.003505 | 0.00087843 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_4075-8_0_4_load_179 | 178 | 0.0035046 | 0.00087833 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_4075-8_0_4_load_173 | 179 | 0.0019283 | 0.00048328 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_4075-8_0_4_load_174 | 180 | 0.0035063 | 0.00087877 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_4075-8_0_4_load_176 | 182 | 0.0035049 | 0.0008784 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_4075-8_0_4_load_186 | 183 | 0.0016437 | 0.00041195 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_4075-8_0_4_load_184 | 184 | 0.0010228 | 0.00025634 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_4075-8_0_4_load_183 | 185 | 0.0012612 | 0.00031608 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_4075-8_0_4_load_185 | 186 | 0.0017225 | 0.0004317 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 110 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4075-8_0_4_line_0 |  | 0 | 1 | 0.01312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4075-8_0_4_line_1 |  | 1 | 2 | 0.024453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4075-8_0_4_line_2 |  | 2 | 3 | 0.032265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4075-8_0_4_line_3 |  | 3 | 4 | 0.022148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4075-8_0_4_line_4 |  | 4 | 10 | 0.017902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4075-8_0_4_line_5 |  | 5 | 6 | 0.021934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4075-8_0_4_line_6 |  | 6 | 7 | 0.0090777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4075-8_0_4_line_7 |  | 7 | 8 | 0.0041464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4075-8_0_4_line_8 |  | 8 | 9 | 0.016688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4075-8_0_4_line_9 |  | 9 | 16 | 0.010897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4075-8_0_4_line_10 |  | 10 | 11 | 0.011846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4075-8_0_4_line_11 |  | 11 | 12 | 0.035449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4075-8_0_4_line_12 |  | 12 | 13 | 0.0042072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4075-8_0_4_line_13 |  | 13 | 14 | 0.036784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4075-8_0_4_line_14 |  | 14 | 15 | 0.016392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4075-8_0_4_line_15 |  | 15 | 49 | 0.023111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_4075-8_0_4_line_16 |  | 15 | 42 | 0.0040043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4075-8_0_4_line_17 |  | 16 | 17 | 0.024034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4075-8_0_4_line_18 |  | 16 | 18 | 0.0018426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4075-8_0_4_line_19 |  | 17 | 19 | 0.014133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4075-8_0_4_line_20 |  | 18 | 20 | 0.019215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4075-8_0_4_line_21 |  | 19 | 24 | 0.016114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4075-8_0_4_line_22 |  | 20 | 21 | 0.024989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4075-8_0_4_line_23 |  | 21 | 22 | 0.030148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4075-8_0_4_line_24 |  | 22 | 23 | 0.0025717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4075-8_0_4_line_25 |  | 23 | 25 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4075-8_0_4_line_26 |  | 23 | 26 | 0.017846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4075-8_0_4_line_27 |  | 24 | 91 | 0.004026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4075-8_0_4_line_28 |  | 25 | 27 | 0.022441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4075-8_0_4_line_29 |  | 26 | 28 | 0.009594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4075-8_0_4_line_30 |  | 27 | 29 | 0.020297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4075-8_0_4_line_31 |  | 28 | 30 | 0.029618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4075-8_0_4_line_32 |  | 28 | 31 | 0.0067763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4075-8_0_4_line_33 |  | 30 | 113 | 0.014092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4075-8_0_4_line_34 |  | 31 | 111 | 0.0062763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4075-8_0_4_line_35 |  | 32 | 33 | 0.022605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_4075-8_0_4_line_36 |  | 32 | 34 | 0.01483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_4075-8_0_4_line_37 |  | 33 | 35 | 0.033441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_4075-8_0_4_line_38 |  | 33 | 36 | 0.021876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4075-8_0_4_line_39 |  | 34 | 37 | 0.0067698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_4075-8_0_4_line_40 |  | 35 | 44 | 0.027786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4075-8_0_4_line_41 |  | 35 | 43 | 0.027839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_4075-8_0_4_line_42 |  | 36 | 45 | 0.034969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4075-8_0_4_line_43 |  | 37 | 46 | 0.012239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_4075-8_0_4_line_44 |  | 37 | 47 | 0.0077843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_4075-8_0_4_line_45 |  | 38 | 39 | 0.031495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4075-8_0_4_line_46 |  | 39 | 40 | 0.0043519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_4075-8_0_4_line_47 |  | 39 | 41 | 0.014987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_4075-8_0_4_line_48 |  | 40 | 42 | 0.018331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_4075-8_0_4_line_49 |  | 41 | 43 | 0.018205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_4075-8_0_4_line_50 |  | 43 | 48 | 0.0044196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4075-8_0_4_line_51 |  | 44 | 55 | 0.015651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4075-8_0_4_line_52 |  | 45 | 85 | 0.018031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4075-8_0_4_line_53 |  | 45 | 83 | 0.0081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4075-8_0_4_line_54 |  | 46 | 112 | 0.016775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
55 | LV_4075-8_0_4_line_55 |  | 47 | 107 | 0.012091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_4075-8_0_4_line_56 |  | 49 | 50 | 0.1495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_4075-8_0_4_line_57 |  | 49 | 51 | 0.070553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4075-8_0_4_line_58 |  | 50 | 54 | 0.036698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4075-8_0_4_line_59 |  | 51 | 53 | 0.031243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4075-8_0_4_line_60 |  | 52 | 53 | 0.066401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4075-8_0_4_line_61 |  | 54 | 60 | 0.035646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4075-8_0_4_line_62 |  | 54 | 61 | 0.16907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4075-8_0_4_line_63 |  | 55 | 56 | 0.0061872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4075-8_0_4_line_64 |  | 56 | 57 | 0.01816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4075-8_0_4_line_65 |  | 57 | 58 | 0.022691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4075-8_0_4_line_66 |  | 58 | 59 | 0.0032696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4075-8_0_4_line_67 |  | 59 | 64 | 0.024107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4075-8_0_4_line_68 |  | 60 | 62 | 0.019858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4075-8_0_4_line_69 |  | 61 | 63 | 0.022568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4075-8_0_4_line_70 |  | 63 | 104 | 0.019103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4075-8_0_4_line_71 |  | 63 | 103 | 0.044504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4075-8_0_4_line_72 |  | 64 | 65 | 0.0010675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4075-8_0_4_line_73 |  | 65 | 66 | 0.020802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4075-8_0_4_line_74 |  | 66 | 67 | 0.0038011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4075-8_0_4_line_75 |  | 67 | 68 | 0.023568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4075-8_0_4_line_76 |  | 68 | 69 | 0.02255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4075-8_0_4_line_77 |  | 69 | 70 | 0.02339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4075-8_0_4_line_78 |  | 71 | 72 | 0.017528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4075-8_0_4_line_79 |  | 72 | 73 | 0.0050586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4075-8_0_4_line_80 |  | 73 | 74 | 0.016951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4075-8_0_4_line_81 |  | 74 | 75 | 0.011607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4075-8_0_4_line_82 |  | 75 | 76 | 0.0097574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4075-8_0_4_line_83 |  | 76 | 77 | 0.012906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4075-8_0_4_line_84 |  | 77 | 78 | 0.013549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4075-8_0_4_line_85 |  | 78 | 79 | 0.010959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4075-8_0_4_line_86 |  | 79 | 80 | 0.015085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4075-8_0_4_line_87 |  | 80 | 81 | 0.0038213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4075-8_0_4_line_88 |  | 81 | 82 | 0.02546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4075-8_0_4_line_89 |  | 82 | 83 | 0.010215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4075-8_0_4_line_90 |  | 83 | 84 | 0.03436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4075-8_0_4_line_91 |  | 84 | 86 | 0.0376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4075-8_0_4_line_92 |  | 85 | 87 | 0.017703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4075-8_0_4_line_93 |  | 86 | 88 | 0.0093139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4075-8_0_4_line_94 |  | 87 | 89 | 0.0024621 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4075-8_0_4_line_95 |  | 88 | 183 | 0.027515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4075-8_0_4_line_96 |  | 88 | 181 | 0.041984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4075-8_0_4_line_97 |  | 90 | 91 | 0.011694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4075-8_0_4_line_98 |  | 90 | 92 | 0.010162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4075-8_0_4_line_99 |  | 92 | 93 | 0.012339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4075-8_0_4_line_100 |  | 93 | 94 | 0.023297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4075-8_0_4_line_101 |  | 94 | 98 | 0.0077022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4075-8_0_4_line_102 |  | 95 | 96 | 0.009973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4075-8_0_4_line_103 |  | 95 | 97 | 0.024453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4075-8_0_4_line_104 |  | 96 | 134 | 0.0070231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4075-8_0_4_line_105 |  | 96 | 135 | 0.025294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4075-8_0_4_line_106 |  | 97 | 114 | 0.032457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4075-8_0_4_line_107 |  | 98 | 99 | 0.020072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4075-8_0_4_line_108 |  | 99 | 100 | 0.026097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4075-8_0_4_line_109 |  | 100 | 101 | 0.0023179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4075-8_0_4_line_110 |  | 102 | 103 | 0.0068603 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4075-8_0_4_line_111 |  | 104 | 105 | 0.035813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4075-8_0_4_line_112 |  | 105 | 106 | 0.013037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4075-8_0_4_line_113 |  | 107 | 108 | 0.011707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
114 | LV_4075-8_0_4_line_114 |  | 108 | 109 | 0.021477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
115 | LV_4075-8_0_4_line_115 |  | 109 | 110 | 0.0081638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
116 | LV_4075-8_0_4_line_116 |  | 110 | 111 | 0.014145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4075-8_0_4_line_117 |  | 112 | 119 | 0.025938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_4075-8_0_4_line_118 |  | 112 | 120 | 0.014495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4075-8_0_4_line_119 |  | 113 | 118 | 0.015183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4075-8_0_4_line_120 |  | 114 | 115 | 0.034375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4075-8_0_4_line_121 |  | 114 | 116 | 0.026611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4075-8_0_4_line_122 |  | 114 | 117 | 0.020208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4075-8_0_4_line_123 |  | 115 | 125 | 0.0091963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4075-8_0_4_line_124 |  | 116 | 126 | 0.03214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4075-8_0_4_line_125 |  | 117 | 127 | 0.02854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4075-8_0_4_line_126 |  | 119 | 122 | 0.019223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_4075-8_0_4_line_127 |  | 120 | 121 | 0.021993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4075-8_0_4_line_128 |  | 122 | 123 | 0.030222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
129 | LV_4075-8_0_4_line_129 |  | 122 | 124 | 0.019373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4075-8_0_4_line_130 |  | 123 | 128 | 0.0049942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4075-8_0_4_line_131 |  | 123 | 129 | 0.014847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_4075-8_0_4_line_132 |  | 125 | 132 | 0.0083761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4075-8_0_4_line_133 |  | 126 | 133 | 0.021458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4075-8_0_4_line_134 |  | 128 | 130 | 0.026826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4075-8_0_4_line_135 |  | 129 | 131 | 0.001077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_4075-8_0_4_line_136 |  | 130 | 147 | 0.014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4075-8_0_4_line_137 |  | 131 | 172 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_4075-8_0_4_line_138 |  | 132 | 170 | 0.014095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4075-8_0_4_line_139 |  | 133 | 156 | 0.026953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4075-8_0_4_line_140 |  | 133 | 153 | 0.022073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4075-8_0_4_line_141 |  | 134 | 136 | 0.0068755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4075-8_0_4_line_142 |  | 135 | 137 | 0.018513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4075-8_0_4_line_143 |  | 136 | 167 | 0.013133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4075-8_0_4_line_144 |  | 137 | 166 | 0.013884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4075-8_0_4_line_145 |  | 138 | 139 | 0.015298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4075-8_0_4_line_146 |  | 138 | 140 | 0.0024152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4075-8_0_4_line_147 |  | 139 | 141 | 0.0027776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4075-8_0_4_line_148 |  | 140 | 142 | 0.016487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4075-8_0_4_line_149 |  | 141 | 143 | 0.010282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4075-8_0_4_line_150 |  | 142 | 144 | 0.0019711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4075-8_0_4_line_151 |  | 144 | 145 | 0.014594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4075-8_0_4_line_152 |  | 145 | 146 | 0.0026517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4075-8_0_4_line_153 |  | 146 | 147 | 0.013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4075-8_0_4_line_154 |  | 147 | 148 | 0.034596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4075-8_0_4_line_155 |  | 148 | 149 | 0.036745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4075-8_0_4_line_156 |  | 149 | 168 | 0.027249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4075-8_0_4_line_157 |  | 150 | 151 | 0.029648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4075-8_0_4_line_158 |  | 150 | 152 | 0.03526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4075-8_0_4_line_159 |  | 151 | 153 | 0.043746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4075-8_0_4_line_160 |  | 152 | 154 | 0.055969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4075-8_0_4_line_161 |  | 154 | 155 | 0.012867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4075-8_0_4_line_162 |  | 155 | 157 | 0.0099057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4075-8_0_4_line_163 |  | 158 | 159 | 0.020712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4075-8_0_4_line_164 |  | 158 | 160 | 0.039076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4075-8_0_4_line_165 |  | 159 | 161 | 0.02334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4075-8_0_4_line_166 |  | 160 | 162 | 0.042691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4075-8_0_4_line_167 |  | 161 | 163 | 0.023834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4075-8_0_4_line_168 |  | 162 | 164 | 0.0051381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4075-8_0_4_line_169 |  | 163 | 165 | 0.03108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4075-8_0_4_line_170 |  | 165 | 166 | 0.0039113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4075-8_0_4_line_171 |  | 168 | 169 | 0.04948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4075-8_0_4_line_172 |  | 170 | 171 | 0.014383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
173 | LV_4075-8_0_4_line_173 |  | 171 | 172 | 0.0040063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
174 | LV_4075-8_0_4_line_174 |  | 173 | 174 | 0.022151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4075-8_0_4_line_175 |  | 173 | 175 | 0.0094432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4075-8_0_4_line_176 |  | 174 | 176 | 0.0038795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4075-8_0_4_line_177 |  | 176 | 177 | 0.01736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_4075-8_0_4_line_178 |  | 177 | 178 | 0.0042707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_4075-8_0_4_line_179 |  | 178 | 182 | 0.017266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_4075-8_0_4_line_180 |  | 179 | 180 | 0.019948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_4075-8_0_4_line_181 |  | 179 | 181 | 0.012377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_4075-8_0_4_line_182 |  | 180 | 182 | 0.006017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_4075-8_0_4_line_183 |  | 183 | 184 | 0.01025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_4075-8_0_4_line_184 |  | 184 | 185 | 0.0094447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_4075-8_0_4_line_185 |  | 185 | 186 | 0.021037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4075-8_0_4_trafo_96 | 0.63 MVA 20/0.4 kV | 187 | 110 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2670981.8645 | 1246612.1514 | 2670974.3703 | 1246601.3824
1 | 2670974.3703 | 1246601.3824 | 2670960.4023 | 1246581.3109
2 | 2670939.7876 | 1246556.5736 | 2670954.0513 | 1246572.1847 | 2670960.4023 | 1246581.3109
3 | 2670939.7876 | 1246556.5736 | 2670929.5637 | 1246545.384 | 2670924.1131 | 1246541.007
4 | 2670910.1549 | 1246529.7983 | 2670924.1131 | 1246541.007
5 | 2670931.9977 | 1246660.3926 | 2670912.8538 | 1246649.6865
6 | 2670912.8538 | 1246649.6865 | 2670911.0138 | 1246648.6575 | 2670906.4446 | 1246643.3947
7 | 2670903.7262 | 1246640.2637 | 2670906.4446 | 1246643.3947
8 | 2670903.7262 | 1246640.2637 | 2670892.7856 | 1246627.6624
9 | 2670885.6413 | 1246619.4336 | 2670892.7856 | 1246627.6624
10 | 2670910.1549 | 1246529.7983 | 2670902.38 | 1246523.5548 | 2670901.9421 | 1246521.7319
11 | 2670888.6218 | 1246489.1385 | 2670898.8899 | 1246509.025 | 2670901.9421 | 1246521.7319
12 | 2670888.6218 | 1246489.1385 | 2670886.6916 | 1246485.4002
13 | 2670886.6916 | 1246485.4002 | 2670883.0673 | 1246478.3809 | 2670870.218 | 1246452.5123
14 | 2670862.9209 | 1246437.8338 | 2670864.1604 | 1246440.317 | 2670870.218 | 1246452.5123
15 | 2670862.9209 | 1246437.8338 | 2670876.352 | 1246430.3112 | 2670881.8037 | 1246424.8502
16 | 2670862.9209 | 1246437.8338 | 2670859.4203 | 1246439.778
17 | 2670885.6413 | 1246619.4336 | 2670878.7915 | 1246623.0654 | 2670862.7416 | 1246625.7994
18 | 2670885.6413 | 1246619.4336 | 2670884.6504 | 1246617.8801
19 | 2670849.4694 | 1246629.5156 | 2670851.4046 | 1246627.7305 | 2670862.7416 | 1246625.7994
20 | 2670884.6504 | 1246617.8801 | 2670874.3175 | 1246601.6794
21 | 2670837.6249 | 1246640.4416 | 2670849.4694 | 1246629.5156
22 | 2670874.3175 | 1246601.6794 | 2670860.88 | 1246580.6113
23 | 2670860.88 | 1246580.6113 | 2670844.6682 | 1246555.1934
24 | 2670843.2852 | 1246553.0251 | 2670844.6682 | 1246555.1934
25 | 2670843.2852 | 1246553.0251 | 2670834.1631 | 1246536.8876
26 | 2670843.2852 | 1246553.0251 | 2670825.5856 | 1246555.3085
27 | 2670837.6249 | 1246640.4416 | 2670840.11 | 1246643.6091
28 | 2670834.1631 | 1246536.8876 | 2670828.9332 | 1246527.6358 | 2670821.2245 | 1246518.6846
29 | 2670816.0705 | 1246556.536 | 2670825.5856 | 1246555.3085
30 | 2670821.2245 | 1246518.6846 | 2670807.9798 | 1246503.3051
31 | 2670790.2784 | 1246571.2274 | 2670816.0705 | 1246556.536
32 | 2670816.0705 | 1246556.536 | 2670812.0182 | 1246551.1049
33 | 2670790.2784 | 1246571.2274 | 2670784.0513 | 1246558.5861
34 | 2670812.0182 | 1246551.1049 | 2670808.2649 | 1246546.0745
35 | 2670785.1375 | 1246477.9335 | 2670788.0491 | 1246455.5191
36 | 2670785.1375 | 1246477.9335 | 2670774.9225 | 1246481.8477 | 2670771.1955 | 1246482.9638
37 | 2670797.1012 | 1246427.5295 | 2670798.3233 | 1246442.855 | 2670796.6307 | 1246449.8508 | 2670793.8447 | 1246453.509 | 2670791.0292 | 1246455.2211 | 2670788.0491 | 1246455.5191
38 | 2670788.0491 | 1246455.5191 | 2670783.0885 | 1246454.0366 | 2670767.6205 | 1246447.7455
39 | 2670764.7102 | 1246484.9058 | 2670771.1955 | 1246482.9638
40 | 2670797.1012 | 1246427.5295 | 2670788.7811 | 1246401.1783 | 2670788.7517 | 1246401.0291
41 | 2670797.1012 | 1246427.5295 | 2670803.8337 | 1246426.1422 | 2670813.108 | 1246425.7304 | 2670824.0308 | 1246421.38
42 | 2670735.2993 | 1246434.3972 | 2670754.2196 | 1246442.295 | 2670767.6205 | 1246447.7455
43 | 2670764.7102 | 1246484.9058 | 2670752.5524 | 1246486.3085
44 | 2670764.7102 | 1246484.9058 | 2670766.0976 | 1246489.559 | 2670767.849 | 1246491.9063
45 | 2670839.5521 | 1246450.7194 | 2670811.6454 | 1246465.3187
46 | 2670839.5521 | 1246450.7194 | 2670842.4409 | 1246449.2083 | 2670843.3954 | 1246448.6782
47 | 2670839.5521 | 1246450.7194 | 2670832.5439 | 1246437.4719
48 | 2670843.3954 | 1246448.6782 | 2670859.4203 | 1246439.778
49 | 2670824.0308 | 1246421.38 | 2670832.5439 | 1246437.4719
50 | 2670824.0308 | 1246421.38 | 2670828.0165 | 1246419.4702
51 | 2670786.5377 | 1246385.5881 | 2670786.6084 | 1246390.1779 | 2670788.7517 | 1246401.0291
52 | 2670735.2993 | 1246434.3972 | 2670733.2543 | 1246438.6424 | 2670725.3677 | 1246449.3752
53 | 2670727.9058 | 1246431.04 | 2670735.2993 | 1246434.3972
54 | 2670735.8884 | 1246488.2311 | 2670752.5524 | 1246486.3085
55 | 2670775.0793 | 1246501.5969 | 2670767.849 | 1246491.9063
56 | 2670881.8037 | 1246424.8502 | 2671002.3146 | 1246336.3733
57 | 2670881.8037 | 1246424.8502 | 2670928.2775 | 1246477.9346
58 | 2671002.3146 | 1246336.3733 | 2671009.0646 | 1246334.7974 | 2671015.4145 | 1246331.938 | 2671023.6891 | 1246324.8098 | 2671031.8706 | 1246316.1948
59 | 2670948.8576 | 1246501.4421 | 2670928.2775 | 1246477.9346
60 | 2670992.7356 | 1246551.2794 | 2670953.341 | 1246506.5632 | 2670948.8576 | 1246501.4421
61 | 2671031.8706 | 1246316.1948 | 2671034.8291 | 1246313.0794 | 2671039.5948 | 1246308.7778 | 2671062.7334 | 1246299.4993
62 | 2671047.8015 | 1246484.5167 | 2671031.8706 | 1246316.1948
63 | 2670786.4424 | 1246379.4017 | 2670786.5377 | 1246385.5881
64 | 2670786.4424 | 1246379.4017 | 2670775.5326 | 1246378.86 | 2670769.5143 | 1246374.8409
65 | 2670757.67 | 1246355.487 | 2670769.5143 | 1246374.8409 | 2670769.5143 | 1246374.8409
66 | 2670755.9633 | 1246352.6982 | 2670757.67 | 1246355.487
67 | 2670755.9633 | 1246352.6982 | 2670743.3794 | 1246332.1357
68 | 2671062.7334 | 1246299.4993 | 2671081.1651 | 1246292.1081
69 | 2671027.512 | 1246494.3977 | 2671047.8015 | 1246484.5167
70 | 2671027.512 | 1246494.3977 | 2671009.8819 | 1246501.7531
71 | 2671027.512 | 1246494.3977 | 2671027.7782 | 1246494.879 | 2671030.581 | 1246499.905 | 2671049.178 | 1246533.2721
72 | 2670742.8221 | 1246331.2252 | 2670743.3794 | 1246332.1357
73 | 2670742.8221 | 1246331.2252 | 2670731.9635 | 1246313.4818
74 | 2670729.9793 | 1246310.2397 | 2670731.9635 | 1246313.4818
75 | 2670729.9793 | 1246310.2397 | 2670726.2543 | 1246304.1529 | 2670716.4238 | 1246290.9865
76 | 2670716.4238 | 1246290.9865 | 2670702.9325 | 1246272.917
77 | 2670702.9325 | 1246272.917 | 2670688.9388 | 1246254.1747
78 | 2670670.3065 | 1246309.6575 | 2670661.4466 | 1246294.5341
79 | 2670670.3065 | 1246309.6575 | 2670672.8636 | 1246314.0223
80 | 2670681.4318 | 1246328.6478 | 2670672.8636 | 1246314.0223
81 | 2670681.4318 | 1246328.6478 | 2670687.299 | 1246338.6629
82 | 2670692.2313 | 1246347.082 | 2670687.299 | 1246338.6629
83 | 2670692.2313 | 1246347.082 | 2670698.7552 | 1246358.2181
84 | 2670704.5895 | 1246370.4336 | 2670700.1004 | 1246360.5143 | 2670698.7552 | 1246358.2181
85 | 2670704.5895 | 1246370.4336 | 2670709.1078 | 1246380.4174
86 | 2670715.3275 | 1246394.1608 | 2670709.1078 | 1246380.4174
87 | 2670715.3275 | 1246394.1608 | 2670716.9031 | 1246397.6422
88 | 2670716.9031 | 1246397.6422 | 2670727.4005 | 1246420.8379
89 | 2670727.9058 | 1246431.04 | 2670727.4005 | 1246420.8379 | 2670727.4005 | 1246420.8379
90 | 2670727.9058 | 1246431.04 | 2670696.0906 | 1246418.0625
91 | 2670696.0906 | 1246418.0625 | 2670661.2756 | 1246403.8615
92 | 2670714.8848 | 1246463.6411 | 2670725.3677 | 1246449.3752
93 | 2670652.6516 | 1246400.3438 | 2670661.2756 | 1246403.8615
94 | 2670713.4269 | 1246465.6251 | 2670714.8848 | 1246463.6411
95 | 2670652.6516 | 1246400.3438 | 2670650.1192 | 1246390.3399 | 2670641.9202 | 1246375.2243
96 | 2670613.8574 | 1246384.0148 | 2670652.6516 | 1246400.3438
97 | 2670847.3279 | 1246652.8095 | 2670840.11 | 1246643.6091
98 | 2670853.6001 | 1246660.8045 | 2670847.3279 | 1246652.8095
99 | 2670853.6001 | 1246660.8045 | 2670861.2161 | 1246670.5124
100 | 2670861.2161 | 1246670.5124 | 2670875.5958 | 1246688.8416
101 | 2670880.3499 | 1246694.9015 | 2670875.5958 | 1246688.8416
102 | 2670793.9746 | 1246639.9979 | 2670793.0507 | 1246630.0688
103 | 2670793.0507 | 1246630.0688 | 2670772.862 | 1246616.2722
104 | 2670793.9746 | 1246639.9979 | 2670797.5896 | 1246646.0192
105 | 2670793.9746 | 1246639.9979 | 2670775.2304 | 1246647.146 | 2670770.5445 | 1246649.4764
106 | 2670748.2781 | 1246595.1544 | 2670767.5817 | 1246612.6637 | 2670772.862 | 1246616.2722
107 | 2670880.3499 | 1246694.9015 | 2670862.879 | 1246704.7827
108 | 2670840.084 | 1246717.4872 | 2670840.9321 | 1246717.0575 | 2670861.3285 | 1246705.6597 | 2670862.879 | 1246704.7827
109 | 2670840.084 | 1246717.4872 | 2670838.0163 | 1246718.5348
110 | 2671052.5179 | 1246539.2645 | 2671049.178 | 1246533.2721
111 | 2670979.3981 | 1246520.2623 | 2671000.9312 | 1246505.4874 | 2671009.8819 | 1246501.7531
112 | 2670979.3981 | 1246520.2623 | 2670986.5878 | 1246531.138
113 | 2670775.0793 | 1246501.5969 | 2670782.0803 | 1246510.9801
114 | 2670794.9238 | 1246528.1938 | 2670782.0803 | 1246510.9801
115 | 2670799.8058 | 1246534.737 | 2670794.9238 | 1246528.1938
116 | 2670799.8058 | 1246534.737 | 2670808.2649 | 1246546.0745
117 | 2670735.8884 | 1246488.2311 | 2670726.0191 | 1246491.6714 | 2670714.6797 | 1246496.1283 | 2670711.7719 | 1246497.6932
118 | 2670735.8884 | 1246488.2311 | 2670737.3958 | 1246492.3186 | 2670740.5851 | 1246496.6375 | 2670743.626 | 1246500.3114
119 | 2670777.3418 | 1246544.9656 | 2670784.0513 | 1246558.5861
120 | 2670748.2781 | 1246595.1544 | 2670713.9037 | 1246595.378 | 2670713.9037 | 1246595.378
121 | 2670748.2781 | 1246595.1544 | 2670742.3732 | 1246612.6742 | 2670737.3982 | 1246619.0948
122 | 2670748.2781 | 1246595.1544 | 2670741.9058 | 1246584.7377 | 2670738.522 | 1246577.4918
123 | 2670710.3272 | 1246586.9057 | 2670713.9037 | 1246595.378
124 | 2670737.3982 | 1246619.0948 | 2670720.3919 | 1246641.0432 | 2670718.5587 | 1246645.015
125 | 2670726.4457 | 1246551.6323 | 2670738.522 | 1246577.4918
126 | 2670695.2725 | 1246507.5272 | 2670704.2101 | 1246501.763 | 2670711.7719 | 1246497.6932
127 | 2670743.626 | 1246500.3114 | 2670757.6493 | 1246517.2535
128 | 2670695.2725 | 1246507.5272 | 2670669.2074 | 1246522.9498
129 | 2670695.2725 | 1246507.5272 | 2670698.8543 | 1246514.4081 | 2670705.9231 | 1246523.6252
130 | 2670669.2074 | 1246522.9498 | 2670665.2431 | 1246525.9872
131 | 2670669.2074 | 1246522.9498 | 2670678.3663 | 1246534.6352
132 | 2670710.3272 | 1246586.9057 | 2670707.0697 | 1246579.189
133 | 2670709.5665 | 1246664.4974 | 2670718.5587 | 1246645.015
134 | 2670665.2431 | 1246525.9872 | 2670643.949 | 1246542.3025
135 | 2670678.3663 | 1246534.6352 | 2670679.0307 | 1246535.4828
136 | 2670631.8448 | 1246550.7578 | 2670634.0687 | 1246549.8725 | 2670643.949 | 1246542.3025
137 | 2670679.0307 | 1246535.4828 | 2670691.2846 | 1246551.117
138 | 2670701.588 | 1246566.2031 | 2670707.0697 | 1246579.189
139 | 2670684.9131 | 1246653.4402 | 2670709.5665 | 1246664.4974
140 | 2670709.5665 | 1246664.4974 | 2670699.3697 | 1246684.0744
141 | 2670797.5896 | 1246646.0192 | 2670801.1286 | 1246651.9139
142 | 2670755.1534 | 1246658.9814 | 2670756.6501 | 1246656.3864 | 2670770.5445 | 1246649.4764
143 | 2670806.8671 | 1246663.7004 | 2670803.3072 | 1246655.5425 | 2670801.1286 | 1246651.9139
144 | 2670749.0835 | 1246671.3512 | 2670749.8157 | 1246668.2355 | 2670755.1534 | 1246658.9814
145 | 2670650.1396 | 1246599.1246 | 2670655.5518 | 1246613.4331
146 | 2670650.1396 | 1246599.1246 | 2670649.2851 | 1246596.8656
147 | 2670656.5344 | 1246616.031 | 2670655.5518 | 1246613.4331
148 | 2670643.4522 | 1246581.4449 | 2670649.2851 | 1246596.8656
149 | 2670660.1721 | 1246625.6481 | 2670656.5344 | 1246616.031
150 | 2670643.4522 | 1246581.4449 | 2670642.7548 | 1246579.6013
151 | 2670637.5916 | 1246565.951 | 2670642.7548 | 1246579.6013
152 | 2670637.5916 | 1246565.951 | 2670636.6535 | 1246563.4708
153 | 2670631.8448 | 1246550.7578 | 2670636.6535 | 1246563.4708
154 | 2670599.9434 | 1246564.043 | 2670610.0966 | 1246558.3153 | 2670631.8448 | 1246550.7578
155 | 2670599.9434 | 1246564.043 | 2670593.4204 | 1246559.9069 | 2670575.6702 | 1246536.9463
156 | 2670559.0042 | 1246515.3882 | 2670575.6702 | 1246536.9463
157 | 2670662.7614 | 1246682.7023 | 2670655.0421 | 1246678.9469 | 2670647.8661 | 1246698.75
158 | 2670623.6283 | 1246719.2012 | 2670642.6616 | 1246713.1124 | 2670647.8661 | 1246698.75
159 | 2670662.7614 | 1246682.7023 | 2670668.1856 | 1246685.3413 | 2670689.5794 | 1246694.1691 | 2670696.2998 | 1246689.9684 | 2670699.3697 | 1246684.0744
160 | 2670623.6283 | 1246719.2012 | 2670622.7896 | 1246711.6081 | 2670623.0524 | 1246707.3082 | 2670623.9934 | 1246703.1387 | 2670625.369 | 1246694.8381 | 2670625.3124 | 1246690.7123 | 2670624.849 | 1246687.1264 | 2670623.5898 | 1246683.7535 | 2670621.7047 | 1246680.2953 | 2670619.3861 | 1246677.7214 | 2670617.1094 | 1246674.7922 | 2670616.2656 | 1246672.7029 | 2670616.2971 | 1246671.3246 | 2670616.7921 | 1246669.7182 | 2670618.8308 | 1246666.7931
161 | 2670624.16 | 1246655.1206 | 2670619.8971 | 1246665.2631 | 2670618.8308 | 1246666.7931
162 | 2670626.5371 | 1246645.6172 | 2670626.4038 | 1246648.5621 | 2670625.8213 | 1246651.1681 | 2670624.16 | 1246655.1206
163 | 2670775.6604 | 1246769.0614 | 2670771.7709 | 1246755.9483 | 2670769.1673 | 1246749.4132
164 | 2670777.2733 | 1246807.5727 | 2670778.9055 | 1246799.9312 | 2670779.4862 | 1246792.4217 | 2670778.6304 | 1246782.4823 | 2670776.4112 | 1246771.5925 | 2670775.6604 | 1246769.0614
165 | 2670769.1673 | 1246749.4132 | 2670760.529 | 1246727.7304
166 | 2670754.4905 | 1246790.4888 | 2670756.2755 | 1246793.4567 | 2670770.2482 | 1246817.0512 | 2670772.9322 | 1246813.0581 | 2670777.2733 | 1246807.5727
167 | 2670760.529 | 1246727.7304 | 2670753.4865 | 1246710.0533 | 2670751.9284 | 1246705.507
168 | 2670754.4905 | 1246790.4888 | 2670750.0095 | 1246787.9746
169 | 2670748.3494 | 1246675.193 | 2670747.2223 | 1246681.0915 | 2670747.108 | 1246686.872 | 2670747.7642 | 1246691.383 | 2670749.9241 | 1246699.659 | 2670751.9284 | 1246705.507
170 | 2670749.0835 | 1246671.3512 | 2670748.3494 | 1246675.193
171 | 2670559.0042 | 1246515.3882 | 2670583.0592 | 1246493.0141 | 2670576.9647 | 1246477.5426
172 | 2670701.588 | 1246566.2031 | 2670699.8127 | 1246561.9976 | 2670693.756 | 1246554.2702
173 | 2670691.2846 | 1246551.117 | 2670693.756 | 1246554.2702
174 | 2670662.0699 | 1246470.7815 | 2670649.5979 | 1246452.4754
175 | 2670667.3869 | 1246478.5857 | 2670662.0699 | 1246470.7815
176 | 2670649.5979 | 1246452.4754 | 2670647.4136 | 1246449.2693
177 | 2670637.6389 | 1246434.9222 | 2670647.4136 | 1246449.2693
178 | 2670635.2343 | 1246431.3928 | 2670637.6389 | 1246434.9222
179 | 2670625.5128 | 1246417.1239 | 2670635.2343 | 1246431.3928
180 | 2670610.8932 | 1246395.6655 | 2670622.125 | 1246412.1513
181 | 2670613.8574 | 1246384.0148 | 2670610.2885 | 1246393.7903 | 2670610.8932 | 1246395.6655 | 2670610.8932 | 1246395.6655
182 | 2670622.125 | 1246412.1513 | 2670625.5128 | 1246417.1239
183 | 2670641.9202 | 1246375.2243 | 2670637.0331 | 1246366.2146
184 | 2670632.5299 | 1246357.9126 | 2670637.0331 | 1246366.2146
185 | 2670632.5299 | 1246357.9126 | 2670629.6134 | 1246352.5357 | 2670622.1472 | 1246339.6185

## bus_geodata
| x | y | coords
0 | 2670981.8645 | 1246612.1514
1 | 2670974.3703 | 1246601.3824
2 | 2670960.4023 | 1246581.3109
3 | 2670939.7876 | 1246556.5736
4 | 2670924.1131 | 1246541.007
5 | 2670931.9977 | 1246660.3926
6 | 2670912.8538 | 1246649.6865
7 | 2670906.4446 | 1246643.3947
8 | 2670903.7262 | 1246640.2637
9 | 2670892.7856 | 1246627.6624
10 | 2670910.1549 | 1246529.7983
11 | 2670901.9421 | 1246521.7319
12 | 2670888.6218 | 1246489.1385
13 | 2670886.6916 | 1246485.4002
14 | 2670870.218 | 1246452.5123
15 | 2670862.9209 | 1246437.8338
16 | 2670885.6413 | 1246619.4336
17 | 2670862.7416 | 1246625.7994
18 | 2670884.6504 | 1246617.8801
19 | 2670849.4694 | 1246629.5156
20 | 2670874.3175 | 1246601.6794
21 | 2670860.88 | 1246580.6113
22 | 2670844.6682 | 1246555.1934
23 | 2670843.2852 | 1246553.0251
24 | 2670837.6249 | 1246640.4416
25 | 2670834.1631 | 1246536.8876
26 | 2670825.5856 | 1246555.3085
27 | 2670821.2245 | 1246518.6846
28 | 2670816.0705 | 1246556.536
29 | 2670807.9798 | 1246503.3051
30 | 2670790.2784 | 1246571.2274
31 | 2670812.0182 | 1246551.1049
32 | 2670785.1375 | 1246477.9335
33 | 2670788.0491 | 1246455.5191
34 | 2670771.1955 | 1246482.9638
35 | 2670797.1012 | 1246427.5295
36 | 2670767.6205 | 1246447.7455
37 | 2670764.7102 | 1246484.9058
38 | 2670811.6454 | 1246465.3187
39 | 2670839.5521 | 1246450.7194
40 | 2670843.3954 | 1246448.6782
41 | 2670832.5439 | 1246437.4719
42 | 2670859.4203 | 1246439.778
43 | 2670824.0308 | 1246421.38
44 | 2670788.7517 | 1246401.0291
45 | 2670735.2993 | 1246434.3972
46 | 2670752.5524 | 1246486.3085
47 | 2670767.849 | 1246491.9063
48 | 2670828.0165 | 1246419.4702
49 | 2670881.8037 | 1246424.8502
50 | 2671002.3146 | 1246336.3733
51 | 2670928.2775 | 1246477.9346
52 | 2670992.7356 | 1246551.2794
53 | 2670948.8576 | 1246501.4421
54 | 2671031.8706 | 1246316.1948
55 | 2670786.5377 | 1246385.5881
56 | 2670786.4424 | 1246379.4017
57 | 2670769.5143 | 1246374.8409
58 | 2670757.67 | 1246355.487
59 | 2670755.9633 | 1246352.6982
60 | 2671062.7334 | 1246299.4993
61 | 2671047.8015 | 1246484.5167
62 | 2671081.1651 | 1246292.1081
63 | 2671027.512 | 1246494.3977
64 | 2670743.3794 | 1246332.1357
65 | 2670742.8221 | 1246331.2252
66 | 2670731.9635 | 1246313.4818
67 | 2670729.9793 | 1246310.2397
68 | 2670716.4238 | 1246290.9865
69 | 2670702.9325 | 1246272.917
70 | 2670688.9388 | 1246254.1747
71 | 2670661.4466 | 1246294.5341
72 | 2670670.3065 | 1246309.6575
73 | 2670672.8636 | 1246314.0223
74 | 2670681.4318 | 1246328.6478
75 | 2670687.299 | 1246338.6629
76 | 2670692.2313 | 1246347.082
77 | 2670698.7552 | 1246358.2181
78 | 2670704.5895 | 1246370.4336
79 | 2670709.1078 | 1246380.4174
80 | 2670715.3275 | 1246394.1608
81 | 2670716.9031 | 1246397.6422
82 | 2670727.4005 | 1246420.8379
83 | 2670727.9058 | 1246431.04
84 | 2670696.0906 | 1246418.0625
85 | 2670725.3677 | 1246449.3752
86 | 2670661.2756 | 1246403.8615
87 | 2670714.8848 | 1246463.6411
88 | 2670652.6516 | 1246400.3438
89 | 2670713.4269 | 1246465.6251
90 | 2670847.3279 | 1246652.8095
91 | 2670840.11 | 1246643.6091
92 | 2670853.6001 | 1246660.8045
93 | 2670861.2161 | 1246670.5124
94 | 2670875.5958 | 1246688.8416
95 | 2670793.0507 | 1246630.0688
96 | 2670793.9746 | 1246639.9979
97 | 2670772.862 | 1246616.2722
98 | 2670880.3499 | 1246694.9015
99 | 2670862.879 | 1246704.7827
100 | 2670840.084 | 1246717.4872
101 | 2670838.0163 | 1246718.5348
102 | 2671052.5179 | 1246539.2645
103 | 2671049.178 | 1246533.2721
104 | 2671009.8819 | 1246501.7531
105 | 2670979.3981 | 1246520.2623
106 | 2670986.5878 | 1246531.138
107 | 2670775.0793 | 1246501.5969
108 | 2670782.0803 | 1246510.9801
109 | 2670794.9238 | 1246528.1938
110 | 2670799.8058 | 1246534.737
111 | 2670808.2649 | 1246546.0745
112 | 2670735.8884 | 1246488.2311
113 | 2670784.0513 | 1246558.5861
114 | 2670748.2781 | 1246595.1544
115 | 2670713.9037 | 1246595.378
116 | 2670737.3982 | 1246619.0948
117 | 2670738.522 | 1246577.4918
118 | 2670777.3418 | 1246544.9656
119 | 2670711.7719 | 1246497.6932
120 | 2670743.626 | 1246500.3114
121 | 2670757.6493 | 1246517.2535
122 | 2670695.2725 | 1246507.5272
123 | 2670669.2074 | 1246522.9498
124 | 2670705.9231 | 1246523.6252
125 | 2670710.3272 | 1246586.9057
126 | 2670718.5587 | 1246645.015
127 | 2670726.4457 | 1246551.6323
128 | 2670665.2431 | 1246525.9872
129 | 2670678.3663 | 1246534.6352
130 | 2670643.949 | 1246542.3025
131 | 2670679.0307 | 1246535.4828
132 | 2670707.0697 | 1246579.189
133 | 2670709.5665 | 1246664.4974
134 | 2670797.5896 | 1246646.0192
135 | 2670770.5445 | 1246649.4764
136 | 2670801.1286 | 1246651.9139
137 | 2670755.1534 | 1246658.9814
138 | 2670650.1396 | 1246599.1246
139 | 2670655.5518 | 1246613.4331
140 | 2670649.2851 | 1246596.8656
141 | 2670656.5344 | 1246616.031
142 | 2670643.4522 | 1246581.4449
143 | 2670660.1721 | 1246625.6481
144 | 2670642.7548 | 1246579.6013
145 | 2670637.5916 | 1246565.951
146 | 2670636.6535 | 1246563.4708
147 | 2670631.8448 | 1246550.7578
148 | 2670599.9434 | 1246564.043
149 | 2670575.6702 | 1246536.9463
150 | 2670647.8661 | 1246698.75
151 | 2670662.7614 | 1246682.7023
152 | 2670623.6283 | 1246719.2012
153 | 2670699.3697 | 1246684.0744
154 | 2670618.8308 | 1246666.7931
155 | 2670624.16 | 1246655.1206
156 | 2670684.9131 | 1246653.4402
157 | 2670626.5371 | 1246645.6172
158 | 2670775.6604 | 1246769.0614
159 | 2670769.1673 | 1246749.4132
160 | 2670777.2733 | 1246807.5727
161 | 2670760.529 | 1246727.7304
162 | 2670754.4905 | 1246790.4888
163 | 2670751.9284 | 1246705.507
164 | 2670750.0095 | 1246787.9746
165 | 2670748.3494 | 1246675.193
166 | 2670749.0835 | 1246671.3512
167 | 2670806.8671 | 1246663.7004
168 | 2670559.0042 | 1246515.3882
169 | 2670576.9647 | 1246477.5426
170 | 2670701.588 | 1246566.2031
171 | 2670693.756 | 1246554.2702
172 | 2670691.2846 | 1246551.117
173 | 2670662.0699 | 1246470.7815
174 | 2670649.5979 | 1246452.4754
175 | 2670667.3869 | 1246478.5857
176 | 2670647.4136 | 1246449.2693
177 | 2670637.6389 | 1246434.9222
178 | 2670635.2343 | 1246431.3928
179 | 2670610.8932 | 1246395.6655
180 | 2670622.125 | 1246412.1513
181 | 2670613.8574 | 1246384.0148
182 | 2670625.5128 | 1246417.1239
183 | 2670641.9202 | 1246375.2243
184 | 2670637.0331 | 1246366.2146
185 | 2670632.5299 | 1246357.9126
186 | 2670622.1472 | 1246339.6185
187 | 2670816.0705 | 1246556.536

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1