## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4080-15_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4080-15_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4080-15_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4080-15_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4080-15_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_4080-15_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_4080-15_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4080-15_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_4080-15_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_4080-15_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_4080-15_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_4080-15_0_4_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_4080-15_0_4_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_4080-15_0_4_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_4080-15_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_4080-15_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4080-15_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_4080-15_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_4080-15_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_4080-15_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_4080-15_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_4080-15_0_4_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_4080-15_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_4080-15_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_4080-15_0_4_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_4080-15_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_4080-15_0_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_4080-15_0_4_node_42 | 0.4 | n |  | TRUE
28 | bus_LV_4080-15_0_4_node_53 | 0.4 | n |  | TRUE
29 | bus_LV_4080-15_0_4_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_4080-15_0_4_node_52 | 0.4 | n |  | TRUE
31 | bus_LV_4080-15_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_4080-15_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_4080-15_0_4_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_4080-15_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_4080-15_0_4_node_163 | 0.4 | n |  | TRUE
36 | bus_LV_4080-15_0_4_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_4080-15_0_4_node_164 | 0.4 | n |  | TRUE
38 | bus_LV_4080-15_0_4_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_4080-15_0_4_node_51 | 0.4 | n |  | TRUE
40 | bus_LV_4080-15_0_4_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_4080-15_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_4080-15_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_4080-15_0_4_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_4080-15_0_4_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_4080-15_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_4080-15_0_4_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_4080-15_0_4_node_63 | 0.4 | n |  | TRUE
48 | bus_LV_4080-15_0_4_node_66 | 0.4 | n |  | TRUE
49 | bus_LV_4080-15_0_4_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_4080-15_0_4_node_76 | 0.4 | n |  | TRUE
51 | bus_LV_4080-15_0_4_node_73 | 0.4 | n |  | TRUE
52 | bus_LV_4080-15_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_4080-15_0_4_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_4080-15_0_4_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_4080-15_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_4080-15_0_4_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_4080-15_0_4_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_4080-15_0_4_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_4080-15_0_4_node_65 | 0.4 | n |  | TRUE
60 | bus_LV_4080-15_0_4_node_67 | 0.4 | n |  | TRUE
61 | bus_LV_4080-15_0_4_node_78 | 0.4 | n |  | TRUE
62 | bus_LV_4080-15_0_4_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_4080-15_0_4_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_4080-15_0_4_node_55 | 0.4 | n |  | TRUE
65 | bus_LV_4080-15_0_4_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_4080-15_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_4080-15_0_4_node_103 | 0.4 | n |  | TRUE
68 | bus_LV_4080-15_0_4_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_4080-15_0_4_node_144 | 0.4 | n |  | TRUE
70 | bus_LV_4080-15_0_4_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_4080-15_0_4_node_159 | 0.4 | n |  | TRUE
72 | bus_LV_4080-15_0_4_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_4080-15_0_4_node_49 | 0.4 | n |  | TRUE
74 | bus_LV_4080-15_0_4_node_50 | 0.4 | n |  | TRUE
75 | bus_LV_4080-15_0_4_node_120 | 0.4 | n |  | TRUE
76 | bus_LV_4080-15_0_4_node_98 | 0.4 | n |  | TRUE
77 | bus_LV_4080-15_0_4_node_92 | 0.4 | n |  | TRUE
78 | bus_LV_4080-15_0_4_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_4080-15_0_4_node_64 | 0.4 | n |  | TRUE
80 | bus_LV_4080-15_0_4_node_68 | 0.4 | n |  | TRUE
81 | bus_LV_4080-15_0_4_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_4080-15_0_4_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_4080-15_0_4_node_72 | 0.4 | n |  | TRUE
84 | bus_LV_4080-15_0_4_node_102 | 0.4 | n |  | TRUE
85 | bus_LV_4080-15_0_4_node_101 | 0.4 | n |  | TRUE
86 | bus_LV_4080-15_0_4_node_77 | 0.4 | n |  | TRUE
87 | bus_LV_4080-15_0_4_node_104 | 0.4 | n |  | TRUE
88 | bus_LV_4080-15_0_4_node_111 | 0.4 | n |  | TRUE
89 | bus_LV_4080-15_0_4_node_108 | 0.4 | n |  | TRUE
90 | bus_LV_4080-15_0_4_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_4080-15_0_4_node_80 | 0.4 | n |  | TRUE
92 | bus_LV_4080-15_0_4_node_81 | 0.4 | n |  | TRUE
93 | bus_LV_4080-15_0_4_node_82 | 0.4 | n |  | TRUE
94 | bus_LV_4080-15_0_4_node_83 | 0.4 | n |  | TRUE
95 | bus_LV_4080-15_0_4_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_4080-15_0_4_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_4080-15_0_4_node_142 | 0.4 | n |  | TRUE
98 | bus_LV_4080-15_0_4_node_143 | 0.4 | n |  | TRUE
99 | bus_LV_4080-15_0_4_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_4080-15_0_4_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_4080-15_0_4_node_88 | 0.4 | n |  | TRUE
102 | bus_LV_4080-15_0_4_node_89 | 0.4 | n |  | TRUE
103 | bus_LV_4080-15_0_4_node_90 | 0.4 | n |  | TRUE
104 | bus_LV_4080-15_0_4_node_91 | 0.4 | n |  | TRUE
105 | bus_LV_4080-15_0_4_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_4080-15_0_4_node_114 | 0.4 | n |  | TRUE
107 | bus_LV_4080-15_0_4_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_4080-15_0_4_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_4080-15_0_4_node_95 | 0.4 | n |  | TRUE
110 | bus_LV_4080-15_0_4_node_96 | 0.4 | n |  | TRUE
111 | bus_LV_4080-15_0_4_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_4080-15_0_4_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_4080-15_0_4_node_175 | 0.4 | n |  | TRUE
114 | bus_LV_4080-15_0_4_node_174 | 0.4 | n |  | TRUE
115 | bus_LV_4080-15_0_4_node_172 | 0.4 | n |  | TRUE
116 | bus_LV_4080-15_0_4_node_136 | 0.4 | n |  | TRUE
117 | bus_LV_4080-15_0_4_node_134 | 0.4 | n |  | TRUE
118 | bus_LV_4080-15_0_4_node_135 | 0.4 | n |  | TRUE
119 | bus_LV_4080-15_0_4_node_105 | 0.4 | n |  | TRUE
120 | bus_LV_4080-15_0_4_node_106 | 0.4 | n |  | TRUE
121 | bus_LV_4080-15_0_4_node_107 | 0.4 | n |  | TRUE
122 | bus_LV_4080-15_0_4_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_4080-15_0_4_node_112 | 0.4 | n |  | TRUE
124 | bus_LV_4080-15_0_4_node_113 | 0.4 | n |  | TRUE
125 | bus_LV_4080-15_0_4_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_4080-15_0_4_node_154 | 0.4 | n |  | TRUE
127 | bus_LV_4080-15_0_4_node_158 | 0.4 | n |  | TRUE
128 | bus_LV_4080-15_0_4_node_117 | 0.4 | n |  | TRUE
129 | bus_LV_4080-15_0_4_node_153 | 0.4 | n |  | TRUE
130 | bus_LV_4080-15_0_4_node_157 | 0.4 | n |  | TRUE
131 | bus_LV_4080-15_0_4_node_116 | 0.4 | n |  | TRUE
132 | bus_LV_4080-15_0_4_node_118 | 0.4 | n |  | TRUE
133 | bus_LV_4080-15_0_4_node_121 | 0.4 | n |  | TRUE
134 | bus_LV_4080-15_0_4_node_122 | 0.4 | n |  | TRUE
135 | bus_LV_4080-15_0_4_node_123 | 0.4 | n |  | TRUE
136 | bus_LV_4080-15_0_4_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_4080-15_0_4_node_126 | 0.4 | n |  | TRUE
138 | bus_LV_4080-15_0_4_node_124 | 0.4 | n |  | TRUE
139 | bus_LV_4080-15_0_4_node_127 | 0.4 | n |  | TRUE
140 | bus_LV_4080-15_0_4_node_128 | 0.4 | n |  | TRUE
141 | bus_LV_4080-15_0_4_node_129 | 0.4 | n |  | TRUE
142 | bus_LV_4080-15_0_4_node_148 | 0.4 | n |  | TRUE
143 | bus_LV_4080-15_0_4_node_156 | 0.4 | n |  | TRUE
144 | bus_LV_4080-15_0_4_node_149 | 0.4 | n |  | TRUE
145 | bus_LV_4080-15_0_4_node_146 | 0.4 | n |  | TRUE
146 | bus_LV_4080-15_0_4_node_155 | 0.4 | n |  | TRUE
147 | bus_LV_4080-15_0_4_node_160 | 0.4 | n |  | TRUE
148 | bus_LV_4080-15_0_4_node_147 | 0.4 | n |  | TRUE
149 | bus_LV_4080-15_0_4_node_130 | 0.4 | n |  | TRUE
150 | bus_LV_4080-15_0_4_node_131 | 0.4 | n |  | TRUE
151 | bus_LV_4080-15_0_4_node_132 | 0.4 | n |  | TRUE
152 | bus_LV_4080-15_0_4_node_133 | 0.4 | n |  | TRUE
153 | bus_LV_4080-15_0_4_node_137 | 0.4 | n |  | TRUE
154 | bus_LV_4080-15_0_4_node_138 | 0.4 | n |  | TRUE
155 | bus_LV_4080-15_0_4_node_139 | 0.4 | n |  | TRUE
156 | bus_LV_4080-15_0_4_node_140 | 0.4 | n |  | TRUE
157 | bus_LV_4080-15_0_4_node_141 | 0.4 | n |  | TRUE
158 | bus_LV_4080-15_0_4_node_151 | 0.4 | n |  | TRUE
159 | bus_LV_4080-15_0_4_node_150 | 0.4 | n |  | TRUE
160 | bus_LV_4080-15_0_4_node_145 | 0.4 | n |  | TRUE
161 | bus_LV_4080-15_0_4_node_161 | 0.4 | n |  | TRUE
162 | bus_LV_4080-15_0_4_node_152 | 0.4 | n |  | TRUE
163 | bus_LV_4080-15_0_4_node_162 | 0.4 | n |  | TRUE
164 | bus_LV_4080-15_0_4_node_165 | 0.4 | n |  | TRUE
165 | bus_LV_4080-15_0_4_node_166 | 0.4 | n |  | TRUE
166 | bus_LV_4080-15_0_4_node_167 | 0.4 | n |  | TRUE
167 | bus_LV_4080-15_0_4_node_168 | 0.4 | n |  | TRUE
168 | bus_LV_4080-15_0_4_node_169 | 0.4 | n |  | TRUE
169 | bus_LV_4080-15_0_4_node_170 | 0.4 | n |  | TRUE
170 | bus_LV_4080-15_0_4_node_171 | 0.4 | n |  | TRUE
171 | bus_LV_4080-15_0_4_node_173 | 0.4 | n |  | TRUE
172 | bus_MV_428_1_node_33 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4080-15_0_4_load_0 | 0 | 0.006306 | 0.0015804 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4080-15_0_4_load_1 | 1 | 0.0092873 | 0.0023276 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4080-15_0_4_load_3 | 3 | 0.0093125 | 0.0023339 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4080-15_0_4_load_5 | 4 | 0.02036 | 0.0051027 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4080-15_0_4_load_6 | 5 | 0.0099154 | 0.002485 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4080-15_0_4_load_7 | 7 | 0.0083127 | 0.0020834 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4080-15_0_4_load_8 | 8 | 0.018244 | 0.0045725 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4080-15_0_4_load_17 | 11 | 0.0083176 | 0.0020846 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4080-15_0_4_load_43 | 12 | 0.0033317 | 0.000835 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4080-15_0_4_load_9 | 14 | 0.0012481 | 0.00031281 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4080-15_0_4_load_10 | 15 | 0.008968 | 0.0022476 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4080-15_0_4_load_12 | 17 | 0.0080443 | 0.0020161 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4080-15_0_4_load_16 | 20 | 0.012104 | 0.0030336 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4080-15_0_4_load_21 | 21 | 0.008061 | 0.0020203 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4080-15_0_4_load_15 | 22 | 0.0024774 | 0.00062089 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4080-15_0_4_load_41 | 26 | 0.0023409 | 0.00058669 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4080-15_0_4_load_42 | 27 | 0.0018589 | 0.00046588 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4080-15_0_4_load_61 | 29 | 0.0082508 | 0.0020678 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4080-15_0_4_load_52 | 30 | 0.0019046 | 0.00047734 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4080-15_0_4_load_23 | 31 | 0.0014267 | 0.00035756 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4080-15_0_4_load_24 | 32 | 0.0048965 | 0.0012272 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4080-15_0_4_load_26 | 34 | 0.0027668 | 0.00069344 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4080-15_0_4_load_163 | 35 | 0.0014837 | 0.00037186 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4080-15_0_4_load_44 | 36 | 0.0082579 | 0.0020696 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4080-15_0_4_load_164 | 37 | 0.0014535 | 0.00036428 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4080-15_0_4_load_51 | 39 | 0.0093295 | 0.0023382 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4080-15_0_4_load_28 | 40 | 0.0053645 | 0.0013445 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4080-15_0_4_load_31 | 43 | 0.0039269 | 0.00098419 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4080-15_0_4_load_66 | 48 | 0.0014232 | 0.00035668 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4080-15_0_4_load_76 | 50 | 0.0070629 | 0.0017701 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4080-15_0_4_load_73 | 51 | 0.0016412 | 0.00041132 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4080-15_0_4_load_34 | 52 | 0.005371 | 0.0013461 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4080-15_0_4_load_39 | 54 | 0.0066239 | 0.0016601 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4080-15_0_4_load_58 | 56 | 0.005287 | 0.001325 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4080-15_0_4_load_54 | 57 | 0.0036512 | 0.00091508 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4080-15_0_4_load_65 | 59 | 0.0032426 | 0.00081268 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4080-15_0_4_load_67 | 60 | 0.0048094 | 0.0012053 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4080-15_0_4_load_78 | 61 | 0.0060203 | 0.0015088 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4080-15_0_4_load_71 | 62 | 0.0017342 | 0.00043462 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4080-15_0_4_load_62 | 65 | 0.0041637 | 0.0010435 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4080-15_0_4_load_56 | 66 | 0.0038603 | 0.00096749 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4080-15_0_4_load_103 | 67 | 0.0016257 | 0.00040745 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4080-15_0_4_load_144 | 69 | 0.0023519 | 0.00058943 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4080-15_0_4_load_48 | 70 | 0.0053927 | 0.0013515 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4080-15_0_4_load_159 | 71 | 0.0021759 | 0.00054533 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4080-15_0_4_load_47 | 72 | 0.0023861 | 0.00059802 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4080-15_0_4_load_49 | 73 | 0.0011435 | 0.0002866 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4080-15_0_4_load_50 | 74 | 0.0017633 | 0.00044194 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4080-15_0_4_load_120 | 75 | 0.0033251 | 0.00083336 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4080-15_0_4_load_98 | 76 | 0.0039407 | 0.00098763 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4080-15_0_4_load_92 | 77 | 0.001811 | 0.00045387 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4080-15_0_4_load_68 | 80 | 0.0021593 | 0.00054117 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4080-15_0_4_load_75 | 82 | 0.0034591 | 0.00086694 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4080-15_0_4_load_72 | 83 | 0.002338 | 0.00058597 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4080-15_0_4_load_102 | 84 | 0.0041579 | 0.0010421 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4080-15_0_4_load_101 | 85 | 0.0024799 | 0.00062153 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4080-15_0_4_load_77 | 86 | 0.0062427 | 0.0015646 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4080-15_0_4_load_104 | 87 | 0.0012999 | 0.0003258 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4080-15_0_4_load_111 | 88 | 0.0061599 | 0.0015438 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4080-15_0_4_load_108 | 89 | 0.0089527 | 0.0022437 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4080-15_0_4_load_79 | 90 | 0.0013207 | 0.00033101 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4080-15_0_4_load_80 | 91 | 0.0024073 | 0.00060332 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4080-15_0_4_load_81 | 92 | 0.0010535 | 0.00026403 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4080-15_0_4_load_83 | 94 | 0.00097361 | 0.00024401 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4080-15_0_4_load_84 | 95 | 0.0014012 | 0.00035117 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4080-15_0_4_load_85 | 96 | 0.00095973 | 0.00024053 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4080-15_0_4_load_142 | 97 | 0.0012521 | 0.0003138 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4080-15_0_4_load_143 | 98 | 0.0013355 | 0.00033471 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4080-15_0_4_load_86 | 99 | 0.0085823 | 0.0021509 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4080-15_0_4_load_87 | 100 | 0.0040205 | 0.0010076 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4080-15_0_4_load_88 | 101 | 0.005047 | 0.0012649 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4080-15_0_4_load_89 | 102 | 0.0021955 | 0.00055025 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4080-15_0_4_load_90 | 103 | 0.0020505 | 0.00051389 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4080-15_0_4_load_91 | 104 | 0.0028642 | 0.00071784 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4080-15_0_4_load_115 | 105 | 0.0028644 | 0.0007179 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4080-15_0_4_load_114 | 106 | 0.012366 | 0.0030993 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4080-15_0_4_load_93 | 107 | 0.0013811 | 0.00034613 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4080-15_0_4_load_94 | 108 | 0.0016492 | 0.00041332 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4080-15_0_4_load_95 | 109 | 0.00055567 | 0.00013926 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4080-15_0_4_load_96 | 110 | 0.0013822 | 0.00034642 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4080-15_0_4_load_175 | 113 | 0.0012316 | 0.00030867 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4080-15_0_4_load_172 | 115 | 0.00067005 | 0.00016793 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4080-15_0_4_load_136 | 116 | 0.00045152 | 0.00011316 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4080-15_0_4_load_134 | 117 | 0.00047378 | 0.00011874 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4080-15_0_4_load_135 | 118 | 0.0026134 | 0.00065498 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4080-15_0_4_load_105 | 119 | 0.003692 | 0.0009253 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4080-15_0_4_load_106 | 120 | 0.0045141 | 0.0011313 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4080-15_0_4_load_112 | 123 | 0.0039362 | 0.00098651 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4080-15_0_4_load_119 | 125 | 0.0034 | 0.00085211 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4080-15_0_4_load_158 | 127 | 0.0014445 | 0.00036204 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4080-15_0_4_load_117 | 128 | 0.003405 | 0.00085337 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4080-15_0_4_load_153 | 129 | 0.00087502 | 0.0002193 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4080-15_0_4_load_116 | 131 | 0.0036406 | 0.00091242 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4080-15_0_4_load_118 | 132 | 0.0036336 | 0.00091067 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4080-15_0_4_load_121 | 133 | 0.0012968 | 0.000325 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4080-15_0_4_load_122 | 134 | 0.0066199 | 0.0016591 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4080-15_0_4_load_125 | 136 | 0.0013658 | 0.00034231 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4080-15_0_4_load_126 | 137 | 0.0012449 | 0.00031199 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4080-15_0_4_load_124 | 138 | 0.0013091 | 0.00032809 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4080-15_0_4_load_127 | 139 | 0.0012213 | 0.00030608 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4080-15_0_4_load_128 | 140 | 0.0012442 | 0.00031184 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4080-15_0_4_load_129 | 141 | 0.0012297 | 0.00030819 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4080-15_0_4_load_148 | 142 | 0.0013466 | 0.00033749 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4080-15_0_4_load_156 | 143 | 0.0014522 | 0.00036396 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4080-15_0_4_load_146 | 145 | 0.0012191 | 0.00030554 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4080-15_0_4_load_155 | 146 | 0.0014368 | 0.0003601 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4080-15_0_4_load_160 | 147 | 0.0012541 | 0.0003143 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4080-15_0_4_load_147 | 148 | 0.0013091 | 0.00032808 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4080-15_0_4_load_130 | 149 | 0.0026741 | 0.00067018 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4080-15_0_4_load_131 | 150 | 0.0028063 | 0.00070332 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4080-15_0_4_load_132 | 151 | 0.0033224 | 0.00083268 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4080-15_0_4_load_133 | 152 | 0.0043892 | 0.0011 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4080-15_0_4_load_137 | 153 | 0.00094057 | 0.00023573 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4080-15_0_4_load_138 | 154 | 0.00097761 | 0.00024501 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4080-15_0_4_load_139 | 155 | 0.00098776 | 0.00024756 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4080-15_0_4_load_140 | 156 | 0.00098615 | 0.00024715 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4080-15_0_4_load_141 | 157 | 0.00092356 | 0.00023147 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4080-15_0_4_load_151 | 158 | 0.00098004 | 0.00024562 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4080-15_0_4_load_150 | 159 | 0.0010625 | 0.00026628 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4080-15_0_4_load_161 | 161 | 0.0011361 | 0.00028474 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4080-15_0_4_load_152 | 162 | 0.0012353 | 0.0003096 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4080-15_0_4_load_162 | 163 | 0.00092841 | 0.00023268 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4080-15_0_4_load_165 | 164 | 0.001586 | 0.0003975 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4080-15_0_4_load_166 | 165 | 0.0027331 | 0.00068499 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4080-15_0_4_load_167 | 166 | 0.0012255 | 0.00030714 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4080-15_0_4_load_168 | 167 | 0.0013747 | 0.00034453 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4080-15_0_4_load_169 | 168 | 0.0026902 | 0.00067422 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4080-15_0_4_load_170 | 169 | 0.0012221 | 0.00030628 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4080-15_0_4_load_171 | 170 | 0.00065363 | 0.00016382 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4080-15_0_4_load_173 | 171 | 0.0051578 | 0.0012927 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4080-15_0_4_line_0 |  | 0 | 1 | 0.031449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4080-15_0_4_line_1 |  | 0 | 2 | 0.05162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4080-15_0_4_line_2 |  | 1 | 3 | 0.030629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4080-15_0_4_line_3 |  | 2 | 4 | 0.059113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4080-15_0_4_line_4 |  | 3 | 5 | 0.030614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4080-15_0_4_line_5 |  | 5 | 9 | 0.03332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4080-15_0_4_line_6 |  | 6 | 7 | 0.055337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4080-15_0_4_line_7 |  | 6 | 8 | 0.017919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4080-15_0_4_line_8 |  | 7 | 10 | 0.029756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4080-15_0_4_line_9 |  | 8 | 11 | 0.038087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4080-15_0_4_line_10 |  | 9 | 12 | 0.013955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_4080-15_0_4_line_11 |  | 9 | 10 | 0.013155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_4080-15_0_4_line_12 |  | 10 | 13 | 0.015608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_4080-15_0_4_line_13 |  | 12 | 28 | 0.021123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_4080-15_0_4_line_14 |  | 13 | 26 | 0.023512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4080-15_0_4_line_15 |  | 13 | 27 | 0.014682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4080-15_0_4_line_16 |  | 14 | 15 | 0.02741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4080-15_0_4_line_17 |  | 14 | 16 | 0.068229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4080-15_0_4_line_18 |  | 15 | 17 | 0.032797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4080-15_0_4_line_19 |  | 16 | 18 | 0.04626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4080-15_0_4_line_20 |  | 17 | 19 | 0.015433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4080-15_0_4_line_21 |  | 18 | 20 | 0.0051723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4080-15_0_4_line_22 |  | 19 | 21 | 0.014564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4080-15_0_4_line_23 |  | 21 | 25 | 0.029548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4080-15_0_4_line_24 |  | 22 | 23 | 0.013723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4080-15_0_4_line_25 |  | 23 | 24 | 0.02198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4080-15_0_4_line_26 |  | 24 | 29 | 0.006949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4080-15_0_4_line_27 |  | 24 | 30 | 0.012296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4080-15_0_4_line_28 |  | 25 | 31 | 0.014742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4080-15_0_4_line_29 |  | 25 | 32 | 0.0087365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4080-15_0_4_line_30 |  | 26 | 67 | 0.0029044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4080-15_0_4_line_31 |  | 27 | 68 | 0.039055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4080-15_0_4_line_32 |  | 28 | 71 | 0.034329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4080-15_0_4_line_33 |  | 28 | 63 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_4080-15_0_4_line_34 |  | 30 | 39 | 0.0037768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4080-15_0_4_line_35 |  | 31 | 33 | 0.011494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4080-15_0_4_line_36 |  | 32 | 34 | 0.019756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4080-15_0_4_line_37 |  | 33 | 35 | 0.017267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4080-15_0_4_line_38 |  | 34 | 36 | 0.011239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4080-15_0_4_line_39 |  | 35 | 37 | 0.01185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4080-15_0_4_line_40 |  | 36 | 38 | 0.0064704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4080-15_0_4_line_41 |  | 37 | 164 | 0.0062802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4080-15_0_4_line_42 |  | 38 | 72 | 0.01532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4080-15_0_4_line_43 |  | 38 | 68 | 0.014608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4080-15_0_4_line_44 |  | 39 | 74 | 0.016857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4080-15_0_4_line_45 |  | 40 | 41 | 0.011736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4080-15_0_4_line_46 |  | 40 | 42 | 0.019102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4080-15_0_4_line_47 |  | 41 | 43 | 0.029816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4080-15_0_4_line_48 |  | 42 | 44 | 0.010445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4080-15_0_4_line_49 |  | 43 | 45 | 0.012196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4080-15_0_4_line_50 |  | 44 | 54 | 0.016223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_4080-15_0_4_line_51 |  | 44 | 49 | 0.031922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
52 | LV_4080-15_0_4_line_52 |  | 45 | 58 | 0.026452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4080-15_0_4_line_53 |  | 46 | 47 | 0.024568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4080-15_0_4_line_54 |  | 46 | 48 | 0.024237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4080-15_0_4_line_55 |  | 47 | 59 | 0.01906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4080-15_0_4_line_56 |  | 48 | 60 | 0.00015226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4080-15_0_4_line_57 |  | 49 | 50 | 0.02516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_4080-15_0_4_line_58 |  | 49 | 51 | 0.020251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4080-15_0_4_line_59 |  | 50 | 61 | 0.031426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_4080-15_0_4_line_60 |  | 51 | 62 | 0.031058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4080-15_0_4_line_61 |  | 52 | 53 | 0.013995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4080-15_0_4_line_62 |  | 53 | 63 | 0.015761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4080-15_0_4_line_63 |  | 54 | 63 | 0.01588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_4080-15_0_4_line_64 |  | 55 | 56 | 0.012958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4080-15_0_4_line_65 |  | 55 | 57 | 0.020503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4080-15_0_4_line_66 |  | 57 | 64 | 0.017958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4080-15_0_4_line_67 |  | 58 | 65 | 0.0037726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4080-15_0_4_line_68 |  | 58 | 66 | 0.023214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4080-15_0_4_line_69 |  | 59 | 79 | 0.019032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4080-15_0_4_line_70 |  | 60 | 80 | 0.026211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4080-15_0_4_line_71 |  | 61 | 88 | 0.00761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4080-15_0_4_line_72 |  | 62 | 83 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4080-15_0_4_line_73 |  | 64 | 66 | 0.015495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4080-15_0_4_line_74 |  | 65 | 78 | 0.024485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4080-15_0_4_line_75 |  | 67 | 69 | 0.011758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4080-15_0_4_line_76 |  | 68 | 70 | 0.022112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4080-15_0_4_line_77 |  | 69 | 118 | 0.018707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4080-15_0_4_line_78 |  | 70 | 74 | 0.0084296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4080-15_0_4_line_79 |  | 71 | 77 | 0.00020497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4080-15_0_4_line_80 |  | 72 | 73 | 0.024224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4080-15_0_4_line_81 |  | 73 | 75 | 0.00016602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4080-15_0_4_line_82 |  | 75 | 76 | 0.014893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4080-15_0_4_line_83 |  | 76 | 110 | 0.01234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4080-15_0_4_line_84 |  | 77 | 103 | 7.8147e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4080-15_0_4_line_85 |  | 78 | 79 | 0.024275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4080-15_0_4_line_86 |  | 81 | 82 | 0.027021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4080-15_0_4_line_87 |  | 81 | 83 | 0.0086089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4080-15_0_4_line_88 |  | 82 | 86 | 0.011373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4080-15_0_4_line_89 |  | 84 | 85 | 0.028932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4080-15_0_4_line_90 |  | 85 | 95 | 0.0077779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4080-15_0_4_line_91 |  | 86 | 87 | 0.0043092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4080-15_0_4_line_92 |  | 88 | 89 | 0.034747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4080-15_0_4_line_93 |  | 89 | 120 | 0.017777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4080-15_0_4_line_94 |  | 90 | 91 | 0.01334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4080-15_0_4_line_95 |  | 90 | 92 | 0.003473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4080-15_0_4_line_96 |  | 91 | 93 | 0.013902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4080-15_0_4_line_97 |  | 92 | 94 | 0.00063678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4080-15_0_4_line_98 |  | 93 | 95 | 0.011796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4080-15_0_4_line_99 |  | 94 | 96 | 0.0058618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4080-15_0_4_line_100 |  | 96 | 97 | 0.01285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4080-15_0_4_line_101 |  | 97 | 98 | 0.004478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4080-15_0_4_line_102 |  | 98 | 160 | 0.005827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4080-15_0_4_line_103 |  | 99 | 100 | 0.006668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4080-15_0_4_line_104 |  | 99 | 101 | 0.010832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4080-15_0_4_line_105 |  | 100 | 102 | 0.032484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4080-15_0_4_line_106 |  | 101 | 103 | 0.018247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4080-15_0_4_line_107 |  | 102 | 104 | 0.0083501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4080-15_0_4_line_108 |  | 104 | 105 | 8.1899e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4080-15_0_4_line_109 |  | 105 | 106 | 0.014863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4080-15_0_4_line_110 |  | 107 | 108 | 0.021545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4080-15_0_4_line_111 |  | 107 | 109 | 0.016517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4080-15_0_4_line_112 |  | 108 | 110 | 0.0081719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4080-15_0_4_line_113 |  | 109 | 111 | 0.028719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4080-15_0_4_line_114 |  | 111 | 112 | 0.047696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4080-15_0_4_line_115 |  | 112 | 113 | 0.028963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4080-15_0_4_line_116 |  | 112 | 114 | 0.024763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4080-15_0_4_line_117 |  | 114 | 115 | 0.050233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4080-15_0_4_line_118 |  | 115 | 169 | 0.0015509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4080-15_0_4_line_119 |  | 116 | 117 | 0.028955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4080-15_0_4_line_120 |  | 117 | 151 | 0.0021408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4080-15_0_4_line_121 |  | 118 | 152 | 0.00034037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4080-15_0_4_line_122 |  | 119 | 120 | 0.024573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4080-15_0_4_line_123 |  | 119 | 121 | 0.019021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4080-15_0_4_line_124 |  | 121 | 122 | 0.044002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4080-15_0_4_line_125 |  | 122 | 123 | 0.021635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4080-15_0_4_line_126 |  | 122 | 124 | 0.065925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4080-15_0_4_line_127 |  | 123 | 125 | 5.96e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4080-15_0_4_line_128 |  | 124 | 126 | 0.023541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4080-15_0_4_line_129 |  | 124 | 127 | 0.0077063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4080-15_0_4_line_130 |  | 125 | 128 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4080-15_0_4_line_131 |  | 126 | 129 | 0.0050013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4080-15_0_4_line_132 |  | 127 | 130 | 0.01451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4080-15_0_4_line_133 |  | 128 | 131 | 0.011444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4080-15_0_4_line_134 |  | 129 | 162 | 0.0036368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4080-15_0_4_line_135 |  | 130 | 146 | 0.018345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4080-15_0_4_line_136 |  | 131 | 132 | 0.00533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4080-15_0_4_line_137 |  | 133 | 134 | 0.0033893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4080-15_0_4_line_138 |  | 133 | 135 | 0.0079429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4080-15_0_4_line_139 |  | 135 | 136 | 0.016488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4080-15_0_4_line_140 |  | 135 | 137 | 0.0067961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4080-15_0_4_line_141 |  | 136 | 140 | 0.006192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4080-15_0_4_line_142 |  | 137 | 141 | 0.0057511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4080-15_0_4_line_143 |  | 138 | 139 | 0.0048719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4080-15_0_4_line_144 |  | 139 | 142 | 0.0032303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4080-15_0_4_line_145 |  | 140 | 143 | 0.019947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4080-15_0_4_line_146 |  | 141 | 144 | 0.010295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4080-15_0_4_line_147 |  | 142 | 145 | 0.0077402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4080-15_0_4_line_148 |  | 143 | 146 | 0.003907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4080-15_0_4_line_149 |  | 144 | 147 | 0.0064523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4080-15_0_4_line_150 |  | 144 | 148 | 0.0089015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4080-15_0_4_line_151 |  | 145 | 160 | 0.011939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4080-15_0_4_line_152 |  | 147 | 161 | 0.0083933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4080-15_0_4_line_153 |  | 148 | 160 | 0.011749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4080-15_0_4_line_154 |  | 149 | 150 | 0.0011601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4080-15_0_4_line_155 |  | 149 | 151 | 0.023342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4080-15_0_4_line_156 |  | 150 | 152 | 0.017366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4080-15_0_4_line_157 |  | 153 | 154 | 0.0023577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4080-15_0_4_line_158 |  | 153 | 155 | 0.0028956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4080-15_0_4_line_159 |  | 154 | 156 | 0.018027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4080-15_0_4_line_160 |  | 156 | 157 | 0.010221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4080-15_0_4_line_161 |  | 157 | 158 | 0.0044427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4080-15_0_4_line_162 |  | 158 | 159 | 0.0018936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4080-15_0_4_line_163 |  | 159 | 162 | 0.002954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4080-15_0_4_line_164 |  | 161 | 163 | 0.016951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4080-15_0_4_line_165 |  | 164 | 165 | 0.0040492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4080-15_0_4_line_166 |  | 165 | 166 | 0.016811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4080-15_0_4_line_167 |  | 166 | 167 | 0.0057667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4080-15_0_4_line_168 |  | 167 | 168 | 0.0020351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4080-15_0_4_line_169 |  | 169 | 170 | 0.0046352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4080-15_0_4_line_170 |  | 170 | 171 | 0.0028733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4080-15_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 172 | 12 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2661382.6857 | 1244599.9813 | 2661365.1974 | 1244626.1196
1 | 2661421.9763 | 1244601.5511 | 2661392.692 | 1244585.0257 | 2661382.6857 | 1244599.9813
2 | 2661348.1651 | 1244651.5763 | 2661365.1974 | 1244626.1196
3 | 2661421.9763 | 1244601.5511 | 2661457.0184 | 1244623.918 | 2661447.0432 | 1244638.3463
4 | 2661331.1413 | 1244677.0203 | 2661348.1651 | 1244651.5763
5 | 2661324.5686 | 1244702.8019 | 2661331.5953 | 1244691.1888 | 2661324.7516 | 1244686.5705 | 2661331.1413 | 1244677.0203
6 | 2661386.9496 | 1244652.1455 | 2661355.4451 | 1244697.6393
7 | 2661386.9496 | 1244652.1455 | 2661401.7563 | 1244662.238
8 | 2661335.0652 | 1244710.7714 | 2661343.3349 | 1244700.2497 | 2661350.9954 | 1244704.0648 | 2661355.4451 | 1244697.6393
9 | 2661403.5924 | 1244689.7493 | 2661415.2903 | 1244671.463 | 2661401.7563 | 1244662.238
10 | 2661324.5686 | 1244702.8019 | 2661313.2662 | 1244694.6171
11 | 2661324.5686 | 1244702.8019 | 2661335.0652 | 1244710.7714
12 | 2661347.5261 | 1244720.2178 | 2661335.0652 | 1244710.7714
13 | 2661296.1577 | 1244682.2277 | 2661313.2662 | 1244694.6171
14 | 2661347.5261 | 1244720.2178 | 2661331.8768 | 1244737.7657
15 | 2661347.5261 | 1244720.2178 | 2661358.9573 | 1244728.4082 | 2661359.4591 | 1244728.7707
16 | 2661515.5709 | 1244706.4652 | 2661498.0609 | 1244727.5536
17 | 2661507.4878 | 1244656.0184 | 2661510.9847 | 1244656.1881 | 2661519.921 | 1244659.3829 | 2661527.4058 | 1244667.0212 | 2661530.2062 | 1244676.7792 | 2661530.3116 | 1244684.8302 | 2661525.2511 | 1244694.8068 | 2661515.5709 | 1244706.4652
18 | 2661476.5521 | 1244752.3038 | 2661488.6289 | 1244738.913 | 2661498.0609 | 1244727.5536
19 | 2661507.4878 | 1244656.0184 | 2661501.0681 | 1244655.6961 | 2661489.5925 | 1244656.9002 | 2661472.0493 | 1244662.4556 | 2661465.6974 | 1244670.184
20 | 2661466.2161 | 1244763.7645 | 2661476.5521 | 1244752.3038
21 | 2661465.6974 | 1244670.184 | 2661462.4179 | 1244674.1837
22 | 2661466.2161 | 1244763.7645 | 2661455.77 | 1244773.913
23 | 2661434.5768 | 1244794.5024 | 2661455.77 | 1244773.913
24 | 2661446.2391 | 1244732.9477 | 2661454.9416 | 1244730.992 | 2661458.2856 | 1244727.5434
25 | 2661437.9879 | 1244718.33 | 2661439.7033 | 1244733.636 | 2661443.8762 | 1244733.468 | 2661446.2391 | 1244732.9477
26 | 2661444.8681 | 1244717.2227 | 2661437.9879 | 1244718.33
27 | 2661437.9879 | 1244718.33 | 2661425.8484 | 1244720.2878
28 | 2661434.5768 | 1244794.5024 | 2661445.4824 | 1244804.422
29 | 2661434.5768 | 1244794.5024 | 2661428.1135 | 1244788.6242
30 | 2661329.9437 | 1244739.9333 | 2661331.8768 | 1244737.7657
31 | 2661389.6103 | 1244753.5313 | 2661385.6431 | 1244749.8989 | 2661370.1553 | 1244736.4962 | 2661359.4591 | 1244728.7707
32 | 2661296.1577 | 1244682.2277 | 2661276.1623 | 1244710.1325
33 | 2661285.3346 | 1244674.3994 | 2661296.1577 | 1244682.2277
34 | 2661422.1197 | 1244720.8891 | 2661425.8484 | 1244720.2878
35 | 2661453.7734 | 1244812.3801 | 2661448.1409 | 1244806.8402 | 2661445.4824 | 1244804.422
36 | 2661413.498 | 1244775.3317 | 2661428.1135 | 1244788.6242
37 | 2661453.7734 | 1244812.3801 | 2661442.8815 | 1244825.7782
38 | 2661405.1835 | 1244767.7698 | 2661413.498 | 1244775.3317
39 | 2661442.8815 | 1244825.7782 | 2661435.4068 | 1244834.9728
40 | 2661400.3967 | 1244763.4163 | 2661405.1835 | 1244767.7698
41 | 2661431.4452 | 1244839.8459 | 2661435.4068 | 1244834.9728
42 | 2661400.3967 | 1244763.4163 | 2661389.8581 | 1244774.5363
43 | 2661400.3967 | 1244763.4163 | 2661394.6564 | 1244758.0644 | 2661389.6103 | 1244753.5313
44 | 2661422.1197 | 1244720.8891 | 2661416.0907 | 1244721.8614 | 2661408.96 | 1244729.9058
45 | 2661274.2999 | 1244616.1123 | 2661271.1445 | 1244627.416
46 | 2661263.9056 | 1244645.047 | 2661269.8743 | 1244631.9663 | 2661271.1445 | 1244627.416
47 | 2661274.2999 | 1244616.1123 | 2661287.9566 | 1244589.5907
48 | 2661259.9669 | 1244654.7241 | 2661263.1613 | 1244646.8739 | 2661263.9056 | 1244645.047
49 | 2661293.5396 | 1244578.741 | 2661287.9566 | 1244589.5907
50 | 2661259.9669 | 1244654.7241 | 2661272.7863 | 1244664.6668
51 | 2661259.9669 | 1244654.7241 | 2661245.0588 | 1244644.4076 | 2661233.9149 | 1244636.1759
52 | 2661304.3679 | 1244554.6363 | 2661298.6524 | 1244568.7981 | 2661293.5396 | 1244578.741
53 | 2661264.021 | 1244576.0788 | 2661274.7456 | 1244553.9633
54 | 2661264.021 | 1244576.0788 | 2661257.3496 | 1244573.0523 | 2661243.7999 | 1244562.9328
55 | 2661274.7456 | 1244553.9633 | 2661282.1978 | 1244536.421
56 | 2661243.7999 | 1244562.9328 | 2661243.6779 | 1244562.8417
57 | 2661233.9149 | 1244636.1759 | 2661228.1438 | 1244647.6909 | 2661222.7356 | 1244658.7156
58 | 2661233.9149 | 1244636.1759 | 2661223.1288 | 1244628.4149 | 2661217.6126 | 1244624.1663
59 | 2661222.7356 | 1244658.7156 | 2661208.8953 | 1244686.9295
60 | 2661193.0068 | 1244605.2151 | 2661217.6126 | 1244624.1663
61 | 2661292.4095 | 1244660.3073 | 2661279.7228 | 1244654.4001
62 | 2661285.3346 | 1244674.3994 | 2661292.4095 | 1244660.3073
63 | 2661285.3346 | 1244674.3994 | 2661272.7863 | 1244664.6668
64 | 2661318.8803 | 1244607.6336 | 2661313.0616 | 1244619.2121
65 | 2661318.8803 | 1244607.6336 | 2661328.085 | 1244589.3129
66 | 2661336.1472 | 1244573.2663 | 2661328.085 | 1244589.3129
67 | 2661304.3679 | 1244554.6363 | 2661306.071 | 1244551.27
68 | 2661304.3679 | 1244554.6363 | 2661310.8381 | 1244563.9762 | 2661318.494 | 1244564.6002 | 2661322.2381 | 1244566.4382
69 | 2661289.6391 | 1244518.9042 | 2661282.1978 | 1244536.421
70 | 2661243.6779 | 1244562.8417 | 2661222.6772 | 1244547.1575
71 | 2661205.5437 | 1244693.7617 | 2661208.8953 | 1244686.9295
72 | 2661193.0068 | 1244605.2151 | 2661184.1356 | 1244598.3825
73 | 2661336.1472 | 1244573.2663 | 2661322.2381 | 1244566.4382
74 | 2661311.6115 | 1244529.3605 | 2661307.0984 | 1244537.5751 | 2661309.7679 | 1244543.9626 | 2661306.071 | 1244551.27
75 | 2661329.9437 | 1244739.9333 | 2661322.1176 | 1244748.7089
76 | 2661389.6103 | 1244753.5313 | 2661403.5108 | 1244736.3345
77 | 2661322.1176 | 1244748.7089 | 2661309.6664 | 1244762.6706
78 | 2661403.5108 | 1244736.3345 | 2661406.0902 | 1244733.1434 | 2661408.96 | 1244729.9058
79 | 2661276.1623 | 1244710.1325 | 2661276.0429 | 1244710.2991
80 | 2661389.8581 | 1244774.5363 | 2661373.195 | 1244792.1189
81 | 2661373.195 | 1244792.1189 | 2661373.0808 | 1244792.2394
82 | 2661373.0808 | 1244792.2394 | 2661362.8361 | 1244803.0493
83 | 2661362.8361 | 1244803.0493 | 2661354.3478 | 1244812.006
84 | 2661276.0429 | 1244710.2991 | 2661275.9974 | 1244710.3626
85 | 2661289.6391 | 1244518.9042 | 2661311.6115 | 1244529.3605
86 | 2661177.3151 | 1244593.1294 | 2661164.8655 | 1244617.1116
87 | 2661177.3151 | 1244593.1294 | 2661184.1356 | 1244598.3825
88 | 2661164.8655 | 1244617.1116 | 2661159.6254 | 1244627.2057
89 | 2661094.0681 | 1244602.4481 | 2661094.832 | 1244600.8183 | 2661106.5348 | 1244576.3395
90 | 2661094.0681 | 1244602.4481 | 2661090.7673 | 1244609.4908
91 | 2661157.64 | 1244631.0303 | 2661159.6254 | 1244627.2057
92 | 2661205.5437 | 1244693.7617 | 2661190.2408 | 1244724.9571
93 | 2661182.4106 | 1244740.9162 | 2661185.6518 | 1244734.3119 | 2661190.2408 | 1244724.9571
94 | 2661101.4583 | 1244638.0611 | 2661100.5253 | 1244629.8412 | 2661098.128 | 1244628.5601 | 2661098.2806 | 1244626.2157 | 2661098.2806 | 1244626.2157
95 | 2661099.7989 | 1244640.9413 | 2661099.7989 | 1244640.9413 | 2661101.5298 | 1244638.691 | 2661101.4583 | 1244638.0611
96 | 2661085.7613 | 1244620.1715 | 2661098.2806 | 1244626.2157
97 | 2661099.862 | 1244641.575 | 2661099.7989 | 1244640.9413
98 | 2661085.7613 | 1244620.1715 | 2661090.7673 | 1244609.4908
99 | 2661100.4426 | 1244647.408 | 2661099.862 | 1244641.575
100 | 2661100.4426 | 1244647.408 | 2661113.2468 | 1244646.3278
101 | 2661113.2468 | 1244646.3278 | 2661117.709 | 1244645.9514
102 | 2661118.0268 | 1244651.7698 | 2661117.709 | 1244645.9514 | 2661117.709 | 1244645.9514
103 | 2661259.0599 | 1244733.9999 | 2661255.1761 | 1244739.4201
104 | 2661259.0599 | 1244733.9999 | 2661265.3692 | 1244725.195
105 | 2661236.0968 | 1244765.7062 | 2661239.2233 | 1244761.6832 | 2661255.1761 | 1244739.4201
106 | 2661275.9974 | 1244710.3626 | 2661265.3692 | 1244725.195
107 | 2661236.0968 | 1244765.7062 | 2661231.4657 | 1244771.6655 | 2661231.0059 | 1244772.3236
108 | 2661231.0059 | 1244772.3236 | 2661230.959 | 1244772.3908
109 | 2661222.4468 | 1244784.5746 | 2661230.959 | 1244772.3908
110 | 2661334.1612 | 1244833.8123 | 2661348.1487 | 1244818.547 | 2661348.7266 | 1244817.9373
111 | 2661334.1612 | 1244833.8123 | 2661323.0027 | 1244845.9902
112 | 2661348.7266 | 1244817.9373 | 2661354.3478 | 1244812.006
113 | 2661303.6008 | 1244867.1644 | 2661323.0027 | 1244845.9902
114 | 2661303.6008 | 1244867.1644 | 2661307.6425 | 1244870.9088 | 2661339.5157 | 1244898.5459
115 | 2661339.5157 | 1244898.5459 | 2661358.4594 | 1244876.5934
116 | 2661339.5157 | 1244898.5459 | 2661354.3214 | 1244911.3855 | 2661358.0314 | 1244915.0375
117 | 2661358.0314 | 1244915.0375 | 2661361.1 | 1244912.045 | 2661387.3304 | 1244874.3213
118 | 2661387.3304 | 1244874.3213 | 2661388.2157 | 1244873.0479
119 | 2661280.1459 | 1244795.7679 | 2661260.8706 | 1244817.3743
120 | 2661281.571 | 1244794.1704 | 2661280.1459 | 1244795.7679
121 | 2661309.6664 | 1244762.6706 | 2661309.4399 | 1244762.9246
122 | 2661171.5844 | 1244762.9757 | 2661182.4106 | 1244740.9162
123 | 2661163.4544 | 1244780.17 | 2661168.1153 | 1244770.0445 | 2661171.5844 | 1244762.9757
124 | 2661125.8806 | 1244757.0893 | 2661153.2589 | 1244773.7717 | 2661163.4544 | 1244780.17
125 | 2661125.8806 | 1244757.0893 | 2661135.459 | 1244737.6899
126 | 2661089.722 | 1244718.3683 | 2661081.8366 | 1244730.5066 | 2661090.4164 | 1244736.0542 | 2661125.8806 | 1244757.0893
127 | 2661135.4854 | 1244737.6365 | 2661135.459 | 1244737.6899
128 | 2661069.6823 | 1244705.9202 | 2661089.722 | 1244718.3683
129 | 2661089.722 | 1244718.3683 | 2661096.2535 | 1244722.4582
130 | 2661135.4854 | 1244737.6365 | 2661144.3388 | 1244719.7054
131 | 2661069.6823 | 1244705.9202 | 2661072.5507 | 1244701.8233
132 | 2661108.5519 | 1244730.1591 | 2661096.2535 | 1244722.4582
133 | 2661149.4054 | 1244709.4438 | 2661144.3388 | 1244719.7054
134 | 2661072.5507 | 1244701.8233 | 2661074.6365 | 1244698.8442
135 | 2661108.5519 | 1244730.1591 | 2661113.6344 | 1244721.639 | 2661115.3874 | 1244720.1783 | 2661118.0839 | 1244714.66
136 | 2661151.7651 | 1244704.6646 | 2661149.4054 | 1244709.4438
137 | 2661142.0462 | 1244665.7364 | 2661143.5534 | 1244662.7006
138 | 2661138.5142 | 1244672.8508 | 2661142.0462 | 1244665.7364
139 | 2661138.5142 | 1244672.8508 | 2661131.2752 | 1244687.6648
140 | 2661138.5142 | 1244672.8508 | 2661136.4553 | 1244672.4626 | 2661131.7625 | 1244672.7398
141 | 2661128.5567 | 1244693.2282 | 2661131.2752 | 1244687.6648
142 | 2661131.7625 | 1244672.7398 | 2661126.0214 | 1244673.079
143 | 2661144.2745 | 1244651.257 | 2661141.5106 | 1244651.2002 | 2661140.1632 | 1244649.9632 | 2661139.8864 | 1244649.992
144 | 2661136.6734 | 1244650.3264 | 2661139.8864 | 1244649.992
145 | 2661128.5567 | 1244693.2282 | 2661119.7993 | 1244711.1497
146 | 2661117.4655 | 1244671.7777 | 2661117.5452 | 1244673.5797 | 2661126.0214 | 1244673.079
147 | 2661129.3798 | 1244649.7792 | 2661130.3651 | 1244649.7065 | 2661131.706 | 1244650.8434 | 2661136.6734 | 1244650.3264
148 | 2661119.7993 | 1244711.1497 | 2661118.0839 | 1244714.66
149 | 2661117.4655 | 1244671.7777 | 2661111.4194 | 1244671.871 | 2661111.0638 | 1244672.0657
150 | 2661117.4655 | 1244671.7777 | 2661117.0832 | 1244662.8844
151 | 2661118.0268 | 1244651.7698 | 2661127.5558 | 1244651.0118 | 2661128.5124 | 1244649.8431 | 2661129.3798 | 1244649.7792
152 | 2661103.2902 | 1244674.8386 | 2661104.0733 | 1244674.197 | 2661108.9876 | 1244673.2025 | 2661111.0638 | 1244672.0657
153 | 2661118.0268 | 1244651.7698 | 2661118.5304 | 1244660.8367 | 2661117.0571 | 1244662.2781 | 2661117.0832 | 1244662.8844
154 | 2661297.109 | 1244776.7515 | 2661297.8812 | 1244775.8856
155 | 2661281.571 | 1244794.1704 | 2661292.2989 | 1244782.1451 | 2661297.109 | 1244776.7515
156 | 2661309.4399 | 1244762.9246 | 2661297.8812 | 1244775.8856
157 | 2661087.5926 | 1244668.3344 | 2661087.5926 | 1244668.3344 | 2661086.6184 | 1244670.4814
158 | 2661087.3659 | 1244665.4478 | 2661087.5926 | 1244668.3344
159 | 2661077.1843 | 1244681.6152 | 2661083.2836 | 1244680.9876 | 2661086.4458 | 1244677.7068 | 2661086.2546 | 1244674.258 | 2661086.8474 | 1244672.4629 | 2661086.6184 | 1244670.4814
160 | 2661075.7132 | 1244690.4161 | 2661077.3147 | 1244689.7322 | 2661076.8009 | 1244681.6547 | 2661077.1843 | 1244681.6152
161 | 2661075.7132 | 1244690.4161 | 2661075.7132 | 1244690.4161 | 2661075.9093 | 1244694.8545 | 2661075.9093 | 1244694.8545
162 | 2661074.3343 | 1244695.9057 | 2661075.9093 | 1244694.8545
163 | 2661074.6365 | 1244698.8442 | 2661074.6365 | 1244698.8442 | 2661074.3343 | 1244695.9057 | 2661074.3343 | 1244695.9057
164 | 2661104.4023 | 1244689.1995 | 2661104.2835 | 1244686.7966 | 2661101.1003 | 1244684.0509 | 2661100.9106 | 1244676.7884 | 2661103.2902 | 1244674.8386
165 | 2661428.891 | 1244842.9879 | 2661431.4452 | 1244839.8459
166 | 2661429.3261 | 1244857.652 | 2661431.9983 | 1244853.7607 | 2661432.0842 | 1244846.2009 | 2661428.891 | 1244842.9879 | 2661428.891 | 1244842.9879
167 | 2661426.0616 | 1244862.4057 | 2661429.3261 | 1244857.652
168 | 2661424.9095 | 1244864.0833 | 2661426.0616 | 1244862.4057
169 | 2661388.2157 | 1244873.0479 | 2661390.8619 | 1244869.2423
170 | 2661392.5022 | 1244866.8832 | 2661390.8619 | 1244869.2423

## bus_geodata
| x | y | coords
0 | 2661382.6857 | 1244599.9813
1 | 2661365.1974 | 1244626.1196
2 | 2661421.9763 | 1244601.5511
3 | 2661348.1651 | 1244651.5763
4 | 2661447.0432 | 1244638.3463
5 | 2661331.1413 | 1244677.0203
6 | 2661386.9496 | 1244652.1455
7 | 2661355.4451 | 1244697.6393
8 | 2661401.7563 | 1244662.238
9 | 2661324.5686 | 1244702.8019
10 | 2661335.0652 | 1244710.7714
11 | 2661403.5924 | 1244689.7493
12 | 2661313.2662 | 1244694.6171
13 | 2661347.5261 | 1244720.2178
14 | 2661515.5709 | 1244706.4652
15 | 2661498.0609 | 1244727.5536
16 | 2661507.4878 | 1244656.0184
17 | 2661476.5521 | 1244752.3038
18 | 2661465.6974 | 1244670.184
19 | 2661466.2161 | 1244763.7645
20 | 2661462.4179 | 1244674.1837
21 | 2661455.77 | 1244773.913
22 | 2661458.2856 | 1244727.5434
23 | 2661446.2391 | 1244732.9477
24 | 2661437.9879 | 1244718.33
25 | 2661434.5768 | 1244794.5024
26 | 2661331.8768 | 1244737.7657
27 | 2661359.4591 | 1244728.7707
28 | 2661296.1577 | 1244682.2277
29 | 2661444.8681 | 1244717.2227
30 | 2661425.8484 | 1244720.2878
31 | 2661445.4824 | 1244804.422
32 | 2661428.1135 | 1244788.6242
33 | 2661453.7734 | 1244812.3801
34 | 2661413.498 | 1244775.3317
35 | 2661442.8815 | 1244825.7782
36 | 2661405.1835 | 1244767.7698
37 | 2661435.4068 | 1244834.9728
38 | 2661400.3967 | 1244763.4163
39 | 2661422.1197 | 1244720.8891
40 | 2661271.1445 | 1244627.416
41 | 2661274.2999 | 1244616.1123
42 | 2661263.9056 | 1244645.047
43 | 2661287.9566 | 1244589.5907
44 | 2661259.9669 | 1244654.7241
45 | 2661293.5396 | 1244578.741
46 | 2661264.021 | 1244576.0788
47 | 2661274.7455 | 1244553.9633
48 | 2661243.7999 | 1244562.9328
49 | 2661233.9149 | 1244636.1759
50 | 2661222.7356 | 1244658.7156
51 | 2661217.6126 | 1244624.1663
52 | 2661279.7228 | 1244654.4001
53 | 2661292.4095 | 1244660.3073
54 | 2661272.7863 | 1244664.6668
55 | 2661318.8803 | 1244607.6336
56 | 2661313.0616 | 1244619.2121
57 | 2661328.085 | 1244589.3129
58 | 2661304.3679 | 1244554.6363
59 | 2661282.1978 | 1244536.421
60 | 2661243.6779 | 1244562.8417
61 | 2661208.8953 | 1244686.9295
62 | 2661193.0068 | 1244605.2151
63 | 2661285.3346 | 1244674.3994
64 | 2661336.1472 | 1244573.2663
65 | 2661306.071 | 1244551.27
66 | 2661322.2381 | 1244566.4382
67 | 2661329.9437 | 1244739.9333
68 | 2661389.6103 | 1244753.5313
69 | 2661322.1176 | 1244748.7089
70 | 2661403.5108 | 1244736.3345
71 | 2661276.1623 | 1244710.1325
72 | 2661389.8581 | 1244774.5363
73 | 2661373.195 | 1244792.1189
74 | 2661408.96 | 1244729.9058
75 | 2661373.0808 | 1244792.2394
76 | 2661362.8361 | 1244803.0493
77 | 2661276.0429 | 1244710.2991
78 | 2661311.6115 | 1244529.3605
79 | 2661289.6391 | 1244518.9042
80 | 2661222.6772 | 1244547.1575
81 | 2661177.3151 | 1244593.1294
82 | 2661164.8655 | 1244617.1116
83 | 2661184.1356 | 1244598.3825
84 | 2661106.5348 | 1244576.3395
85 | 2661094.0681 | 1244602.4481
86 | 2661159.6254 | 1244627.2057
87 | 2661157.64 | 1244631.0303
88 | 2661205.5437 | 1244693.7617
89 | 2661190.2408 | 1244724.9571
90 | 2661101.4583 | 1244638.0611
91 | 2661098.2806 | 1244626.2157
92 | 2661099.7989 | 1244640.9413
93 | 2661085.7613 | 1244620.1715
94 | 2661099.862 | 1244641.575
95 | 2661090.7673 | 1244609.4908
96 | 2661100.4426 | 1244647.408
97 | 2661113.2468 | 1244646.3278
98 | 2661117.709 | 1244645.9514
99 | 2661259.0599 | 1244733.9999
100 | 2661255.1761 | 1244739.4201
101 | 2661265.3692 | 1244725.195
102 | 2661236.0968 | 1244765.7062
103 | 2661275.9974 | 1244710.3626
104 | 2661231.0059 | 1244772.3236
105 | 2661230.959 | 1244772.3908
106 | 2661222.4468 | 1244784.5746
107 | 2661334.1612 | 1244833.8123
108 | 2661348.7266 | 1244817.9373
109 | 2661323.0027 | 1244845.9902
110 | 2661354.3478 | 1244812.006
111 | 2661303.6008 | 1244867.1644
112 | 2661339.5157 | 1244898.5459
113 | 2661358.4594 | 1244876.5934
114 | 2661358.0314 | 1244915.0375
115 | 2661387.3304 | 1244874.3213
116 | 2661260.8706 | 1244817.3743
117 | 2661280.1459 | 1244795.7679
118 | 2661309.6664 | 1244762.6706
119 | 2661171.5844 | 1244762.9757
120 | 2661182.4106 | 1244740.9162
121 | 2661163.4544 | 1244780.17
122 | 2661125.8806 | 1244757.0893
123 | 2661135.459 | 1244737.6899
124 | 2661089.722 | 1244718.3683
125 | 2661135.4854 | 1244737.6365
126 | 2661069.6823 | 1244705.9202
127 | 2661096.2535 | 1244722.4582
128 | 2661144.3388 | 1244719.7054
129 | 2661072.5507 | 1244701.8233
130 | 2661108.5519 | 1244730.1591
131 | 2661149.4054 | 1244709.4438
132 | 2661151.7651 | 1244704.6646
133 | 2661142.0462 | 1244665.7364
134 | 2661143.5534 | 1244662.7006
135 | 2661138.5142 | 1244672.8508
136 | 2661131.2752 | 1244687.6648
137 | 2661131.7625 | 1244672.7398
138 | 2661144.2745 | 1244651.257
139 | 2661139.8864 | 1244649.992
140 | 2661128.5567 | 1244693.2282
141 | 2661126.0215 | 1244673.079
142 | 2661136.6734 | 1244650.3264
143 | 2661119.7993 | 1244711.1497
144 | 2661117.4655 | 1244671.7777
145 | 2661129.3798 | 1244649.7792
146 | 2661118.0839 | 1244714.66
147 | 2661111.0638 | 1244672.0657
148 | 2661117.0832 | 1244662.8844
149 | 2661297.109 | 1244776.7515
150 | 2661297.8812 | 1244775.8856
151 | 2661281.571 | 1244794.1704
152 | 2661309.4399 | 1244762.9246
153 | 2661087.5926 | 1244668.3344
154 | 2661086.6184 | 1244670.4814
155 | 2661087.3659 | 1244665.4478
156 | 2661077.1843 | 1244681.6152
157 | 2661075.7132 | 1244690.4161
158 | 2661075.9093 | 1244694.8545
159 | 2661074.3343 | 1244695.9057
160 | 2661118.0268 | 1244651.7698
161 | 2661103.2902 | 1244674.8386
162 | 2661074.6365 | 1244698.8442
163 | 2661104.4023 | 1244689.1995
164 | 2661431.4452 | 1244839.8459
165 | 2661428.891 | 1244842.9879
166 | 2661429.3261 | 1244857.652
167 | 2661426.0616 | 1244862.4057
168 | 2661424.9095 | 1244864.0833
169 | 2661388.2157 | 1244873.0479
170 | 2661390.8619 | 1244869.2423
171 | 2661392.5022 | 1244866.8832
172 | 2661324.5686 | 1244702.8019

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1