## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4095-3_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4095-3_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_4095-3_0_5_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_4095-3_0_5_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_4095-3_0_5_node_37 | 0.4 | n |  | TRUE
5 | bus_LV_4095-3_0_5_node_81 | 0.4 | n |  | TRUE
6 | bus_LV_4095-3_0_5_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_4095-3_0_5_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_4095-3_0_5_node_62 | 0.4 | n |  | TRUE
9 | bus_LV_4095-3_0_5_node_63 | 0.4 | n |  | TRUE
10 | bus_LV_4095-3_0_5_node_64 | 0.4 | n |  | TRUE
11 | bus_LV_4095-3_0_5_node_61 | 0.4 | n |  | TRUE
12 | bus_LV_4095-3_0_5_node_43 | 0.4 | n |  | TRUE
13 | bus_LV_4095-3_0_5_node_45 | 0.4 | n |  | TRUE
14 | bus_LV_4095-3_0_5_node_42 | 0.4 | n |  | TRUE
15 | bus_LV_4095-3_0_5_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_4095-3_0_5_node_79 | 0.4 | n |  | TRUE
17 | bus_LV_4095-3_0_5_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_4095-3_0_5_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_4095-3_0_5_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_4095-3_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_4095-3_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_4095-3_0_5_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_4095-3_0_5_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_4095-3_0_5_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_4095-3_0_5_node_87 | 0.4 | n |  | TRUE
26 | bus_LV_4095-3_0_5_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_4095-3_0_5_node_90 | 0.4 | n |  | TRUE
28 | bus_LV_4095-3_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_4095-3_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_4095-3_0_5_node_85 | 0.4 | n |  | TRUE
31 | bus_LV_4095-3_0_5_node_89 | 0.4 | n |  | TRUE
32 | bus_LV_4095-3_0_5_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_4095-3_0_5_node_18 | 0.4 | n |  | TRUE
34 | bus_LV_4095-3_0_5_node_39 | 0.4 | n |  | TRUE
35 | bus_LV_4095-3_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_4095-3_0_5_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_4095-3_0_5_node_19 | 0.4 | n |  | TRUE
38 | bus_LV_4095-3_0_5_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_4095-3_0_5_node_100 | 0.4 | n |  | TRUE
40 | bus_LV_4095-3_0_5_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_4095-3_0_5_node_98 | 0.4 | n |  | TRUE
42 | bus_LV_4095-3_0_5_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_4095-3_0_5_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_4095-3_0_5_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_4095-3_0_5_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_4095-3_0_5_node_26 | 0.4 | n |  | TRUE
47 | bus_LV_4095-3_0_5_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_4095-3_0_5_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_4095-3_0_5_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_4095-3_0_5_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_4095-3_0_5_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_4095-3_0_5_node_76 | 0.4 | n |  | TRUE
53 | bus_LV_4095-3_0_5_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_4095-3_0_5_node_82 | 0.4 | n |  | TRUE
55 | bus_LV_4095-3_0_5_node_80 | 0.4 | n |  | TRUE
56 | bus_LV_4095-3_0_5_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_4095-3_0_5_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_4095-3_0_5_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_4095-3_0_5_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_4095-3_0_5_node_58 | 0.4 | n |  | TRUE
61 | bus_LV_4095-3_0_5_node_47 | 0.4 | n |  | TRUE
62 | bus_LV_4095-3_0_5_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_4095-3_0_5_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_4095-3_0_5_node_56 | 0.4 | n |  | TRUE
65 | bus_LV_4095-3_0_5_node_50 | 0.4 | n |  | TRUE
66 | bus_LV_4095-3_0_5_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_4095-3_0_5_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_4095-3_0_5_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_4095-3_0_5_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_4095-3_0_5_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_4095-3_0_5_node_52 | 0.4 | n |  | TRUE
72 | bus_LV_4095-3_0_5_node_53 | 0.4 | n |  | TRUE
73 | bus_LV_4095-3_0_5_node_104 | 0.4 | n |  | TRUE
74 | bus_LV_4095-3_0_5_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_4095-3_0_5_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_4095-3_0_5_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_4095-3_0_5_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_4095-3_0_5_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_4095-3_0_5_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_4095-3_0_5_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_4095-3_0_5_node_72 | 0.4 | n |  | TRUE
82 | bus_LV_4095-3_0_5_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_4095-3_0_5_node_74 | 0.4 | n |  | TRUE
84 | bus_LV_4095-3_0_5_node_77 | 0.4 | n |  | TRUE
85 | bus_LV_4095-3_0_5_node_78 | 0.4 | n |  | TRUE
86 | bus_LV_4095-3_0_5_node_92 | 0.4 | n |  | TRUE
87 | bus_LV_4095-3_0_5_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_4095-3_0_5_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_4095-3_0_5_node_86 | 0.4 | n |  | TRUE
90 | bus_LV_4095-3_0_5_node_88 | 0.4 | n |  | TRUE
91 | bus_LV_4095-3_0_5_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_4095-3_0_5_node_94 | 0.4 | n |  | TRUE
93 | bus_LV_4095-3_0_5_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_4095-3_0_5_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_4095-3_0_5_node_101 | 0.4 | n |  | TRUE
96 | bus_LV_4095-3_0_5_node_99 | 0.4 | n |  | TRUE
97 | bus_LV_4095-3_0_5_node_97 | 0.4 | n |  | TRUE
98 | bus_MV_430_1_node_182 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4095-3_0_5_load_0 | 0 | 0.050709 | 0.012709 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4095-3_0_5_load_5 | 2 | 0.012926 | 0.0032396 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4095-3_0_5_load_6 | 3 | 0.012425 | 0.0031141 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4095-3_0_5_load_37 | 4 | 0.0042235 | 0.0010585 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4095-3_0_5_load_41 | 6 | 0.0077794 | 0.0019497 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4095-3_0_5_load_36 | 7 | 0.0059941 | 0.0015023 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4095-3_0_5_load_64 | 10 | 0.056195 | 0.014084 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4095-3_0_5_load_61 | 11 | 0.0051236 | 0.0012841 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4095-3_0_5_load_45 | 13 | 0.0029813 | 0.00074718 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4095-3_0_5_load_42 | 14 | 0.0025608 | 0.00064179 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4095-3_0_5_load_7 | 17 | 0.020337 | 0.005097 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4095-3_0_5_load_10 | 20 | 0.02884 | 0.007228 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4095-3_0_5_load_11 | 21 | 0.0046874 | 0.0011748 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4095-3_0_5_load_12 | 22 | 0.0067859 | 0.0017007 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4095-3_0_5_load_13 | 23 | 0.0022602 | 0.00056645 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4095-3_0_5_load_87 | 25 | 0.0037156 | 0.00093122 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4095-3_0_5_load_34 | 26 | 0.0058641 | 0.0014697 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4095-3_0_5_load_90 | 27 | 0.0044607 | 0.001118 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4095-3_0_5_load_15 | 28 | 0.0027768 | 0.00069594 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4095-3_0_5_load_16 | 29 | 0.0022306 | 0.00055904 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4095-3_0_5_load_85 | 30 | 0.0025772 | 0.0006459 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4095-3_0_5_load_89 | 31 | 0.0046571 | 0.0011672 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4095-3_0_5_load_38 | 32 | 0.011596 | 0.0029063 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4095-3_0_5_load_39 | 34 | 0.0039828 | 0.00099818 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4095-3_0_5_load_17 | 36 | 0.014677 | 0.0036785 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4095-3_0_5_load_21 | 38 | 0.014671 | 0.0036768 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4095-3_0_5_load_100 | 39 | 0.0014664 | 0.00036753 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4095-3_0_5_load_98 | 41 | 0.0010138 | 0.00025409 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4095-3_0_5_load_24 | 42 | 0.01455 | 0.0036466 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4095-3_0_5_load_25 | 43 | 0.0054621 | 0.0013689 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4095-3_0_5_load_29 | 44 | 0.015381 | 0.0038549 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4095-3_0_5_load_27 | 45 | 0.0060861 | 0.0015253 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4095-3_0_5_load_28 | 47 | 0.0080649 | 0.0020212 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4095-3_0_5_load_30 | 48 | 0.011011 | 0.0027595 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4095-3_0_5_load_31 | 49 | 0.0034973 | 0.00087651 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4095-3_0_5_load_33 | 51 | 0.0041887 | 0.0010498 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4095-3_0_5_load_76 | 52 | 0.004192 | 0.0010506 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4095-3_0_5_load_75 | 53 | 0.0026561 | 0.00066568 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4095-3_0_5_load_82 | 54 | 0.0063164 | 0.001583 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4095-3_0_5_load_46 | 57 | 0.0018251 | 0.00045741 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4095-3_0_5_load_58 | 60 | 0.0030575 | 0.00076628 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4095-3_0_5_load_59 | 62 | 0.0047915 | 0.0012009 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4095-3_0_5_load_57 | 63 | 0.0074219 | 0.0018601 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4095-3_0_5_load_56 | 64 | 0.0024734 | 0.0006199 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4095-3_0_5_load_51 | 66 | 0.0027863 | 0.0006983 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4095-3_0_5_load_60 | 67 | 0.01369 | 0.003431 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4095-3_0_5_load_103 | 70 | 0.0030361 | 0.00076092 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4095-3_0_5_load_52 | 71 | 0.0049276 | 0.001235 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4095-3_0_5_load_53 | 72 | 0.0031127 | 0.00078011 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4095-3_0_5_load_104 | 73 | 0.0016371 | 0.00041029 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4095-3_0_5_load_68 | 74 | 0.0056185 | 0.0014081 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4095-3_0_5_load_65 | 75 | 0.0035333 | 0.00088552 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4095-3_0_5_load_71 | 76 | 0.0047781 | 0.0011975 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4095-3_0_5_load_66 | 77 | 0.0028848 | 0.000723 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4095-3_0_5_load_67 | 78 | 0.0027257 | 0.00068312 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4095-3_0_5_load_70 | 80 | 0.0041559 | 0.0010416 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4095-3_0_5_load_72 | 81 | 0.010451 | 0.0026192 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4095-3_0_5_load_73 | 82 | 0.0021464 | 0.00053793 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4095-3_0_5_load_74 | 83 | 0.0048394 | 0.0012129 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4095-3_0_5_load_77 | 84 | 0.002745 | 0.00068797 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4095-3_0_5_load_78 | 85 | 0.0040704 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4095-3_0_5_load_92 | 86 | 0.002093 | 0.00052456 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4095-3_0_5_load_91 | 87 | 0.00079747 | 0.00019986 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4095-3_0_5_load_84 | 88 | 0.0045146 | 0.0011315 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4095-3_0_5_load_86 | 89 | 0.0033495 | 0.00083945 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4095-3_0_5_load_88 | 90 | 0.0037954 | 0.00095121 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4095-3_0_5_load_93 | 91 | 0.00071901 | 0.0001802 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4095-3_0_5_load_94 | 92 | 0.00057673 | 0.00014454 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4095-3_0_5_load_95 | 93 | 0.00055709 | 0.00013962 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4095-3_0_5_load_96 | 94 | 0.00072172 | 0.00018088 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4095-3_0_5_load_101 | 95 | 0.00072565 | 0.00018187 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4095-3_0_5_load_99 | 96 | 0.00099241 | 0.00024872 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4095-3_0_5_load_97 | 97 | 0.00067409 | 0.00016894 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4095-3_0_5_line_0 |  | 0 | 1 | 0.041498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4095-3_0_5_line_1 |  | 1 | 2 | 0.012108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4095-3_0_5_line_2 |  | 1 | 3 | 0.0086861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4095-3_0_5_line_3 |  | 2 | 4 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4095-3_0_5_line_4 |  | 3 | 5 | 0.014841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4095-3_0_5_line_5 |  | 4 | 15 | 0.037018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4095-3_0_5_line_6 |  | 5 | 16 | 0.008182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4095-3_0_5_line_7 |  | 6 | 7 | 0.014343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4095-3_0_5_line_8 |  | 7 | 15 | 0.029336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4095-3_0_5_line_9 |  | 8 | 9 | 0.025554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4095-3_0_5_line_10 |  | 8 | 10 | 0.05325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4095-3_0_5_line_11 |  | 8 | 11 | 0.017196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4095-3_0_5_line_12 |  | 9 | 74 | 0.012784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4095-3_0_5_line_13 |  | 9 | 75 | 0.016261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4095-3_0_5_line_14 |  | 11 | 61 | 0.027586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4095-3_0_5_line_15 |  | 12 | 13 | 0.02702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4095-3_0_5_line_16 |  | 12 | 14 | 0.049717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4095-3_0_5_line_17 |  | 13 | 59 | 0.027851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4095-3_0_5_line_18 |  | 15 | 26 | 0.01536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4095-3_0_5_line_19 |  | 15 | 51 | 0.019466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_4095-3_0_5_line_20 |  | 16 | 84 | 0.016213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4095-3_0_5_line_21 |  | 17 | 18 | 0.029329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4095-3_0_5_line_22 |  | 17 | 19 | 0.011716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4095-3_0_5_line_23 |  | 18 | 20 | 0.026445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4095-3_0_5_line_24 |  | 18 | 21 | 0.01479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4095-3_0_5_line_25 |  | 19 | 22 | 0.03316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4095-3_0_5_line_26 |  | 19 | 23 | 0.013157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4095-3_0_5_line_27 |  | 20 | 24 | 0.0028657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4095-3_0_5_line_28 |  | 21 | 25 | 0.0018529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4095-3_0_5_line_29 |  | 22 | 26 | 0.0030659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4095-3_0_5_line_30 |  | 23 | 27 | 0.0029172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4095-3_0_5_line_31 |  | 24 | 28 | 0.03786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4095-3_0_5_line_32 |  | 24 | 29 | 0.021795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4095-3_0_5_line_33 |  | 25 | 30 | 0.025145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4095-3_0_5_line_34 |  | 27 | 31 | 0.018176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4095-3_0_5_line_35 |  | 28 | 32 | 0.010978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4095-3_0_5_line_36 |  | 29 | 33 | 0.0069312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4095-3_0_5_line_37 |  | 30 | 88 | 0.012698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4095-3_0_5_line_38 |  | 31 | 90 | 0.0038317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4095-3_0_5_line_39 |  | 32 | 34 | 0.031502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4095-3_0_5_line_40 |  | 33 | 35 | 0.019759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4095-3_0_5_line_41 |  | 35 | 39 | 0.015052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4095-3_0_5_line_42 |  | 36 | 37 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4095-3_0_5_line_43 |  | 37 | 38 | 0.028643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4095-3_0_5_line_44 |  | 38 | 40 | 0.015098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4095-3_0_5_line_45 |  | 39 | 41 | 0.016496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4095-3_0_5_line_46 |  | 40 | 42 | 0.011367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4095-3_0_5_line_47 |  | 40 | 43 | 0.015443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4095-3_0_5_line_48 |  | 41 | 97 | 0.0050867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4095-3_0_5_line_49 |  | 42 | 46 | 0.045485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4095-3_0_5_line_50 |  | 44 | 45 | 0.018965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4095-3_0_5_line_51 |  | 45 | 46 | 0.020927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4095-3_0_5_line_52 |  | 46 | 47 | 0.040278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4095-3_0_5_line_53 |  | 47 | 48 | 0.00077509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4095-3_0_5_line_54 |  | 48 | 49 | 0.019457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4095-3_0_5_line_55 |  | 49 | 50 | 0.029227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_4095-3_0_5_line_56 |  | 49 | 51 | 0.024124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_4095-3_0_5_line_57 |  | 50 | 52 | 0.01191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_4095-3_0_5_line_58 |  | 52 | 53 | 0.020656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_4095-3_0_5_line_59 |  | 53 | 83 | 0.0064703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_4095-3_0_5_line_60 |  | 54 | 55 | 0.025496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4095-3_0_5_line_61 |  | 55 | 85 | 0.009083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4095-3_0_5_line_62 |  | 56 | 57 | 0.010659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4095-3_0_5_line_63 |  | 56 | 58 | 0.030725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4095-3_0_5_line_64 |  | 57 | 60 | 0.00026508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4095-3_0_5_line_65 |  | 58 | 63 | 0.042354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4095-3_0_5_line_66 |  | 58 | 64 | 0.019235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4095-3_0_5_line_67 |  | 58 | 61 | 0.024261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4095-3_0_5_line_68 |  | 59 | 65 | 0.018868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4095-3_0_5_line_69 |  | 59 | 66 | 0.010624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4095-3_0_5_line_70 |  | 61 | 62 | 0.015144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4095-3_0_5_line_71 |  | 62 | 67 | 0.007454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4095-3_0_5_line_72 |  | 64 | 68 | 0.015986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4095-3_0_5_line_73 |  | 65 | 69 | 0.013886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4095-3_0_5_line_74 |  | 65 | 70 | 0.0109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4095-3_0_5_line_75 |  | 66 | 71 | 0.004835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4095-3_0_5_line_76 |  | 68 | 72 | 0.019232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4095-3_0_5_line_77 |  | 69 | 72 | 0.0058096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4095-3_0_5_line_78 |  | 70 | 73 | 0.0082256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4095-3_0_5_line_79 |  | 74 | 76 | 0.00034057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4095-3_0_5_line_80 |  | 75 | 77 | 0.0075459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4095-3_0_5_line_81 |  | 76 | 81 | 0.0064988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4095-3_0_5_line_82 |  | 77 | 78 | 0.012148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_4095-3_0_5_line_83 |  | 78 | 79 | 0.0067382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_4095-3_0_5_line_84 |  | 79 | 80 | 0.011801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_4095-3_0_5_line_85 |  | 80 | 82 | 0.024608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_4095-3_0_5_line_86 |  | 82 | 83 | 0.0030916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_4095-3_0_5_line_87 |  | 84 | 85 | 0.017718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4095-3_0_5_line_88 |  | 86 | 87 | 0.0014023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4095-3_0_5_line_89 |  | 87 | 91 | 0.012854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4095-3_0_5_line_90 |  | 88 | 89 | 0.0069154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4095-3_0_5_line_91 |  | 91 | 92 | 0.0013758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4095-3_0_5_line_92 |  | 92 | 93 | 0.0058854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4095-3_0_5_line_93 |  | 93 | 94 | 0.00027684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4095-3_0_5_line_94 |  | 94 | 95 | 0.01363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4095-3_0_5_line_95 |  | 95 | 96 | 0.0023463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4095-3_0_5_line_96 |  | 96 | 97 | 0.0052569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4095-3_0_5_trafo_35 | 0.63 MVA 20/0.4 kV | 98 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2657719.632 | 1259080.1209 | 2657736.1735 | 1259057.388 | 2657735.9222 | 1259053.783 | 2657733.7268 | 1259050.1145 | 2657736.7041 | 1259045.4957
1 | 2657719.632 | 1259080.1209 | 2657729.8688 | 1259086.5868
2 | 2657719.632 | 1259080.1209 | 2657712.2466 | 1259075.5487
3 | 2657729.8688 | 1259086.5868 | 2657743.6702 | 1259095.3042
4 | 2657699.8712 | 1259067.3635 | 2657707.8984 | 1259072.8568 | 2657712.2466 | 1259075.5487
5 | 2657774.7824 | 1259115.3508 | 2657769.3922 | 1259111.551 | 2657743.6702 | 1259095.3042
6 | 2657693.1555 | 1259062.6614 | 2657699.8712 | 1259067.3635
7 | 2657791.9322 | 1259091.5621 | 2657800.5383 | 1259080.0885
8 | 2657774.7824 | 1259115.3508 | 2657780.4279 | 1259106.8998 | 2657791.9322 | 1259091.5621
9 | 2657825.9194 | 1259046.7339 | 2657840.2911 | 1259055.5473 | 2657847.9076 | 1259059.8581
10 | 2657825.9194 | 1259046.7339 | 2657782.2391 | 1259016.2782
11 | 2657825.9194 | 1259046.7339 | 2657835.9696 | 1259032.7808
12 | 2657847.9076 | 1259059.8581 | 2657841.3037 | 1259070.804
13 | 2657847.9076 | 1259059.8581 | 2657862.304 | 1259067.4189
14 | 2657852.0924 | 1259010.3968 | 2657835.9696 | 1259032.7808
15 | 2657798.1369 | 1258899.8459 | 2657821.1129 | 1258914.0656
16 | 2657798.1369 | 1258899.8459 | 2657793.2001 | 1258916.7543 | 2657795.0196 | 1258941.9346 | 2657799.9328 | 1258946.717
17 | 2657844.795 | 1258928.7223 | 2657821.1129 | 1258914.0656
18 | 2657774.7824 | 1259115.3508 | 2657769.041 | 1259122.044 | 2657765.1891 | 1259127.3315
19 | 2657774.7824 | 1259115.3508 | 2657781.8324 | 1259118.2327 | 2657792.6204 | 1259123.1362
20 | 2657693.1555 | 1259062.6614 | 2657689.1616 | 1259067.9485 | 2657683.4169 | 1259075.6233
21 | 2657720.1644 | 1259190.1274 | 2657737.0954 | 1259166.1787
22 | 2657743.8587 | 1259156.6121 | 2657737.0954 | 1259166.1787
23 | 2657720.1644 | 1259190.1274 | 2657704.6806 | 1259211.5653
24 | 2657720.1644 | 1259190.1274 | 2657708.0377 | 1259181.6607
25 | 2657743.8587 | 1259156.6121 | 2657763.3839 | 1259129.8096
26 | 2657743.8587 | 1259156.6121 | 2657733.013 | 1259149.1638
27 | 2657703.0027 | 1259213.8883 | 2657704.6806 | 1259211.5653
28 | 2657706.5184 | 1259180.5999 | 2657708.0377 | 1259181.6607
29 | 2657763.3839 | 1259129.8096 | 2657765.1891 | 1259127.3315
30 | 2657733.013 | 1259149.1638 | 2657730.6083 | 1259147.5123
31 | 2657703.0027 | 1259213.8883 | 2657672.1462 | 1259191.9508
32 | 2657703.0027 | 1259213.8883 | 2657701.7735 | 1259215.4886 | 2657690.1251 | 1259231.4716
33 | 2657706.5184 | 1259180.5999 | 2657685.9017 | 1259166.2055
34 | 2657730.6083 | 1259147.5123 | 2657715.6249 | 1259137.2224
35 | 2657663.1989 | 1259185.5897 | 2657672.1462 | 1259191.9508
36 | 2657686.0427 | 1259237.0731 | 2657690.1251 | 1259231.4716
37 | 2657675.4902 | 1259158.9363 | 2657675.4902 | 1259158.9363 | 2657685.9017 | 1259166.2055
38 | 2657712.4664 | 1259135.0533 | 2657715.6249 | 1259137.2224
39 | 2657663.1989 | 1259185.5897 | 2657637.5243 | 1259167.3362
40 | 2657674.3994 | 1259253.0601 | 2657686.0427 | 1259237.0731
41 | 2657674.3994 | 1259253.0601 | 2657662.0357 | 1259244.4755
42 | 2657745.719 | 1259273.3921 | 2657733.5023 | 1259265.9424
43 | 2657745.719 | 1259273.3921 | 2657762.9325 | 1259250.4991
44 | 2657764.2176 | 1259235.4563 | 2657762.9325 | 1259250.4991
45 | 2657662.0357 | 1259244.4755 | 2657648.486 | 1259235.0674
46 | 2657764.2176 | 1259235.4563 | 2657769.4844 | 1259225.3833
47 | 2657764.2176 | 1259235.4563 | 2657751.0401 | 1259227.4045
48 | 2657644.3077 | 1259232.1662 | 2657648.486 | 1259235.0674
49 | 2657789.5466 | 1259185.0783 | 2657776.6537 | 1259203.9328 | 2657770.4009 | 1259223.6304 | 2657769.4844 | 1259225.3833
50 | 2657805.03 | 1259199.1571 | 2657810.8327 | 1259204.4334 | 2657805.8401 | 1259214.3722
51 | 2657789.5466 | 1259185.0783 | 2657805.03 | 1259199.1571
52 | 2657789.5466 | 1259185.0783 | 2657786.7373 | 1259182.5269 | 2657794.6094 | 1259168.3713 | 2657804.6091 | 1259150.7217
53 | 2657804.9911 | 1259150.0473 | 2657804.6091 | 1259150.7217
54 | 2657814.5824 | 1259133.1187 | 2657804.9911 | 1259150.0473
55 | 2657814.5824 | 1259133.1187 | 2657841.531 | 1259144.6235
56 | 2657814.5824 | 1259133.1187 | 2657792.6204 | 1259123.1362
57 | 2657841.531 | 1259144.6235 | 2657848.0144 | 1259134.6332
58 | 2657848.0144 | 1259134.6332 | 2657859.259 | 1259117.3063
59 | 2657862.8522 | 1259111.9269 | 2657861.6513 | 1259113.62 | 2657859.259 | 1259117.3063
60 | 2657667.3567 | 1259097.0792 | 2657652.078 | 1259117.4905
61 | 2657667.3567 | 1259097.0792 | 2657672.7996 | 1259089.8077
62 | 2657844.2915 | 1258985.6139 | 2657850.3949 | 1258976.8748
63 | 2657844.2915 | 1258985.6139 | 2657860.4984 | 1258998.7261 | 2657864.8308 | 1258993.5313 | 2657866.5672 | 1258990.9465
64 | 2657850.5467 | 1258976.6574 | 2657850.3949 | 1258976.8748
65 | 2657866.5672 | 1258990.9465 | 2657882.6814 | 1259003.5019 | 2657887.8187 | 1259006.9546 | 2657892.1463 | 1259001.493 | 2657896.578 | 1258993.853
66 | 2657866.5672 | 1258990.9465 | 2657878.2599 | 1258975.6734
67 | 2657852.0924 | 1259010.3968 | 2657860.4984 | 1258998.7261 | 2657864.8308 | 1258993.5313 | 2657866.5672 | 1258990.9465
68 | 2657844.795 | 1258928.7223 | 2657859.0088 | 1258937.5231 | 2657860.9359 | 1258938.5649
69 | 2657844.795 | 1258928.7223 | 2657839.2664 | 1258937.7946
70 | 2657852.0924 | 1259010.3968 | 2657864.49 | 1259019.0947
71 | 2657870.592 | 1259023.3758 | 2657864.49 | 1259019.0947
72 | 2657887.9776 | 1258962.9801 | 2657878.2599 | 1258975.6734
73 | 2657860.9359 | 1258938.5649 | 2657870.5186 | 1258943.7845 | 2657873.452 | 1258944.447
74 | 2657860.9359 | 1258938.5649 | 2657855.0124 | 1258947.7144
75 | 2657839.2664 | 1258937.7946 | 2657836.7504 | 1258941.9234
76 | 2657887.9776 | 1258962.9801 | 2657884.8059 | 1258960.4806 | 2657885.078 | 1258958.8599 | 2657884.5192 | 1258955.1073 | 2657882.5398 | 1258951.7077 | 2657877.9909 | 1258948.0733
77 | 2657873.452 | 1258944.447 | 2657877.9909 | 1258948.0733
78 | 2657850.5421 | 1258954.6193 | 2657855.0124 | 1258947.7144
79 | 2657841.1278 | 1259071.0956 | 2657841.3037 | 1259070.804
80 | 2657862.304 | 1259067.4189 | 2657868.9847 | 1259070.9274
81 | 2657837.7706 | 1259076.6601 | 2657841.1278 | 1259071.0956
82 | 2657879.7393 | 1259076.5755 | 2657868.9847 | 1259070.9274
83 | 2657885.7049 | 1259079.7085 | 2657879.7393 | 1259076.5755
84 | 2657885.7049 | 1259079.7085 | 2657878.8775 | 1259089.3339
85 | 2657878.8775 | 1259089.3339 | 2657864.6408 | 1259109.4052
86 | 2657862.8522 | 1259111.9269 | 2657864.6408 | 1259109.4052
87 | 2657683.4169 | 1259075.6233 | 2657672.7996 | 1259089.8077
88 | 2657610.1165 | 1259208.4259 | 2657608.9646 | 1259207.6261
89 | 2657610.1165 | 1259208.4259 | 2657620.6745 | 1259215.7567
90 | 2657675.4902 | 1259158.9363 | 2657678.8942 | 1259152.9167
91 | 2657621.8046 | 1259216.5414 | 2657620.6745 | 1259215.7567
92 | 2657621.8046 | 1259216.5414 | 2657626.6389 | 1259219.8981
93 | 2657626.6389 | 1259219.8981 | 2657626.8663 | 1259220.056
94 | 2657626.8663 | 1259220.056 | 2657638.0623 | 1259227.8298
95 | 2657638.0623 | 1259227.8298 | 2657639.9896 | 1259229.168
96 | 2657644.3077 | 1259232.1662 | 2657639.9896 | 1259229.168

## bus_geodata
| x | y | coords
0 | 2657736.7041 | 1259045.4957
1 | 2657719.632 | 1259080.1209
2 | 2657729.8688 | 1259086.5868
3 | 2657712.2466 | 1259075.5487
4 | 2657743.6702 | 1259095.3042
5 | 2657699.8712 | 1259067.3635
6 | 2657800.5383 | 1259080.0885
7 | 2657791.9322 | 1259091.5621
8 | 2657825.9194 | 1259046.7339
9 | 2657847.9076 | 1259059.8581
10 | 2657782.2391 | 1259016.2782
11 | 2657835.9696 | 1259032.7808
12 | 2657798.1369 | 1258899.8459
13 | 2657821.1129 | 1258914.0656
14 | 2657799.9328 | 1258946.717
15 | 2657774.7824 | 1259115.3508
16 | 2657693.1555 | 1259062.6614
17 | 2657737.0954 | 1259166.1787
18 | 2657720.1644 | 1259190.1274
19 | 2657743.8587 | 1259156.6121
20 | 2657704.6806 | 1259211.5653
21 | 2657708.0377 | 1259181.6607
22 | 2657763.3839 | 1259129.8096
23 | 2657733.013 | 1259149.1638
24 | 2657703.0027 | 1259213.8883
25 | 2657706.5184 | 1259180.5999
26 | 2657765.1891 | 1259127.3315
27 | 2657730.6083 | 1259147.5123
28 | 2657672.1462 | 1259191.9508
29 | 2657690.1251 | 1259231.4716
30 | 2657685.9017 | 1259166.2055
31 | 2657715.6249 | 1259137.2224
32 | 2657663.1989 | 1259185.5897
33 | 2657686.0427 | 1259237.0731
34 | 2657637.5243 | 1259167.3362
35 | 2657674.3994 | 1259253.0601
36 | 2657733.5023 | 1259265.9424
37 | 2657745.719 | 1259273.3921
38 | 2657762.9325 | 1259250.4991
39 | 2657662.0357 | 1259244.4755
40 | 2657764.2176 | 1259235.4563
41 | 2657648.486 | 1259235.0674
42 | 2657769.4844 | 1259225.3833
43 | 2657751.0401 | 1259227.4045
44 | 2657805.8401 | 1259214.3722
45 | 2657805.03 | 1259199.1571
46 | 2657789.5466 | 1259185.0783
47 | 2657804.6091 | 1259150.7217
48 | 2657804.9911 | 1259150.0473
49 | 2657814.5824 | 1259133.1187
50 | 2657841.531 | 1259144.6235
51 | 2657792.6204 | 1259123.1362
52 | 2657848.0144 | 1259134.6332
53 | 2657859.259 | 1259117.3063
54 | 2657652.078 | 1259117.4905
55 | 2657667.3567 | 1259097.0792
56 | 2657844.2915 | 1258985.6139
57 | 2657850.3949 | 1258976.8748
58 | 2657866.5672 | 1258990.9465
59 | 2657844.795 | 1258928.7223
60 | 2657850.5467 | 1258976.6574
61 | 2657852.0924 | 1259010.3968
62 | 2657864.49 | 1259019.0947
63 | 2657896.578 | 1258993.853
64 | 2657878.2599 | 1258975.6734
65 | 2657860.9359 | 1258938.5649
66 | 2657839.2664 | 1258937.7946
67 | 2657870.592 | 1259023.3758
68 | 2657887.9776 | 1258962.9801
69 | 2657873.452 | 1258944.447
70 | 2657855.0124 | 1258947.7144
71 | 2657836.7504 | 1258941.9234
72 | 2657877.9909 | 1258948.0733
73 | 2657850.5421 | 1258954.6193
74 | 2657841.3037 | 1259070.804
75 | 2657862.3041 | 1259067.4189
76 | 2657841.1278 | 1259071.0956
77 | 2657868.9847 | 1259070.9274
78 | 2657879.7393 | 1259076.5755
79 | 2657885.7049 | 1259079.7085
80 | 2657878.8775 | 1259089.3339
81 | 2657837.7706 | 1259076.6601
82 | 2657864.6408 | 1259109.4052
83 | 2657862.8522 | 1259111.9269
84 | 2657683.4169 | 1259075.6233
85 | 2657672.7996 | 1259089.8077
86 | 2657608.9646 | 1259207.6261
87 | 2657610.1165 | 1259208.4259
88 | 2657675.4902 | 1259158.9363
89 | 2657678.8942 | 1259152.9167
90 | 2657712.4664 | 1259135.0533
91 | 2657620.6745 | 1259215.7567
92 | 2657621.8046 | 1259216.5414
93 | 2657626.6389 | 1259219.8981
94 | 2657626.8663 | 1259220.056
95 | 2657638.0623 | 1259227.8298
96 | 2657639.9896 | 1259229.168
97 | 2657644.3077 | 1259232.1662
98 | 2657814.5824 | 1259133.1187

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1