## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4123-13_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4123-13_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4123-13_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4123-13_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4123-13_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4123-13_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4123-13_0_5_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_4123-13_0_5_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_4123-13_0_5_node_64 | 0.4 | n |  | TRUE
9 | bus_LV_4123-13_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_4123-13_0_5_node_99 | 0.4 | n |  | TRUE
11 | bus_LV_4123-13_0_5_node_77 | 0.4 | n |  | TRUE
12 | bus_LV_4123-13_0_5_node_79 | 0.4 | n |  | TRUE
13 | bus_LV_4123-13_0_5_node_149 | 0.4 | n |  | TRUE
14 | bus_LV_4123-13_0_5_node_65 | 0.4 | n |  | TRUE
15 | bus_LV_4123-13_0_5_node_97 | 0.4 | n |  | TRUE
16 | bus_LV_4123-13_0_5_node_75 | 0.4 | n |  | TRUE
17 | bus_LV_4123-13_0_5_node_80 | 0.4 | n |  | TRUE
18 | bus_LV_4123-13_0_5_node_150 | 0.4 | n |  | TRUE
19 | bus_LV_4123-13_0_5_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_4123-13_0_5_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_4123-13_0_5_node_85 | 0.4 | n |  | TRUE
22 | bus_LV_4123-13_0_5_node_167 | 0.4 | n |  | TRUE
23 | bus_LV_4123-13_0_5_node_47 | 0.4 | n |  | TRUE
24 | bus_LV_4123-13_0_5_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_4123-13_0_5_node_93 | 0.4 | n |  | TRUE
26 | bus_LV_4123-13_0_5_node_92 | 0.4 | n |  | TRUE
27 | bus_LV_4123-13_0_5_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_4123-13_0_5_node_15 | 0.4 | n |  | TRUE
29 | bus_LV_4123-13_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_4123-13_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_4123-13_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_4123-13_0_5_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_4123-13_0_5_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_4123-13_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_4123-13_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_4123-13_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_4123-13_0_5_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_4123-13_0_5_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_4123-13_0_5_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_4123-13_0_5_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_4123-13_0_5_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_4123-13_0_5_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_4123-13_0_5_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_4123-13_0_5_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_4123-13_0_5_node_26 | 0.4 | n |  | TRUE
46 | bus_LV_4123-13_0_5_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_4123-13_0_5_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_4123-13_0_5_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_4123-13_0_5_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_4123-13_0_5_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_4123-13_0_5_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_4123-13_0_5_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_4123-13_0_5_node_60 | 0.4 | n |  | TRUE
54 | bus_LV_4123-13_0_5_node_129 | 0.4 | n |  | TRUE
55 | bus_LV_4123-13_0_5_node_61 | 0.4 | n |  | TRUE
56 | bus_LV_4123-13_0_5_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_4123-13_0_5_node_128 | 0.4 | n |  | TRUE
58 | bus_LV_4123-13_0_5_node_40 | 0.4 | n |  | TRUE
59 | bus_LV_4123-13_0_5_node_56 | 0.4 | n |  | TRUE
60 | bus_LV_4123-13_0_5_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_4123-13_0_5_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_4123-13_0_5_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_4123-13_0_5_node_42 | 0.4 | n |  | TRUE
64 | bus_LV_4123-13_0_5_node_43 | 0.4 | n |  | TRUE
65 | bus_LV_4123-13_0_5_node_44 | 0.4 | n |  | TRUE
66 | bus_LV_4123-13_0_5_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_4123-13_0_5_node_46 | 0.4 | n |  | TRUE
68 | bus_LV_4123-13_0_5_node_48 | 0.4 | n |  | TRUE
69 | bus_LV_4123-13_0_5_node_83 | 0.4 | n |  | TRUE
70 | bus_LV_4123-13_0_5_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_4123-13_0_5_node_58 | 0.4 | n |  | TRUE
72 | bus_LV_4123-13_0_5_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_4123-13_0_5_node_69 | 0.4 | n |  | TRUE
74 | bus_LV_4123-13_0_5_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_4123-13_0_5_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_4123-13_0_5_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_4123-13_0_5_node_53 | 0.4 | n |  | TRUE
78 | bus_LV_4123-13_0_5_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_4123-13_0_5_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_4123-13_0_5_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_4123-13_0_5_node_68 | 0.4 | n |  | TRUE
82 | bus_LV_4123-13_0_5_node_70 | 0.4 | n |  | TRUE
83 | bus_LV_4123-13_0_5_node_62 | 0.4 | n |  | TRUE
84 | bus_LV_4123-13_0_5_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_4123-13_0_5_node_94 | 0.4 | n |  | TRUE
86 | bus_LV_4123-13_0_5_node_88 | 0.4 | n |  | TRUE
87 | bus_LV_4123-13_0_5_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_4123-13_0_5_node_95 | 0.4 | n |  | TRUE
89 | bus_LV_4123-13_0_5_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_4123-13_0_5_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_4123-13_0_5_node_96 | 0.4 | n |  | TRUE
92 | bus_LV_4123-13_0_5_node_91 | 0.4 | n |  | TRUE
93 | bus_LV_4123-13_0_5_node_73 | 0.4 | n |  | TRUE
94 | bus_LV_4123-13_0_5_node_74 | 0.4 | n |  | TRUE
95 | bus_LV_4123-13_0_5_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_4123-13_0_5_node_78 | 0.4 | n |  | TRUE
97 | bus_LV_4123-13_0_5_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_4123-13_0_5_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_4123-13_0_5_node_86 | 0.4 | n |  | TRUE
100 | bus_LV_4123-13_0_5_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_4123-13_0_5_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_4123-13_0_5_node_148 | 0.4 | n |  | TRUE
103 | bus_LV_4123-13_0_5_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_4123-13_0_5_node_101 | 0.4 | n |  | TRUE
105 | bus_LV_4123-13_0_5_node_102 | 0.4 | n |  | TRUE
106 | bus_LV_4123-13_0_5_node_103 | 0.4 | n |  | TRUE
107 | bus_LV_4123-13_0_5_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_4123-13_0_5_node_105 | 0.4 | n |  | TRUE
109 | bus_LV_4123-13_0_5_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_4123-13_0_5_node_172 | 0.4 | n |  | TRUE
111 | bus_LV_4123-13_0_5_node_115 | 0.4 | n |  | TRUE
112 | bus_LV_4123-13_0_5_node_173 | 0.4 | n |  | TRUE
113 | bus_LV_4123-13_0_5_node_116 | 0.4 | n |  | TRUE
114 | bus_LV_4123-13_0_5_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_4123-13_0_5_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_4123-13_0_5_node_109 | 0.4 | n |  | TRUE
117 | bus_LV_4123-13_0_5_node_110 | 0.4 | n |  | TRUE
118 | bus_LV_4123-13_0_5_node_111 | 0.4 | n |  | TRUE
119 | bus_LV_4123-13_0_5_node_112 | 0.4 | n |  | TRUE
120 | bus_LV_4123-13_0_5_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_4123-13_0_5_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_4123-13_0_5_node_151 | 0.4 | n |  | TRUE
123 | bus_LV_4123-13_0_5_node_170 | 0.4 | n |  | TRUE
124 | bus_LV_4123-13_0_5_node_154 | 0.4 | n |  | TRUE
125 | bus_LV_4123-13_0_5_node_171 | 0.4 | n |  | TRUE
126 | bus_LV_4123-13_0_5_node_117 | 0.4 | n |  | TRUE
127 | bus_LV_4123-13_0_5_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_4123-13_0_5_node_134 | 0.4 | n |  | TRUE
129 | bus_LV_4123-13_0_5_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_4123-13_0_5_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_4123-13_0_5_node_141 | 0.4 | n |  | TRUE
132 | bus_LV_4123-13_0_5_node_137 | 0.4 | n |  | TRUE
133 | bus_LV_4123-13_0_5_node_144 | 0.4 | n |  | TRUE
134 | bus_LV_4123-13_0_5_node_130 | 0.4 | n |  | TRUE
135 | bus_LV_4123-13_0_5_node_163 | 0.4 | n |  | TRUE
136 | bus_LV_4123-13_0_5_node_136 | 0.4 | n |  | TRUE
137 | bus_LV_4123-13_0_5_node_120 | 0.4 | n |  | TRUE
138 | bus_LV_4123-13_0_5_node_121 | 0.4 | n |  | TRUE
139 | bus_LV_4123-13_0_5_node_122 | 0.4 | n |  | TRUE
140 | bus_LV_4123-13_0_5_node_123 | 0.4 | n |  | TRUE
141 | bus_LV_4123-13_0_5_node_124 | 0.4 | n |  | TRUE
142 | bus_LV_4123-13_0_5_node_125 | 0.4 | n |  | TRUE
143 | bus_LV_4123-13_0_5_node_126 | 0.4 | n |  | TRUE
144 | bus_LV_4123-13_0_5_node_127 | 0.4 | n |  | TRUE
145 | bus_LV_4123-13_0_5_node_147 | 0.4 | n |  | TRUE
146 | bus_LV_4123-13_0_5_node_142 | 0.4 | n |  | TRUE
147 | bus_LV_4123-13_0_5_node_132 | 0.4 | n |  | TRUE
148 | bus_LV_4123-13_0_5_node_133 | 0.4 | n |  | TRUE
149 | bus_LV_4123-13_0_5_node_135 | 0.4 | n |  | TRUE
150 | bus_LV_4123-13_0_5_node_174 | 0.4 | n |  | TRUE
151 | bus_LV_4123-13_0_5_node_145 | 0.4 | n |  | TRUE
152 | bus_LV_4123-13_0_5_node_138 | 0.4 | n |  | TRUE
153 | bus_LV_4123-13_0_5_node_139 | 0.4 | n |  | TRUE
154 | bus_LV_4123-13_0_5_node_140 | 0.4 | n |  | TRUE
155 | bus_LV_4123-13_0_5_node_143 | 0.4 | n |  | TRUE
156 | bus_LV_4123-13_0_5_node_159 | 0.4 | n |  | TRUE
157 | bus_LV_4123-13_0_5_node_162 | 0.4 | n |  | TRUE
158 | bus_LV_4123-13_0_5_node_160 | 0.4 | n |  | TRUE
159 | bus_LV_4123-13_0_5_node_146 | 0.4 | n |  | TRUE
160 | bus_LV_4123-13_0_5_node_152 | 0.4 | n |  | TRUE
161 | bus_LV_4123-13_0_5_node_165 | 0.4 | n |  | TRUE
162 | bus_LV_4123-13_0_5_node_153 | 0.4 | n |  | TRUE
163 | bus_LV_4123-13_0_5_node_155 | 0.4 | n |  | TRUE
164 | bus_LV_4123-13_0_5_node_156 | 0.4 | n |  | TRUE
165 | bus_LV_4123-13_0_5_node_157 | 0.4 | n |  | TRUE
166 | bus_LV_4123-13_0_5_node_158 | 0.4 | n |  | TRUE
167 | bus_LV_4123-13_0_5_node_164 | 0.4 | n |  | TRUE
168 | bus_LV_4123-13_0_5_node_168 | 0.4 | n |  | TRUE
169 | bus_LV_4123-13_0_5_node_161 | 0.4 | n |  | TRUE
170 | bus_LV_4123-13_0_5_node_169 | 0.4 | n |  | TRUE
171 | bus_MV_421_0_node_117 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4123-13_0_5_load_0 | 0 | 0.0082723 | 0.0020732 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4123-13_0_5_load_1 | 1 | 0.0024357 | 0.00061044 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4123-13_0_5_load_2 | 2 | 0.0042012 | 0.0010529 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4123-13_0_5_load_4 | 4 | 0.0026175 | 0.000656 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4123-13_0_5_load_8 | 7 | 0.0021481 | 0.00053836 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4123-13_0_5_load_64 | 8 | 0.0075225 | 0.0018853 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4123-13_0_5_load_99 | 10 | 0.0053704 | 0.001346 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4123-13_0_5_load_77 | 11 | 0.0032585 | 0.00081665 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4123-13_0_5_load_79 | 12 | 0.0057695 | 0.001446 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4123-13_0_5_load_149 | 13 | 0.0026019 | 0.0006521 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4123-13_0_5_load_65 | 14 | 0.0063229 | 0.0015847 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4123-13_0_5_load_75 | 16 | 0.001122 | 0.0002812 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4123-13_0_5_load_80 | 17 | 0.0028318 | 0.00070971 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4123-13_0_5_load_9 | 19 | 0.018214 | 0.0045649 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4123-13_0_5_load_85 | 21 | 0.0044992 | 0.0011276 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4123-13_0_5_load_167 | 22 | 0.0089355 | 0.0022394 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4123-13_0_5_load_13 | 24 | 0.00057372 | 0.00014379 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4123-13_0_5_load_93 | 25 | 0.00080904 | 0.00020276 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4123-13_0_5_load_14 | 27 | 0.0019579 | 0.00049069 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4123-13_0_5_load_15 | 28 | 0.0017973 | 0.00045045 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4123-13_0_5_load_16 | 29 | 0.001141 | 0.00028597 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4123-13_0_5_load_17 | 30 | 0.000843 | 0.00021128 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4123-13_0_5_load_18 | 31 | 0.00097688 | 0.00024483 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4123-13_0_5_load_34 | 32 | 0.0012395 | 0.00031064 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4123-13_0_5_load_35 | 33 | 0.00036827 | 9.2297e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4123-13_0_5_load_19 | 34 | 0.0018739 | 0.00046964 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4123-13_0_5_load_20 | 35 | 0.0022439 | 0.00056237 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4123-13_0_5_load_39 | 38 | 0.0015203 | 0.00038102 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4123-13_0_5_load_36 | 39 | 0.0015373 | 0.00038528 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4123-13_0_5_load_41 | 40 | 0.0012952 | 0.00032462 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4123-13_0_5_load_23 | 42 | 0.0021271 | 0.00053311 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4123-13_0_5_load_24 | 43 | 0.0011741 | 0.00029426 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4123-13_0_5_load_26 | 45 | 0.00054381 | 0.00013629 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4123-13_0_5_load_27 | 46 | 0.0007233 | 0.00018128 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4123-13_0_5_load_28 | 47 | 0.0018724 | 0.00046926 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4123-13_0_5_load_29 | 48 | 0.0018119 | 0.0004541 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4123-13_0_5_load_30 | 49 | 0.00041005 | 0.00010277 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4123-13_0_5_load_31 | 50 | 0.0040584 | 0.0010171 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4123-13_0_5_load_32 | 51 | 0.00089582 | 0.00022451 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4123-13_0_5_load_33 | 52 | 0.0017986 | 0.00045078 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4123-13_0_5_load_60 | 53 | 0.0017161 | 0.0004301 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4123-13_0_5_load_129 | 54 | 0.0011425 | 0.00028634 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4123-13_0_5_load_61 | 55 | 0.0048495 | 0.0012154 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4123-13_0_5_load_38 | 56 | 0.0012447 | 0.00031195 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4123-13_0_5_load_128 | 57 | 0.00090337 | 0.00022641 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4123-13_0_5_load_56 | 59 | 0.0010869 | 0.00027241 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4123-13_0_5_load_59 | 61 | 0.00083407 | 0.00020904 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4123-13_0_5_load_42 | 63 | 0.0014589 | 0.00036563 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4123-13_0_5_load_43 | 64 | 0.0036525 | 0.00091541 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4123-13_0_5_load_44 | 65 | 0.0039241 | 0.00098348 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4123-13_0_5_load_45 | 66 | 0.003264 | 0.00081804 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4123-13_0_5_load_46 | 67 | 0.0025699 | 0.00064408 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4123-13_0_5_load_48 | 68 | 0.0012539 | 0.00031426 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4123-13_0_5_load_83 | 69 | 0.0047702 | 0.0011955 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4123-13_0_5_load_58 | 71 | 0.00048007 | 0.00012032 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4123-13_0_5_load_69 | 73 | 0.0098402 | 0.0024662 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4123-13_0_5_load_49 | 74 | 0.001407 | 0.00035262 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4123-13_0_5_load_50 | 75 | 0.0041821 | 0.0010481 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4123-13_0_5_load_51 | 76 | 0.0014012 | 0.00035117 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4123-13_0_5_load_53 | 77 | 0.0034283 | 0.00085921 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4123-13_0_5_load_55 | 78 | 0.0031079 | 0.00077891 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4123-13_0_5_load_57 | 79 | 0.0023309 | 0.00058417 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4123-13_0_5_load_63 | 80 | 0.0017407 | 0.00043625 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4123-13_0_5_load_70 | 82 | 0.0054162 | 0.0013574 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4123-13_0_5_load_94 | 85 | 0.0021761 | 0.00054538 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4123-13_0_5_load_66 | 87 | 0.002918 | 0.00073133 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4123-13_0_5_load_95 | 88 | 0.0045038 | 0.0011288 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4123-13_0_5_load_90 | 89 | 0.0031653 | 0.00079329 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4123-13_0_5_load_72 | 90 | 0.0054324 | 0.0013615 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4123-13_0_5_load_96 | 91 | 0.0053861 | 0.0013499 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4123-13_0_5_load_73 | 93 | 0.0016513 | 0.00041386 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4123-13_0_5_load_74 | 94 | 0.0012846 | 0.00032195 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4123-13_0_5_load_76 | 95 | 0.0030691 | 0.0007692 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4123-13_0_5_load_78 | 96 | 0.0012192 | 0.00030556 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4123-13_0_5_load_84 | 97 | 0.0055441 | 0.0013895 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4123-13_0_5_load_98 | 98 | 0.0056879 | 0.0014255 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4123-13_0_5_load_86 | 99 | 0.0027008 | 0.00067689 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4123-13_0_5_load_87 | 100 | 0.0027763 | 0.00069581 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4123-13_0_5_load_89 | 101 | 0.0052356 | 0.0013122 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4123-13_0_5_load_148 | 102 | 0.0046439 | 0.0011639 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4123-13_0_5_load_100 | 103 | 0.0058218 | 0.0014591 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4123-13_0_5_load_101 | 104 | 0.0073419 | 0.0018401 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4123-13_0_5_load_103 | 106 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4123-13_0_5_load_104 | 107 | 0.0084274 | 0.0021121 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4123-13_0_5_load_105 | 108 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4123-13_0_5_load_106 | 109 | 0.0030508 | 0.0007646 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4123-13_0_5_load_172 | 110 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4123-13_0_5_load_115 | 111 | 0.0074039 | 0.0018556 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4123-13_0_5_load_173 | 112 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4123-13_0_5_load_107 | 114 | 0.010605 | 0.0026578 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4123-13_0_5_load_108 | 115 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4123-13_0_5_load_110 | 117 | 0.001866 | 0.00046768 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4123-13_0_5_load_111 | 118 | 0.0022936 | 0.00057484 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4123-13_0_5_load_112 | 119 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4123-13_0_5_load_113 | 120 | 0.0023832 | 0.00059728 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4123-13_0_5_load_114 | 121 | 0.0012274 | 0.00030761 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4123-13_0_5_load_170 | 123 | 0.0012267 | 0.00030743 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4123-13_0_5_load_154 | 124 | 0.009475 | 0.0023746 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4123-13_0_5_load_171 | 125 | 0.0012255 | 0.00030715 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4123-13_0_5_load_117 | 126 | 0.0022659 | 0.00056788 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4123-13_0_5_load_134 | 128 | 0.0034863 | 0.00087376 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4123-13_0_5_load_131 | 129 | 0.0035702 | 0.00089479 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4123-13_0_5_load_141 | 131 | 0.0032099 | 0.00080448 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4123-13_0_5_load_144 | 133 | 0.001225 | 0.00030702 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4123-13_0_5_load_130 | 134 | 0.004053 | 0.0010158 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4123-13_0_5_load_163 | 135 | 0.0072659 | 0.001821 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4123-13_0_5_load_136 | 136 | 0.0043782 | 0.0010973 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4123-13_0_5_load_120 | 137 | 0.0028292 | 0.00070907 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4123-13_0_5_load_121 | 138 | 0.0033805 | 0.00084724 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4123-13_0_5_load_122 | 139 | 0.0033543 | 0.00084066 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4123-13_0_5_load_123 | 140 | 0.0026743 | 0.00067024 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4123-13_0_5_load_124 | 141 | 0.0043472 | 0.0010895 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4123-13_0_5_load_125 | 142 | 0.0012333 | 0.00030908 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4123-13_0_5_load_126 | 143 | 0.0030218 | 0.00075734 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4123-13_0_5_load_127 | 144 | 0.0025293 | 0.00063389 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4123-13_0_5_load_147 | 145 | 0.0025555 | 0.00064046 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4123-13_0_5_load_142 | 146 | 0.004058 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4123-13_0_5_load_132 | 147 | 0.001428 | 0.00035788 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4123-13_0_5_load_133 | 148 | 0.0014267 | 0.00035758 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4123-13_0_5_load_135 | 149 | 0.0014277 | 0.00035782 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4123-13_0_5_load_174 | 150 | 0.0030985 | 0.00077656 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4123-13_0_5_load_145 | 151 | 0.0012254 | 0.00030711 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4123-13_0_5_load_139 | 153 | 0.0026165 | 0.00065575 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4123-13_0_5_load_140 | 154 | 0.0015623 | 0.00039156 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4123-13_0_5_load_143 | 155 | 0.001114 | 0.0002792 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4123-13_0_5_load_159 | 156 | 0.0015615 | 0.00039135 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4123-13_0_5_load_162 | 157 | 0.0074276 | 0.0018615 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4123-13_0_5_load_160 | 158 | 0.0012258 | 0.00030722 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4123-13_0_5_load_146 | 159 | 0.0012262 | 0.00030731 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4123-13_0_5_load_152 | 160 | 0.013887 | 0.0034804 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4123-13_0_5_load_165 | 161 | 0.0034394 | 0.000862 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4123-13_0_5_load_155 | 163 | 0.005251 | 0.001316 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4123-13_0_5_load_156 | 164 | 0.010618 | 0.0026611 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4123-13_0_5_load_157 | 165 | 0.0066438 | 0.0016651 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4123-13_0_5_load_158 | 166 | 0.0065112 | 0.0016319 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4123-13_0_5_load_164 | 167 | 0.0067225 | 0.0016848 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4123-13_0_5_load_168 | 168 | 0.007822 | 0.0019604 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4123-13_0_5_load_161 | 169 | 0.0078723 | 0.001973 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4123-13_0_5_load_169 | 170 | 0.042949 | 0.010764 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4123-13_0_5_line_0 |  | 0 | 1 | 0.0028096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_4123-13_0_5_line_1 |  | 0 | 2 | 0.018343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
2 | LV_4123-13_0_5_line_2 |  | 1 | 3 | 0.019205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_4123-13_0_5_line_3 |  | 2 | 4 | 0.0029278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
4 | LV_4123-13_0_5_line_4 |  | 3 | 5 | 0.014616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_4123-13_0_5_line_5 |  | 3 | 6 | 0.043001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_4123-13_0_5_line_6 |  | 4 | 7 | 0.0057186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_4123-13_0_5_line_7 |  | 5 | 8 | 0.016236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_4123-13_0_5_line_8 |  | 6 | 11 | 0.028641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4123-13_0_5_line_9 |  | 6 | 12 | 0.020461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4123-13_0_5_line_10 |  | 6 | 9 | 0.029252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4123-13_0_5_line_11 |  | 7 | 13 | 0.01537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_4123-13_0_5_line_12 |  | 8 | 14 | 0.0028967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_4123-13_0_5_line_13 |  | 9 | 10 | 0.013032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4123-13_0_5_line_14 |  | 10 | 15 | 0.03145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4123-13_0_5_line_15 |  | 11 | 16 | 0.012066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4123-13_0_5_line_16 |  | 12 | 17 | 0.038666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4123-13_0_5_line_17 |  | 13 | 18 | 0.014274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_4123-13_0_5_line_18 |  | 14 | 87 | 0.02721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_4123-13_0_5_line_19 |  | 15 | 98 | 0.02657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4123-13_0_5_line_20 |  | 16 | 93 | 0.0013766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4123-13_0_5_line_21 |  | 17 | 72 | 0.0066575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4123-13_0_5_line_22 |  | 18 | 160 | 0.03434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4123-13_0_5_line_23 |  | 18 | 122 | 0.012706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_4123-13_0_5_line_24 |  | 19 | 20 | 0.074252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4123-13_0_5_line_25 |  | 20 | 21 | 0.064423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4123-13_0_5_line_26 |  | 21 | 22 | 0.07698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4123-13_0_5_line_27 |  | 21 | 23 | 0.01871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4123-13_0_5_line_28 |  | 23 | 69 | 0.014705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4123-13_0_5_line_29 |  | 23 | 70 | 0.003376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4123-13_0_5_line_30 |  | 23 | 66 | 0.035768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4123-13_0_5_line_31 |  | 24 | 25 | 0.016696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4123-13_0_5_line_32 |  | 25 | 26 | 0.017605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4123-13_0_5_line_33 |  | 26 | 58 | 0.008205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4123-13_0_5_line_34 |  | 27 | 28 | 0.00035916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4123-13_0_5_line_35 |  | 27 | 29 | 0.03735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4123-13_0_5_line_36 |  | 28 | 30 | 0.020917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4123-13_0_5_line_37 |  | 30 | 31 | 0.0031573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4123-13_0_5_line_38 |  | 31 | 32 | 0.010264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4123-13_0_5_line_39 |  | 32 | 33 | 0.0049261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4123-13_0_5_line_40 |  | 33 | 49 | 0.0047157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4123-13_0_5_line_41 |  | 34 | 35 | 0.012702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4123-13_0_5_line_42 |  | 34 | 36 | 0.043031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4123-13_0_5_line_43 |  | 36 | 37 | 0.039532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4123-13_0_5_line_44 |  | 37 | 38 | 0.010768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4123-13_0_5_line_45 |  | 37 | 39 | 0.0045998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4123-13_0_5_line_46 |  | 38 | 40 | 0.025721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4123-13_0_5_line_47 |  | 39 | 41 | 0.016916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4123-13_0_5_line_48 |  | 41 | 56 | 0.033148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4123-13_0_5_line_49 |  | 42 | 43 | 0.0079887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4123-13_0_5_line_50 |  | 42 | 44 | 0.016307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4123-13_0_5_line_51 |  | 43 | 45 | 0.0017115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4123-13_0_5_line_52 |  | 44 | 46 | 0.012406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4123-13_0_5_line_53 |  | 44 | 47 | 0.017568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4123-13_0_5_line_54 |  | 44 | 48 | 0.020363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4123-13_0_5_line_55 |  | 45 | 49 | 0.005117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4123-13_0_5_line_56 |  | 46 | 50 | 0.0057153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4123-13_0_5_line_57 |  | 47 | 51 | 0.012173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4123-13_0_5_line_58 |  | 48 | 52 | 0.00079404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4123-13_0_5_line_59 |  | 50 | 53 | 0.0050799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4123-13_0_5_line_60 |  | 52 | 54 | 0.011557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4123-13_0_5_line_61 |  | 53 | 55 | 0.020829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4123-13_0_5_line_62 |  | 54 | 57 | 0.00019249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4123-13_0_5_line_63 |  | 55 | 83 | 0.023822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4123-13_0_5_line_64 |  | 56 | 58 | 0.018192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4123-13_0_5_line_65 |  | 57 | 144 | 0.0095394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4123-13_0_5_line_66 |  | 58 | 59 | 0.028827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4123-13_0_5_line_67 |  | 59 | 62 | 0.012742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4123-13_0_5_line_68 |  | 60 | 61 | 0.00026604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4123-13_0_5_line_69 |  | 60 | 62 | 0.003118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4123-13_0_5_line_70 |  | 61 | 71 | 0.010145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4123-13_0_5_line_71 |  | 62 | 78 | 0.023203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4123-13_0_5_line_72 |  | 62 | 75 | 0.032429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4123-13_0_5_line_73 |  | 63 | 64 | 0.0095566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4123-13_0_5_line_74 |  | 63 | 65 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4123-13_0_5_line_75 |  | 64 | 66 | 0.021895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4123-13_0_5_line_76 |  | 65 | 67 | 0.019316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4123-13_0_5_line_77 |  | 67 | 68 | 0.013818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4123-13_0_5_line_78 |  | 68 | 71 | 0.012433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4123-13_0_5_line_79 |  | 69 | 72 | 0.033411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4123-13_0_5_line_80 |  | 70 | 73 | 0.018706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4123-13_0_5_line_81 |  | 73 | 81 | 0.040819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4123-13_0_5_line_82 |  | 74 | 75 | 3.0679e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4123-13_0_5_line_83 |  | 74 | 76 | 0.019688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4123-13_0_5_line_84 |  | 76 | 77 | 0.0036105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4123-13_0_5_line_85 |  | 77 | 79 | 0.019997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4123-13_0_5_line_86 |  | 79 | 80 | 0.0043509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4123-13_0_5_line_87 |  | 81 | 82 | 0.015328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4123-13_0_5_line_88 |  | 82 | 90 | 0.017044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4123-13_0_5_line_89 |  | 83 | 84 | 0.005287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4123-13_0_5_line_90 |  | 83 | 85 | 0.030727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4123-13_0_5_line_91 |  | 84 | 86 | 0.035433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4123-13_0_5_line_92 |  | 84 | 87 | 0.012655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4123-13_0_5_line_93 |  | 85 | 88 | 0.009917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4123-13_0_5_line_94 |  | 86 | 89 | 0.01246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4123-13_0_5_line_95 |  | 88 | 102 | 0.0040613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4123-13_0_5_line_96 |  | 90 | 91 | 0.016822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4123-13_0_5_line_97 |  | 91 | 92 | 0.013259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4123-13_0_5_line_98 |  | 92 | 101 | 0.0048433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4123-13_0_5_line_99 |  | 93 | 94 | 0.0069712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4123-13_0_5_line_100 |  | 94 | 95 | 0.018703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4123-13_0_5_line_101 |  | 95 | 96 | 0.041599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4123-13_0_5_line_102 |  | 97 | 98 | 0.017115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4123-13_0_5_line_103 |  | 99 | 100 | 0.01709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4123-13_0_5_line_104 |  | 100 | 101 | 0.011005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4123-13_0_5_line_105 |  | 103 | 104 | 0.0020259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4123-13_0_5_line_106 |  | 103 | 105 | 0.014207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4123-13_0_5_line_107 |  | 104 | 106 | 0.0064135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4123-13_0_5_line_108 |  | 105 | 107 | 0.0075038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4123-13_0_5_line_109 |  | 106 | 108 | 0.0064147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4123-13_0_5_line_110 |  | 107 | 109 | 0.029643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4123-13_0_5_line_111 |  | 108 | 110 | 0.0064135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4123-13_0_5_line_112 |  | 109 | 111 | 0.01262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4123-13_0_5_line_113 |  | 110 | 112 | 0.0064147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4123-13_0_5_line_114 |  | 111 | 113 | 0.0096716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4123-13_0_5_line_115 |  | 112 | 125 | 0.0064098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4123-13_0_5_line_116 |  | 113 | 126 | 0.012436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4123-13_0_5_line_117 |  | 114 | 115 | 0.0073067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4123-13_0_5_line_118 |  | 114 | 116 | 0.0032097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4123-13_0_5_line_119 |  | 115 | 117 | 0.0023317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4123-13_0_5_line_120 |  | 116 | 118 | 0.0035871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4123-13_0_5_line_121 |  | 116 | 119 | 0.014801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4123-13_0_5_line_122 |  | 118 | 120 | 0.029019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4123-13_0_5_line_123 |  | 119 | 121 | 0.0064126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4123-13_0_5_line_124 |  | 120 | 122 | 0.012644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4123-13_0_5_line_125 |  | 121 | 123 | 0.0070766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4123-13_0_5_line_126 |  | 122 | 124 | 0.010724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4123-13_0_5_line_127 |  | 123 | 125 | 0.0064092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4123-13_0_5_line_128 |  | 124 | 162 | 0.011179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4123-13_0_5_line_129 |  | 127 | 128 | 0.012622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4123-13_0_5_line_130 |  | 127 | 129 | 0.018349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4123-13_0_5_line_131 |  | 128 | 133 | 0.016026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4123-13_0_5_line_132 |  | 129 | 134 | 0.0017933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4123-13_0_5_line_133 |  | 130 | 131 | 0.020573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4123-13_0_5_line_134 |  | 130 | 132 | 0.003293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4123-13_0_5_line_135 |  | 131 | 135 | 0.010819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4123-13_0_5_line_136 |  | 132 | 136 | 0.014677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4123-13_0_5_line_137 |  | 133 | 151 | 0.023585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4123-13_0_5_line_138 |  | 134 | 147 | 0.020112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4123-13_0_5_line_139 |  | 135 | 157 | 0.01052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4123-13_0_5_line_140 |  | 136 | 152 | 0.0016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4123-13_0_5_line_141 |  | 137 | 138 | 0.017249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4123-13_0_5_line_142 |  | 137 | 139 | 0.0013457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4123-13_0_5_line_143 |  | 138 | 140 | 0.0023704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4123-13_0_5_line_144 |  | 139 | 141 | 0.0018012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4123-13_0_5_line_145 |  | 140 | 142 | 0.0073476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4123-13_0_5_line_146 |  | 141 | 143 | 0.0083948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4123-13_0_5_line_147 |  | 142 | 144 | 0.0018938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4123-13_0_5_line_148 |  | 143 | 145 | 0.0075549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4123-13_0_5_line_149 |  | 145 | 146 | 0.0080415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4123-13_0_5_line_150 |  | 146 | 153 | 0.004669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4123-13_0_5_line_151 |  | 147 | 148 | 0.006263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4123-13_0_5_line_152 |  | 148 | 149 | 0.0062639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4123-13_0_5_line_153 |  | 149 | 150 | 0.0018874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4123-13_0_5_line_154 |  | 151 | 159 | 0.005499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4123-13_0_5_line_155 |  | 152 | 153 | 0.01794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4123-13_0_5_line_156 |  | 152 | 154 | 0.011619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4123-13_0_5_line_157 |  | 154 | 155 | 0.001076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4123-13_0_5_line_158 |  | 155 | 156 | 0.0044219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4123-13_0_5_line_159 |  | 156 | 158 | 0.0055006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4123-13_0_5_line_160 |  | 157 | 169 | 0.019921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4123-13_0_5_line_161 |  | 158 | 159 | 0.0055024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4123-13_0_5_line_162 |  | 160 | 161 | 0.034504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4123-13_0_5_line_163 |  | 162 | 163 | 0.018034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4123-13_0_5_line_164 |  | 163 | 164 | 0.0049984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4123-13_0_5_line_165 |  | 164 | 165 | 0.00036451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4123-13_0_5_line_166 |  | 165 | 166 | 0.0059278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4123-13_0_5_line_167 |  | 166 | 167 | 0.0059682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4123-13_0_5_line_168 |  | 167 | 168 | 0.0065525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4123-13_0_5_line_169 |  | 168 | 170 | 0.0032385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4123-13_0_5_trafo_65 | 0.63 MVA 20/0.4 kV | 171 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2659575.7823 | 1259461.4488 | 2659573.0884 | 1259462.2467
1 | 2659575.7823 | 1259461.4488 | 2659582.7785 | 1259456.8158 | 2659589.8514 | 1259449.8153
2 | 2659554.2074 | 1259465.4346 | 2659562.793 | 1259464.6537 | 2659569.1748 | 1259463.4059 | 2659573.0884 | 1259462.2467
3 | 2659589.8514 | 1259449.8153 | 2659589.8514 | 1259449.8153 | 2659591.5005 | 1259447.3961
4 | 2659540.7202 | 1259459.7059 | 2659554.2074 | 1259465.4346
5 | 2659554.2074 | 1259465.4346 | 2659555.6501 | 1259471.131 | 2659558.2384 | 1259476.8278 | 2659560.0449 | 1259480.0706 | 2659565.4236 | 1259490.1097 | 2659566.8839 | 1259494.0495 | 2659567.9251 | 1259499.1859 | 2659568.359 | 1259505.4948
6 | 2659594.7215 | 1259442.6708 | 2659591.5005 | 1259447.3961
7 | 2659540.7202 | 1259459.7059 | 2659525.4804 | 1259454.1058
8 | 2659568.359 | 1259505.4948 | 2659576.1641 | 1259507.3636 | 2659590.445 | 1259522.2308
9 | 2659568.359 | 1259505.4948 | 2659565.9072 | 1259513.943 | 2659561.9392 | 1259524.7553 | 2659561.8767 | 1259524.8883
10 | 2659561.1104 | 1259517.9865 | 2659563.3911 | 1259512.3053 | 2659564.8227 | 1259504.1249 | 2659564.824 | 1259498.7544 | 2659567.9251 | 1259499.1859 | 2659568.359 | 1259505.4948
11 | 2659594.7215 | 1259442.6708 | 2659603.3788 | 1259429.9704
12 | 2659525.4804 | 1259454.1058 | 2659522.7615 | 1259453.1067
13 | 2659561.1104 | 1259517.9865 | 2659549.1323 | 1259512.8512
14 | 2659533.7494 | 1259497.0184 | 2659535.9855 | 1259496.5183 | 2659553.3453 | 1259503.1532 | 2659549.1323 | 1259512.8512
15 | 2659590.445 | 1259522.2308 | 2659593.8947 | 1259525.8221 | 2659599.6762 | 1259529.9199
16 | 2659561.8767 | 1259524.8883 | 2659557.9185 | 1259533.3099 | 2659544.4092 | 1259559.3777
17 | 2659611.4185 | 1259418.1762 | 2659603.3788 | 1259429.9704
18 | 2659497.2215 | 1259443.7217 | 2659522.7615 | 1259453.1067
19 | 2659533.7494 | 1259497.0184 | 2659524.7999 | 1259522.0362
20 | 2659600.7993 | 1259530.716 | 2659599.6762 | 1259529.9199
21 | 2659541.346 | 1259565.2886 | 2659544.4092 | 1259559.3777
22 | 2659611.4185 | 1259418.1762 | 2659639.78 | 1259437.5368
23 | 2659614.685 | 1259408.1796 | 2659609.1981 | 1259416.3636 | 2659611.4185 | 1259418.1762
24 | 2659469.4068 | 1259668.2401 | 2659443.4408 | 1259681.0108 | 2659437.9554 | 1259679.3434 | 2659432.7659 | 1259676.7227 | 2659424.7366 | 1259674.6851 | 2659399.4603 | 1259671.4324
25 | 2659504.4925 | 1259614.2094 | 2659469.4068 | 1259668.2401
26 | 2659504.4925 | 1259614.2094 | 2659562.3437 | 1259664.9942
27 | 2659509.0972 | 1259596.3869 | 2659509.2934 | 1259601.6149 | 2659504.4925 | 1259614.2094
28 | 2659509.0972 | 1259596.3869 | 2659515.9068 | 1259596.0551 | 2659523.1514 | 1259592.9368
29 | 2659509.0972 | 1259596.3869 | 2659509.3421 | 1259593.0202
30 | 2659509.0972 | 1259596.3869 | 2659500.6149 | 1259595.1674 | 2659475.3035 | 1259585.214
31 | 2659336.5136 | 1259577.2401 | 2659340.8526 | 1259561.1176
32 | 2659345.428 | 1259544.1173 | 2659340.8526 | 1259561.1176
33 | 2659347.1516 | 1259536.0954 | 2659345.428 | 1259544.1173
34 | 2659352.3986 | 1259376.8586 | 2659352.661 | 1259377.1039
35 | 2659352.3986 | 1259376.8586 | 2659349.7612 | 1259374.3935 | 2659336.2893 | 1259360.3261 | 2659326.752 | 1259349.7221
36 | 2659352.661 | 1259377.1039 | 2659358.095 | 1259382.1827 | 2659365.5891 | 1259388.0176 | 2659368.8663 | 1259390.2786
37 | 2659368.8663 | 1259390.2786 | 2659371.4651 | 1259392.0715
38 | 2659380.0616 | 1259397.6654 | 2659377.1846 | 1259396.0175 | 2659371.4651 | 1259392.0715
39 | 2659384.3361 | 1259400.1138 | 2659380.0616 | 1259397.6654
40 | 2659388.4281 | 1259402.4577 | 2659384.3361 | 1259400.1138
41 | 2659332.5787 | 1259415.3954 | 2659327.8188 | 1259427.1723
42 | 2659311.6942 | 1259467.0679 | 2659327.8188 | 1259427.1723
43 | 2659311.6942 | 1259467.0679 | 2659329.3801 | 1259474.2948 | 2659333.8848 | 1259476.0635 | 2659348.39 | 1259481.7685
44 | 2659348.39 | 1259481.7685 | 2659353.6891 | 1259472.3945
45 | 2659348.39 | 1259481.7685 | 2659352.6709 | 1259483.4517
46 | 2659366.3465 | 1259450.0034 | 2659353.6891 | 1259472.3945
47 | 2659368.4135 | 1259489.6417 | 2659352.6709 | 1259483.4517
48 | 2659368.4135 | 1259489.6417 | 2659353.2664 | 1259519.127
49 | 2659394.4352 | 1259405.7033 | 2659401.4915 | 1259409.4485
50 | 2659415.46 | 1259417.8395 | 2659406.5101 | 1259412.1122 | 2659401.4915 | 1259409.4485
51 | 2659394.4352 | 1259405.7033 | 2659392.9235 | 1259404.9009
52 | 2659415.46 | 1259417.8395 | 2659426.9959 | 1259421.2466 | 2659427.3592 | 1259421.3487
53 | 2659415.46 | 1259417.8395 | 2659414.1634 | 1259423.853 | 2659410.3111 | 1259431.4198 | 2659408.6374 | 1259433.8184
54 | 2659415.46 | 1259417.8395 | 2659418.3682 | 1259410.4633 | 2659423.3376 | 1259401.996 | 2659424.7285 | 1259399.7804
55 | 2659392.9235 | 1259404.9009 | 2659389.7904 | 1259403.238 | 2659388.4281 | 1259402.4577
56 | 2659432.8613 | 1259422.8954 | 2659427.3592 | 1259421.3487
57 | 2659401.671 | 1259443.8012 | 2659408.6374 | 1259433.8184
58 | 2659424.7285 | 1259399.7804 | 2659425.1507 | 1259399.1079
59 | 2659437.7517 | 1259424.2702 | 2659432.8613 | 1259422.8954
60 | 2659425.1507 | 1259399.1079 | 2659431.2954 | 1259389.3199
61 | 2659437.7517 | 1259424.2702 | 2659441.4348 | 1259425.3056 | 2659450.6875 | 1259427.9004 | 2659457.7346 | 1259430.136
62 | 2659431.2954 | 1259389.3199 | 2659431.3978 | 1259389.1569
63 | 2659480.4413 | 1259437.3394 | 2659457.7346 | 1259430.136
64 | 2659347.1516 | 1259536.0954 | 2659349.0408 | 1259527.3525 | 2659353.2664 | 1259519.127
65 | 2659436.4698 | 1259381.0776 | 2659431.3978 | 1259389.1569
66 | 2659347.1516 | 1259536.0954 | 2659355.7181 | 1259531.945 | 2659357.0889 | 1259534.2937 | 2659359.0607 | 1259536.1037 | 2659362.8805 | 1259538.5215 | 2659369.0803 | 1259541.1189 | 2659371.5946 | 1259542.0145
67 | 2659383.5982 | 1259546.2905 | 2659371.5946 | 1259542.0145
68 | 2659382.3185 | 1259549.1353 | 2659382.5653 | 1259549.2346
69 | 2659383.5982 | 1259546.2905 | 2659382.3185 | 1259549.1353
70 | 2659391.9771 | 1259553.0224 | 2659382.5653 | 1259549.2346
71 | 2659383.5982 | 1259546.2905 | 2659389.5976 | 1259548.5856 | 2659405.0864 | 1259555.0393
72 | 2659383.5982 | 1259546.2905 | 2659396.6705 | 1259516.6127
73 | 2659445.8463 | 1259574.198 | 2659454.8226 | 1259577.4775
74 | 2659445.8463 | 1259574.198 | 2659434.274 | 1259569.9702
75 | 2659454.8226 | 1259577.4775 | 2659466.1997 | 1259581.634 | 2659475.3035 | 1259585.214
76 | 2659434.274 | 1259569.9702 | 2659432.5258 | 1259569.3314 | 2659416.3315 | 1259562.8189
77 | 2659416.3315 | 1259562.8189 | 2659403.5113 | 1259557.6632
78 | 2659391.9771 | 1259553.0224 | 2659399.4046 | 1259556.0116 | 2659403.5113 | 1259557.6632
79 | 2659541.346 | 1259565.2886 | 2659536.5547 | 1259576.2706 | 2659529.8803 | 1259585.6436 | 2659523.1514 | 1259592.9368
80 | 2659509.3421 | 1259593.0202 | 2659503.8168 | 1259592.3197 | 2659498.539 | 1259590.9768 | 2659491.356 | 1259588.2292
81 | 2659453.1631 | 1259573.8308 | 2659465.5135 | 1259578.6695 | 2659489.8517 | 1259587.6538 | 2659491.356 | 1259588.2292
82 | 2659396.6718 | 1259516.6099 | 2659396.6705 | 1259516.6127
83 | 2659396.6718 | 1259516.6099 | 2659404.6081 | 1259498.5924
84 | 2659406.0635 | 1259495.2882 | 2659404.6081 | 1259498.5924
85 | 2659414.1244 | 1259476.9875 | 2659406.0635 | 1259495.2882
86 | 2659415.8783 | 1259473.0058 | 2659414.1244 | 1259476.9875
87 | 2659453.1631 | 1259573.8308 | 2659458.7638 | 1259559.5625
88 | 2659458.7638 | 1259559.5625 | 2659464.9914 | 1259543.6972
89 | 2659485.3431 | 1259439.3568 | 2659480.4413 | 1259437.3394
90 | 2659480.4413 | 1259437.3394 | 2659489.7507 | 1259408.0562 | 2659489.7507 | 1259408.0562
91 | 2659473.6252 | 1259472.7966 | 2659480.8034 | 1259452.3094 | 2659485.3431 | 1259439.3568
92 | 2659485.3431 | 1259439.3568 | 2659497.2215 | 1259443.7217
93 | 2659480.5229 | 1259404.4239 | 2659489.7507 | 1259408.0562
94 | 2659473.6252 | 1259472.7966 | 2659485.2329 | 1259477.3261
95 | 2659480.5229 | 1259404.4239 | 2659476.7438 | 1259402.9363
96 | 2659471.138 | 1259528.0382 | 2659464.9914 | 1259543.6972
97 | 2659475.9828 | 1259515.6957 | 2659471.138 | 1259528.0382
98 | 2659475.9828 | 1259515.6957 | 2659477.7542 | 1259511.188 | 2659477.7542 | 1259511.188
99 | 2659600.7993 | 1259530.716 | 2659606.4867 | 1259534.7471
100 | 2659621.7452 | 1259545.5622 | 2659606.4867 | 1259534.7471
101 | 2659621.7452 | 1259545.5622 | 2659655.6839 | 1259569.6175
102 | 2659524.7999 | 1259522.0362 | 2659519.0354 | 1259538.1507
103 | 2659467.438 | 1259507.3549 | 2659451.4178 | 1259501.4023
104 | 2659467.438 | 1259507.3549 | 2659477.7542 | 1259511.188
105 | 2659610.4587 | 1259326.3098 | 2659611.4513 | 1259324.5437
106 | 2659618.4114 | 1259312.1588 | 2659611.4513 | 1259324.5437
107 | 2659607.3166 | 1259331.9009 | 2659610.4587 | 1259326.3098
108 | 2659618.4114 | 1259312.1588 | 2659611.4844 | 1259309.2738
109 | 2659604.1739 | 1259337.493 | 2659607.3166 | 1259331.9009
110 | 2659611.4844 | 1259309.2738 | 2659591.5992 | 1259300.9919 | 2659584.0866 | 1259297.9581
111 | 2659601.0318 | 1259343.0841 | 2659604.1739 | 1259337.493
112 | 2659572.385 | 1259293.2327 | 2659584.0866 | 1259297.9581
113 | 2659601.0318 | 1259343.0841 | 2659597.8891 | 1259348.6762
114 | 2659563.4171 | 1259289.6112 | 2659572.385 | 1259293.2327
115 | 2659594.7488 | 1259354.2641 | 2659597.8891 | 1259348.6762
116 | 2659563.4171 | 1259289.6112 | 2659566.3044 | 1259277.5152
117 | 2659567.7061 | 1259378.1322 | 2659573.8606 | 1259382.0705
118 | 2659576.5642 | 1259383.8005 | 2659573.8606 | 1259382.0705
119 | 2659565.742 | 1259376.8755 | 2659567.7061 | 1259378.1322
120 | 2659576.5642 | 1259383.8005 | 2659579.5862 | 1259385.7331
121 | 2659576.5642 | 1259383.8005 | 2659584.5759 | 1259371.3554
122 | 2659579.5862 | 1259385.7331 | 2659604.0331 | 1259401.3675
123 | 2659584.5759 | 1259371.3554 | 2659588.047 | 1259365.9635
124 | 2659614.685 | 1259408.1796 | 2659604.0331 | 1259401.3675
125 | 2659588.047 | 1259365.9635 | 2659589.0458 | 1259364.4121 | 2659591.6088 | 1259359.8514
126 | 2659614.685 | 1259408.1796 | 2659619.7882 | 1259398.7473
127 | 2659591.6088 | 1259359.8514 | 2659594.7488 | 1259354.2641
128 | 2659625.1077 | 1259388.9151 | 2659619.7882 | 1259398.7473
129 | 2659547.6978 | 1259307.1435 | 2659535.0893 | 1259306.554
130 | 2659547.6978 | 1259307.1435 | 2659537.8019 | 1259322.5955
131 | 2659524.1147 | 1259311.3358 | 2659524.3645 | 1259306.0526 | 2659535.0893 | 1259306.554
132 | 2659537.8019 | 1259322.5955 | 2659536.8348 | 1259324.1057
133 | 2659477.2335 | 1259295.3156 | 2659457.3621 | 1259289.9902
134 | 2659476.0944 | 1259298.4064 | 2659477.2335 | 1259295.3156
135 | 2659446.9119 | 1259287.1896 | 2659457.3621 | 1259289.9902
136 | 2659476.0944 | 1259298.4064 | 2659476.245 | 1259313.0826
137 | 2659509.4279 | 1259320.2305 | 2659520.3067 | 1259322.0344 | 2659523.7134 | 1259319.8226 | 2659524.1147 | 1259311.3358
138 | 2659525.9883 | 1259341.0419 | 2659536.8348 | 1259324.1057
139 | 2659437.2837 | 1259282.9876 | 2659445.7653 | 1259286.8823 | 2659446.9119 | 1259287.1896
140 | 2659476.262 | 1259314.731 | 2659476.245 | 1259313.0826
141 | 2659453.5331 | 1259357.815 | 2659443.1813 | 1259371.6127
142 | 2659453.5331 | 1259357.815 | 2659454.3407 | 1259356.7386
143 | 2659441.7588 | 1259373.5088 | 2659443.1813 | 1259371.6127
144 | 2659455.4217 | 1259355.2978 | 2659454.3407 | 1259356.7386
145 | 2659441.7588 | 1259373.5088 | 2659438.4665 | 1259377.8971 | 2659437.4767 | 1259379.4737
146 | 2659460.4596 | 1259348.5827 | 2659455.4217 | 1259355.2978
147 | 2659436.4698 | 1259381.0776 | 2659437.4767 | 1259379.4737
148 | 2659465.2847 | 1259342.7762 | 2659462.0969 | 1259346.4005 | 2659460.4596 | 1259348.5827
149 | 2659465.2847 | 1259342.7762 | 2659468.9897 | 1259338.564 | 2659469.92 | 1259336.3172
150 | 2659471.7062 | 1259332.0034 | 2659469.92 | 1259336.3172
151 | 2659522.6106 | 1259346.3161 | 2659525.9883 | 1259341.0419
152 | 2659522.6106 | 1259346.3161 | 2659519.2324 | 1259351.5909
153 | 2659518.2145 | 1259353.1804 | 2659519.2324 | 1259351.5909
154 | 2659504.0029 | 1259319.3309 | 2659509.4279 | 1259320.2305
155 | 2659476.262 | 1259314.731 | 2659475.2454 | 1259319.88 | 2659473.9184 | 1259326.6605 | 2659471.7062 | 1259332.0034
156 | 2659476.262 | 1259314.731 | 2659487.7243 | 1259316.6316
157 | 2659487.7243 | 1259316.6316 | 2659488.7858 | 1259316.8077
158 | 2659493.1481 | 1259317.531 | 2659488.7858 | 1259316.8077
159 | 2659498.5747 | 1259318.4308 | 2659493.1481 | 1259317.531
160 | 2659418.4128 | 1259277.1584 | 2659428.238 | 1259278.8339 | 2659437.2837 | 1259282.9876
161 | 2659498.5747 | 1259318.4308 | 2659504.0029 | 1259319.3309
162 | 2659667.9943 | 1259457.398 | 2659640.7639 | 1259438.2084 | 2659639.78 | 1259437.5368
163 | 2659625.1077 | 1259388.9151 | 2659615.4918 | 1259382.7249 | 2659617.8331 | 1259376.5563
164 | 2659617.8331 | 1259376.5563 | 2659619.6068 | 1259371.8832
165 | 2659619.7361 | 1259371.5424 | 2659619.6068 | 1259371.8832
166 | 2659621.8396 | 1259366.0004 | 2659619.7361 | 1259371.5424
167 | 2659623.9575 | 1259360.4206 | 2659621.8396 | 1259366.0004
168 | 2659623.9575 | 1259360.4206 | 2659626.2827 | 1259354.2945
169 | 2659627.4318 | 1259351.2668 | 2659626.2827 | 1259354.2945

## bus_geodata
| x | y | coords
0 | 2659575.7823 | 1259461.4488
1 | 2659573.0884 | 1259462.2467
2 | 2659589.8514 | 1259449.8153
3 | 2659554.2074 | 1259465.4346
4 | 2659591.5005 | 1259447.3961
5 | 2659540.7202 | 1259459.7059
6 | 2659568.359 | 1259505.4948
7 | 2659594.7215 | 1259442.6708
8 | 2659525.4804 | 1259454.1058
9 | 2659561.1104 | 1259517.9865
10 | 2659549.1323 | 1259512.8512
11 | 2659590.445 | 1259522.2308
12 | 2659561.8767 | 1259524.8883
13 | 2659603.3788 | 1259429.9704
14 | 2659522.7615 | 1259453.1067
15 | 2659533.7494 | 1259497.0184
16 | 2659599.6762 | 1259529.9199
17 | 2659544.4092 | 1259559.3777
18 | 2659611.4185 | 1259418.1762
19 | 2659399.4603 | 1259671.4324
20 | 2659469.4068 | 1259668.2401
21 | 2659504.4925 | 1259614.2094
22 | 2659562.3437 | 1259664.9942
23 | 2659509.0972 | 1259596.3869
24 | 2659336.5136 | 1259577.2401
25 | 2659340.8526 | 1259561.1176
26 | 2659345.428 | 1259544.1173
27 | 2659352.3986 | 1259376.8586
28 | 2659352.661 | 1259377.1039
29 | 2659326.752 | 1259349.7221
30 | 2659368.8663 | 1259390.2786
31 | 2659371.4651 | 1259392.0715
32 | 2659380.0616 | 1259397.6654
33 | 2659384.3361 | 1259400.1138
34 | 2659327.8189 | 1259427.1723
35 | 2659332.5787 | 1259415.3954
36 | 2659311.6942 | 1259467.0679
37 | 2659348.39 | 1259481.7685
38 | 2659353.6891 | 1259472.3945
39 | 2659352.6709 | 1259483.4517
40 | 2659366.3465 | 1259450.0034
41 | 2659368.4135 | 1259489.6417
42 | 2659401.4915 | 1259409.4485
43 | 2659394.4352 | 1259405.7033
44 | 2659415.46 | 1259417.8395
45 | 2659392.9235 | 1259404.9009
46 | 2659427.3592 | 1259421.3487
47 | 2659408.6374 | 1259433.8184
48 | 2659424.7285 | 1259399.7804
49 | 2659388.4281 | 1259402.4577
50 | 2659432.8613 | 1259422.8954
51 | 2659401.671 | 1259443.8012
52 | 2659425.1507 | 1259399.1079
53 | 2659437.7517 | 1259424.2702
54 | 2659431.2954 | 1259389.3199
55 | 2659457.7346 | 1259430.136
56 | 2659353.2664 | 1259519.127
57 | 2659431.3978 | 1259389.1569
58 | 2659347.1516 | 1259536.0954
59 | 2659371.5946 | 1259542.0145
60 | 2659382.3185 | 1259549.1353
61 | 2659382.5653 | 1259549.2346
62 | 2659383.5982 | 1259546.2905
63 | 2659445.8463 | 1259574.198
64 | 2659454.8226 | 1259577.4775
65 | 2659434.274 | 1259569.9702
66 | 2659475.3035 | 1259585.214
67 | 2659416.3315 | 1259562.8189
68 | 2659403.5113 | 1259557.6632
69 | 2659523.1514 | 1259592.9368
70 | 2659509.3421 | 1259593.0202
71 | 2659391.9771 | 1259553.0224
72 | 2659541.346 | 1259565.2886
73 | 2659491.356 | 1259588.2292
74 | 2659396.6718 | 1259516.6099
75 | 2659396.6705 | 1259516.6127
76 | 2659404.6081 | 1259498.5924
77 | 2659406.0635 | 1259495.2882
78 | 2659405.0864 | 1259555.0393
79 | 2659414.1244 | 1259476.9875
80 | 2659415.8783 | 1259473.0058
81 | 2659453.1631 | 1259573.8308
82 | 2659458.7638 | 1259559.5625
83 | 2659480.4413 | 1259437.3394
84 | 2659485.3431 | 1259439.3568
85 | 2659489.7507 | 1259408.0562
86 | 2659473.6252 | 1259472.7966
87 | 2659497.2215 | 1259443.7217
88 | 2659480.5229 | 1259404.4239
89 | 2659485.2329 | 1259477.3261
90 | 2659464.9914 | 1259543.6972
91 | 2659471.138 | 1259528.0382
92 | 2659475.9828 | 1259515.6957
93 | 2659600.7993 | 1259530.716
94 | 2659606.4867 | 1259534.7471
95 | 2659621.7452 | 1259545.5622
96 | 2659655.6839 | 1259569.6175
97 | 2659519.0354 | 1259538.1507
98 | 2659524.7999 | 1259522.0362
99 | 2659451.4178 | 1259501.4023
100 | 2659467.438 | 1259507.3549
101 | 2659477.7542 | 1259511.188
102 | 2659476.7438 | 1259402.9363
103 | 2659611.4513 | 1259324.5437
104 | 2659610.4587 | 1259326.3098
105 | 2659618.4114 | 1259312.1588
106 | 2659607.3166 | 1259331.9009
107 | 2659611.4844 | 1259309.2738
108 | 2659604.1739 | 1259337.493
109 | 2659584.0866 | 1259297.9581
110 | 2659601.0318 | 1259343.0841
111 | 2659572.385 | 1259293.2327
112 | 2659597.8891 | 1259348.6762
113 | 2659563.4171 | 1259289.6112
114 | 2659573.8606 | 1259382.0705
115 | 2659567.7061 | 1259378.1322
116 | 2659576.5642 | 1259383.8005
117 | 2659565.742 | 1259376.8755
118 | 2659579.5862 | 1259385.7331
119 | 2659584.5759 | 1259371.3554
120 | 2659604.0331 | 1259401.3675
121 | 2659588.047 | 1259365.9635
122 | 2659614.685 | 1259408.1796
123 | 2659591.6088 | 1259359.8514
124 | 2659619.7882 | 1259398.7473
125 | 2659594.7488 | 1259354.2641
126 | 2659566.3044 | 1259277.5152
127 | 2659547.6978 | 1259307.1435
128 | 2659535.0893 | 1259306.554
129 | 2659537.8019 | 1259322.5955
130 | 2659477.2335 | 1259295.3156
131 | 2659457.3621 | 1259289.9902
132 | 2659476.0944 | 1259298.4064
133 | 2659524.1147 | 1259311.3358
134 | 2659536.8348 | 1259324.1057
135 | 2659446.9119 | 1259287.1896
136 | 2659476.245 | 1259313.0826
137 | 2659453.5331 | 1259357.815
138 | 2659443.1813 | 1259371.6127
139 | 2659454.3407 | 1259356.7386
140 | 2659441.7588 | 1259373.5088
141 | 2659455.4217 | 1259355.2978
142 | 2659437.4767 | 1259379.4737
143 | 2659460.4596 | 1259348.5827
144 | 2659436.4698 | 1259381.0776
145 | 2659465.2847 | 1259342.7762
146 | 2659469.92 | 1259336.3172
147 | 2659525.9883 | 1259341.0419
148 | 2659522.6106 | 1259346.3161
149 | 2659519.2324 | 1259351.5909
150 | 2659518.2145 | 1259353.1804
151 | 2659509.4279 | 1259320.2305
152 | 2659476.262 | 1259314.731
153 | 2659471.7062 | 1259332.0034
154 | 2659487.7243 | 1259316.6316
155 | 2659488.7858 | 1259316.8077
156 | 2659493.1481 | 1259317.531
157 | 2659437.2837 | 1259282.9876
158 | 2659498.5747 | 1259318.4308
159 | 2659504.0029 | 1259319.3309
160 | 2659639.78 | 1259437.5368
161 | 2659667.9943 | 1259457.398
162 | 2659625.1077 | 1259388.9151
163 | 2659617.8331 | 1259376.5563
164 | 2659619.6068 | 1259371.8832
165 | 2659619.7361 | 1259371.5424
166 | 2659621.8396 | 1259366.0004
167 | 2659623.9575 | 1259360.4206
168 | 2659626.2827 | 1259354.2945
169 | 2659418.4128 | 1259277.1584
170 | 2659627.4318 | 1259351.2668
171 | 2659540.7202 | 1259459.7059

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1