## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4133-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4133-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4133-1_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4133-1_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4133-1_0_6_node_51 | 0.4 | n |  | TRUE
5 | bus_LV_4133-1_0_6_node_43 | 0.4 | n |  | TRUE
6 | bus_LV_4133-1_0_6_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_4133-1_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_4133-1_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_4133-1_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_4133-1_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_4133-1_0_6_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_4133-1_0_6_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_4133-1_0_6_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_4133-1_0_6_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_4133-1_0_6_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_4133-1_0_6_node_146 | 0.4 | n |  | TRUE
17 | bus_LV_4133-1_0_6_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_4133-1_0_6_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_4133-1_0_6_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_4133-1_0_6_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_4133-1_0_6_node_147 | 0.4 | n |  | TRUE
22 | bus_LV_4133-1_0_6_node_31 | 0.4 | n |  | TRUE
23 | bus_LV_4133-1_0_6_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_4133-1_0_6_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_4133-1_0_6_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_4133-1_0_6_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_4133-1_0_6_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_4133-1_0_6_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_4133-1_0_6_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_4133-1_0_6_node_16 | 0.4 | n |  | TRUE
31 | bus_LV_4133-1_0_6_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_4133-1_0_6_node_17 | 0.4 | n |  | TRUE
33 | bus_LV_4133-1_0_6_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_4133-1_0_6_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_4133-1_0_6_node_98 | 0.4 | n |  | TRUE
36 | bus_LV_4133-1_0_6_node_96 | 0.4 | n |  | TRUE
37 | bus_LV_4133-1_0_6_node_100 | 0.4 | n |  | TRUE
38 | bus_LV_4133-1_0_6_node_101 | 0.4 | n |  | TRUE
39 | bus_LV_4133-1_0_6_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_4133-1_0_6_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_4133-1_0_6_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_4133-1_0_6_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_4133-1_0_6_node_61 | 0.4 | n |  | TRUE
44 | bus_LV_4133-1_0_6_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_4133-1_0_6_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_4133-1_0_6_node_53 | 0.4 | n |  | TRUE
47 | bus_LV_4133-1_0_6_node_55 | 0.4 | n |  | TRUE
48 | bus_LV_4133-1_0_6_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_4133-1_0_6_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_4133-1_0_6_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_4133-1_0_6_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_4133-1_0_6_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_4133-1_0_6_node_74 | 0.4 | n |  | TRUE
54 | bus_LV_4133-1_0_6_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_4133-1_0_6_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_4133-1_0_6_node_130 | 0.4 | n |  | TRUE
57 | bus_LV_4133-1_0_6_node_89 | 0.4 | n |  | TRUE
58 | bus_LV_4133-1_0_6_node_136 | 0.4 | n |  | TRUE
59 | bus_LV_4133-1_0_6_node_93 | 0.4 | n |  | TRUE
60 | bus_LV_4133-1_0_6_node_128 | 0.4 | n |  | TRUE
61 | bus_LV_4133-1_0_6_node_88 | 0.4 | n |  | TRUE
62 | bus_LV_4133-1_0_6_node_91 | 0.4 | n |  | TRUE
63 | bus_LV_4133-1_0_6_node_157 | 0.4 | n |  | TRUE
64 | bus_LV_4133-1_0_6_node_36 | 0.4 | n |  | TRUE
65 | bus_LV_4133-1_0_6_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_4133-1_0_6_node_38 | 0.4 | n |  | TRUE
67 | bus_LV_4133-1_0_6_node_39 | 0.4 | n |  | TRUE
68 | bus_LV_4133-1_0_6_node_40 | 0.4 | n |  | TRUE
69 | bus_LV_4133-1_0_6_node_77 | 0.4 | n |  | TRUE
70 | bus_LV_4133-1_0_6_node_71 | 0.4 | n |  | TRUE
71 | bus_LV_4133-1_0_6_node_148 | 0.4 | n |  | TRUE
72 | bus_LV_4133-1_0_6_node_47 | 0.4 | n |  | TRUE
73 | bus_LV_4133-1_0_6_node_132 | 0.4 | n |  | TRUE
74 | bus_LV_4133-1_0_6_node_69 | 0.4 | n |  | TRUE
75 | bus_LV_4133-1_0_6_node_151 | 0.4 | n |  | TRUE
76 | bus_LV_4133-1_0_6_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_4133-1_0_6_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_4133-1_0_6_node_57 | 0.4 | n |  | TRUE
79 | bus_LV_4133-1_0_6_node_48 | 0.4 | n |  | TRUE
80 | bus_LV_4133-1_0_6_node_67 | 0.4 | n |  | TRUE
81 | bus_LV_4133-1_0_6_node_66 | 0.4 | n |  | TRUE
82 | bus_LV_4133-1_0_6_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_4133-1_0_6_node_58 | 0.4 | n |  | TRUE
84 | bus_LV_4133-1_0_6_node_60 | 0.4 | n |  | TRUE
85 | bus_LV_4133-1_0_6_node_63 | 0.4 | n |  | TRUE
86 | bus_LV_4133-1_0_6_node_75 | 0.4 | n |  | TRUE
87 | bus_LV_4133-1_0_6_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_4133-1_0_6_node_64 | 0.4 | n |  | TRUE
89 | bus_LV_4133-1_0_6_node_65 | 0.4 | n |  | TRUE
90 | bus_LV_4133-1_0_6_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_4133-1_0_6_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_4133-1_0_6_node_149 | 0.4 | n |  | TRUE
93 | bus_LV_4133-1_0_6_node_150 | 0.4 | n |  | TRUE
94 | bus_LV_4133-1_0_6_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_4133-1_0_6_node_72 | 0.4 | n |  | TRUE
96 | bus_LV_4133-1_0_6_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_4133-1_0_6_node_133 | 0.4 | n |  | TRUE
98 | bus_LV_4133-1_0_6_node_106 | 0.4 | n |  | TRUE
99 | bus_LV_4133-1_0_6_node_80 | 0.4 | n |  | TRUE
100 | bus_LV_4133-1_0_6_node_81 | 0.4 | n |  | TRUE
101 | bus_LV_4133-1_0_6_node_82 | 0.4 | n |  | TRUE
102 | bus_LV_4133-1_0_6_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_4133-1_0_6_node_84 | 0.4 | n |  | TRUE
104 | bus_LV_4133-1_0_6_node_116 | 0.4 | n |  | TRUE
105 | bus_LV_4133-1_0_6_node_87 | 0.4 | n |  | TRUE
106 | bus_LV_4133-1_0_6_node_114 | 0.4 | n |  | TRUE
107 | bus_LV_4133-1_0_6_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_4133-1_0_6_node_86 | 0.4 | n |  | TRUE
109 | bus_LV_4133-1_0_6_node_90 | 0.4 | n |  | TRUE
110 | bus_LV_4133-1_0_6_node_155 | 0.4 | n |  | TRUE
111 | bus_LV_4133-1_0_6_node_156 | 0.4 | n |  | TRUE
112 | bus_LV_4133-1_0_6_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_4133-1_0_6_node_94 | 0.4 | n |  | TRUE
114 | bus_LV_4133-1_0_6_node_120 | 0.4 | n |  | TRUE
115 | bus_LV_4133-1_0_6_node_121 | 0.4 | n |  | TRUE
116 | bus_LV_4133-1_0_6_node_122 | 0.4 | n |  | TRUE
117 | bus_LV_4133-1_0_6_node_95 | 0.4 | n |  | TRUE
118 | bus_LV_4133-1_0_6_node_97 | 0.4 | n |  | TRUE
119 | bus_LV_4133-1_0_6_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_4133-1_0_6_node_160 | 0.4 | n |  | TRUE
121 | bus_LV_4133-1_0_6_node_102 | 0.4 | n |  | TRUE
122 | bus_LV_4133-1_0_6_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_4133-1_0_6_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_4133-1_0_6_node_103 | 0.4 | n |  | TRUE
125 | bus_LV_4133-1_0_6_node_104 | 0.4 | n |  | TRUE
126 | bus_LV_4133-1_0_6_node_105 | 0.4 | n |  | TRUE
127 | bus_LV_4133-1_0_6_node_107 | 0.4 | n |  | TRUE
128 | bus_LV_4133-1_0_6_node_153 | 0.4 | n |  | TRUE
129 | bus_LV_4133-1_0_6_node_152 | 0.4 | n |  | TRUE
130 | bus_LV_4133-1_0_6_node_159 | 0.4 | n |  | TRUE
131 | bus_LV_4133-1_0_6_node_141 | 0.4 | n |  | TRUE
132 | bus_LV_4133-1_0_6_node_108 | 0.4 | n |  | TRUE
133 | bus_LV_4133-1_0_6_node_109 | 0.4 | n |  | TRUE
134 | bus_LV_4133-1_0_6_node_110 | 0.4 | n |  | TRUE
135 | bus_LV_4133-1_0_6_node_111 | 0.4 | n |  | TRUE
136 | bus_LV_4133-1_0_6_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_4133-1_0_6_node_113 | 0.4 | n |  | TRUE
138 | bus_LV_4133-1_0_6_node_125 | 0.4 | n |  | TRUE
139 | bus_LV_4133-1_0_6_node_140 | 0.4 | n |  | TRUE
140 | bus_LV_4133-1_0_6_node_126 | 0.4 | n |  | TRUE
141 | bus_LV_4133-1_0_6_node_138 | 0.4 | n |  | TRUE
142 | bus_LV_4133-1_0_6_node_115 | 0.4 | n |  | TRUE
143 | bus_LV_4133-1_0_6_node_135 | 0.4 | n |  | TRUE
144 | bus_LV_4133-1_0_6_node_123 | 0.4 | n |  | TRUE
145 | bus_LV_4133-1_0_6_node_124 | 0.4 | n |  | TRUE
146 | bus_LV_4133-1_0_6_node_134 | 0.4 | n |  | TRUE
147 | bus_LV_4133-1_0_6_node_161 | 0.4 | n |  | TRUE
148 | bus_LV_4133-1_0_6_node_154 | 0.4 | n |  | TRUE
149 | bus_LV_4133-1_0_6_node_139 | 0.4 | n |  | TRUE
150 | bus_LV_4133-1_0_6_node_162 | 0.4 | n |  | TRUE
151 | bus_LV_4133-1_0_6_node_145 | 0.4 | n |  | TRUE
152 | bus_LV_4133-1_0_6_node_142 | 0.4 | n |  | TRUE
153 | bus_LV_4133-1_0_6_node_143 | 0.4 | n |  | TRUE
154 | bus_LV_4133-1_0_6_node_127 | 0.4 | n |  | TRUE
155 | bus_LV_4133-1_0_6_node_129 | 0.4 | n |  | TRUE
156 | bus_LV_4133-1_0_6_node_131 | 0.4 | n |  | TRUE
157 | bus_LV_4133-1_0_6_node_137 | 0.4 | n |  | TRUE
158 | bus_LV_4133-1_0_6_node_144 | 0.4 | n |  | TRUE
159 | bus_LV_4133-1_0_6_node_163 | 0.4 | n |  | TRUE
160 | bus_LV_4133-1_0_6_node_164 | 0.4 | n |  | TRUE
161 | bus_LV_4133-1_0_6_node_165 | 0.4 | n |  | TRUE
162 | bus_LV_4133-1_0_6_node_166 | 0.4 | n |  | TRUE
163 | bus_LV_4133-1_0_6_node_169 | 0.4 | n |  | TRUE
164 | bus_LV_4133-1_0_6_node_168 | 0.4 | n |  | TRUE
165 | bus_LV_4133-1_0_6_node_167 | 0.4 | n |  | TRUE
166 | bus_MV_473_1_node_89 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4133-1_0_6_load_0 | 0 | 0.0038297 | 0.00095982 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4133-1_0_6_load_1 | 1 | 0.0019123 | 0.00047927 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4133-1_0_6_load_2 | 2 | 0.0049805 | 0.0012482 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4133-1_0_6_load_3 | 3 | 0.00074083 | 0.00018567 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4133-1_0_6_load_51 | 4 | 0.001366 | 0.00034236 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4133-1_0_6_load_43 | 5 | 0.0029584 | 0.00074145 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4133-1_0_6_load_4 | 6 | 0.0033488 | 0.00083929 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4133-1_0_6_load_7 | 9 | 0.0033951 | 0.00085088 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4133-1_0_6_load_8 | 10 | 0.0021319 | 0.0005343 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4133-1_0_6_load_9 | 11 | 0.0019985 | 0.00050086 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4133-1_0_6_load_10 | 12 | 0.00064589 | 0.00016187 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4133-1_0_6_load_11 | 13 | 0.0030484 | 0.00076399 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4133-1_0_6_load_19 | 14 | 0.0015921 | 0.00039903 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4133-1_0_6_load_21 | 15 | 0.0023792 | 0.0005963 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4133-1_0_6_load_146 | 16 | 0.0026078 | 0.00065357 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4133-1_0_6_load_34 | 18 | 0.0029459 | 0.0007383 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4133-1_0_6_load_20 | 19 | 0.0022217 | 0.0005568 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4133-1_0_6_load_22 | 20 | 0.0035501 | 0.00088975 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4133-1_0_6_load_147 | 21 | 0.0076342 | 0.0019133 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4133-1_0_6_load_32 | 23 | 0.00072706 | 0.00018222 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4133-1_0_6_load_33 | 24 | 0.0014988 | 0.00037563 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4133-1_0_6_load_35 | 25 | 0.00060816 | 0.00015242 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4133-1_0_6_load_12 | 26 | 0.0020918 | 0.00052425 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4133-1_0_6_load_13 | 27 | 0.0019518 | 0.00048918 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4133-1_0_6_load_14 | 28 | 0.0027025 | 0.0006773 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4133-1_0_6_load_15 | 29 | 0.0012281 | 0.00030778 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4133-1_0_6_load_16 | 30 | 0.0017192 | 0.00043088 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4133-1_0_6_load_23 | 31 | 0.0020956 | 0.00052522 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4133-1_0_6_load_24 | 33 | 0.0020109 | 0.00050398 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4133-1_0_6_load_98 | 35 | 0.00069453 | 0.00017407 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4133-1_0_6_load_96 | 36 | 0.00067771 | 0.00016985 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4133-1_0_6_load_100 | 37 | 0.0031758 | 0.00079593 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4133-1_0_6_load_101 | 38 | 0.0037679 | 0.00094433 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4133-1_0_6_load_25 | 39 | 0.0018434 | 0.00046201 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4133-1_0_6_load_26 | 40 | 0.001519 | 0.00038069 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4133-1_0_6_load_27 | 42 | 0.00084763 | 0.00021244 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4133-1_0_6_load_61 | 43 | 0.0021541 | 0.00053986 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4133-1_0_6_load_54 | 44 | 0.0018401 | 0.00046118 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4133-1_0_6_load_49 | 45 | 0.0011066 | 0.00027735 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4133-1_0_6_load_53 | 46 | 0.0028048 | 0.00070294 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4133-1_0_6_load_55 | 47 | 0.002751 | 0.00068947 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4133-1_0_6_load_52 | 48 | 0.0016911 | 0.00042382 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4133-1_0_6_load_44 | 50 | 0.00086361 | 0.00021644 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4133-1_0_6_load_45 | 51 | 0.0025599 | 0.00064157 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4133-1_0_6_load_41 | 52 | 0.0024201 | 0.00060653 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4133-1_0_6_load_74 | 53 | 0.0023779 | 0.00059597 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4133-1_0_6_load_42 | 55 | 0.0020753 | 0.00052012 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4133-1_0_6_load_130 | 56 | 0.0066557 | 0.0016681 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4133-1_0_6_load_89 | 57 | 0.001163 | 0.00029147 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4133-1_0_6_load_136 | 58 | 0.0044644 | 0.0011189 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4133-1_0_6_load_93 | 59 | 0.004648 | 0.0011649 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4133-1_0_6_load_128 | 60 | 0.006655 | 0.0016679 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4133-1_0_6_load_91 | 62 | 0.0019392 | 0.00048602 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4133-1_0_6_load_157 | 63 | 0.0045575 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4133-1_0_6_load_36 | 64 | 0.0012467 | 0.00031245 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4133-1_0_6_load_37 | 65 | 0.0014187 | 0.00035557 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4133-1_0_6_load_38 | 66 | 0.00118 | 0.00029575 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4133-1_0_6_load_77 | 69 | 0.0029065 | 0.00072843 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4133-1_0_6_load_148 | 71 | 0.0010555 | 0.00026454 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4133-1_0_6_load_47 | 72 | 0.00082999 | 0.00020801 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4133-1_0_6_load_132 | 73 | 0.00080663 | 0.00020216 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4133-1_0_6_load_69 | 74 | 0.0057728 | 0.0014468 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4133-1_0_6_load_151 | 75 | 0.00095113 | 0.00023838 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4133-1_0_6_load_46 | 76 | 0.0010936 | 0.00027408 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4133-1_0_6_load_73 | 77 | 0.0031291 | 0.00078423 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4133-1_0_6_load_57 | 78 | 0.002654 | 0.00066515 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4133-1_0_6_load_48 | 79 | 0.001624 | 0.00040702 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4133-1_0_6_load_67 | 80 | 0.0010669 | 0.00026738 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4133-1_0_6_load_66 | 81 | 0.0014418 | 0.00036135 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4133-1_0_6_load_56 | 82 | 0.0017194 | 0.00043093 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4133-1_0_6_load_58 | 83 | 0.0021638 | 0.0005423 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4133-1_0_6_load_60 | 84 | 0.0030943 | 0.0007755 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4133-1_0_6_load_63 | 85 | 0.0017059 | 0.00042753 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4133-1_0_6_load_75 | 86 | 0.0020555 | 0.00051515 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4133-1_0_6_load_62 | 87 | 0.0021897 | 0.0005488 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4133-1_0_6_load_64 | 88 | 0.0017731 | 0.00044437 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4133-1_0_6_load_78 | 90 | 0.00098439 | 0.00024671 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4133-1_0_6_load_79 | 91 | 0.0020816 | 0.00052169 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4133-1_0_6_load_149 | 92 | 0.0017079 | 0.00042803 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4133-1_0_6_load_150 | 93 | 0.0020078 | 0.00050321 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4133-1_0_6_load_70 | 94 | 0.0021605 | 0.00054146 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4133-1_0_6_load_72 | 95 | 0.0029807 | 0.00074705 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4133-1_0_6_load_76 | 96 | 0.0010236 | 0.00025653 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4133-1_0_6_load_133 | 97 | 0.001784 | 0.00044711 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4133-1_0_6_load_106 | 98 | 0.0018698 | 0.00046862 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4133-1_0_6_load_80 | 99 | 0.0035214 | 0.00088254 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4133-1_0_6_load_81 | 100 | 0.0016338 | 0.00040947 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4133-1_0_6_load_84 | 103 | 0.0033199 | 0.00083204 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4133-1_0_6_load_116 | 104 | 0.0048466 | 0.0012147 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4133-1_0_6_load_87 | 105 | 0.0014162 | 0.00035493 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4133-1_0_6_load_114 | 106 | 0.0027323 | 0.00068479 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4133-1_0_6_load_85 | 107 | 0.010544 | 0.0026426 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4133-1_0_6_load_86 | 108 | 0.0088053 | 0.0022068 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4133-1_0_6_load_90 | 109 | 0.0034388 | 0.00086184 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4133-1_0_6_load_155 | 110 | 0.0060549 | 0.0015175 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4133-1_0_6_load_156 | 111 | 0.0023764 | 0.00059559 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4133-1_0_6_load_92 | 112 | 0.0055741 | 0.001397 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4133-1_0_6_load_94 | 113 | 0.00077964 | 0.0001954 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4133-1_0_6_load_121 | 115 | 0.00090407 | 0.00022658 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4133-1_0_6_load_95 | 117 | 0.0022546 | 0.00056506 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4133-1_0_6_load_99 | 119 | 0.0009722 | 0.00024366 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4133-1_0_6_load_160 | 120 | 0.020272 | 0.0050808 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4133-1_0_6_load_102 | 121 | 0.00054532 | 0.00013667 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4133-1_0_6_load_118 | 122 | 0.0016197 | 0.00040594 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4133-1_0_6_load_103 | 124 | 0.00096649 | 0.00024223 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4133-1_0_6_load_104 | 125 | 0.0015998 | 0.00040094 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4133-1_0_6_load_105 | 126 | 0.0018115 | 0.00045401 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4133-1_0_6_load_153 | 128 | 0.00082039 | 0.00020561 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4133-1_0_6_load_152 | 129 | 0.0025159 | 0.00063053 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4133-1_0_6_load_159 | 130 | 0.0028369 | 0.000711 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4133-1_0_6_load_141 | 131 | 0.0014952 | 0.00037474 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4133-1_0_6_load_108 | 132 | 0.0038882 | 0.00097447 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4133-1_0_6_load_109 | 133 | 0.00069481 | 0.00017414 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4133-1_0_6_load_111 | 135 | 0.00071538 | 0.00017929 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4133-1_0_6_load_112 | 136 | 0.0023284 | 0.00058355 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4133-1_0_6_load_113 | 137 | 0.0024621 | 0.00061706 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4133-1_0_6_load_125 | 138 | 0.0037184 | 0.00093191 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4133-1_0_6_load_140 | 139 | 0.0014871 | 0.00037269 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4133-1_0_6_load_115 | 142 | 0.0031894 | 0.00079934 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4133-1_0_6_load_135 | 143 | 0.010302 | 0.0025819 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4133-1_0_6_load_123 | 144 | 0.00095286 | 0.00023881 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4133-1_0_6_load_124 | 145 | 0.0016743 | 0.00041961 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4133-1_0_6_load_134 | 146 | 0.0013361 | 0.00033486 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4133-1_0_6_load_161 | 147 | 0.00098362 | 0.00024652 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4133-1_0_6_load_139 | 149 | 0.00070501 | 0.00017669 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4133-1_0_6_load_162 | 150 | 0.0017267 | 0.00043275 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4133-1_0_6_load_145 | 151 | 0.0030891 | 0.0007742 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4133-1_0_6_load_142 | 152 | 0.0036916 | 0.00092521 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4133-1_0_6_load_143 | 153 | 0.0043855 | 0.0010991 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4133-1_0_6_load_127 | 154 | 0.0066674 | 0.001671 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4133-1_0_6_load_131 | 156 | 0.0037097 | 0.00092973 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4133-1_0_6_load_137 | 157 | 0.00063155 | 0.00015828 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4133-1_0_6_load_144 | 158 | 0.0013964 | 0.00034996 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4133-1_0_6_load_163 | 159 | 0.0010629 | 0.00026639 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4133-1_0_6_load_164 | 160 | 0.0020881 | 0.00052332 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4133-1_0_6_load_165 | 161 | 0.0013067 | 0.00032749 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4133-1_0_6_load_166 | 162 | 0.0022528 | 0.0005646 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4133-1_0_6_load_169 | 163 | 0.0013067 | 0.00032749 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4133-1_0_6_load_168 | 164 | 0.0023202 | 0.00058151 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4133-1_0_6_load_167 | 165 | 0.0013067 | 0.0003275 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4133-1_0_6_line_0 |  | 0 | 1 | 0.018739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4133-1_0_6_line_1 |  | 0 | 2 | 0.049703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4133-1_0_6_line_2 |  | 2 | 3 | 0.032828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4133-1_0_6_line_3 |  | 3 | 4 | 0.05122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4133-1_0_6_line_4 |  | 4 | 5 | 0.034934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4133-1_0_6_line_5 |  | 5 | 55 | 0.025508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4133-1_0_6_line_6 |  | 6 | 7 | 0.040465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4133-1_0_6_line_7 |  | 7 | 12 | 0.029738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4133-1_0_6_line_8 |  | 7 | 13 | 0.01024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4133-1_0_6_line_9 |  | 8 | 9 | 0.017066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4133-1_0_6_line_10 |  | 8 | 10 | 0.017271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_4133-1_0_6_line_11 |  | 8 | 11 | 0.019506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4133-1_0_6_line_12 |  | 9 | 14 | 0.0086842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4133-1_0_6_line_13 |  | 10 | 15 | 0.023879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_4133-1_0_6_line_14 |  | 11 | 16 | 0.0020437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4133-1_0_6_line_15 |  | 12 | 17 | 0.029698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4133-1_0_6_line_16 |  | 13 | 18 | 0.01782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4133-1_0_6_line_17 |  | 14 | 19 | 0.0021533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4133-1_0_6_line_18 |  | 15 | 20 | 0.014678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_4133-1_0_6_line_19 |  | 16 | 21 | 0.010976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4133-1_0_6_line_20 |  | 17 | 22 | 0.030086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4133-1_0_6_line_21 |  | 17 | 23 | 0.014317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4133-1_0_6_line_22 |  | 17 | 24 | 0.031123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4133-1_0_6_line_23 |  | 18 | 25 | 0.024335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4133-1_0_6_line_24 |  | 19 | 33 | 0.019725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4133-1_0_6_line_25 |  | 20 | 37 | 0.051581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_4133-1_0_6_line_26 |  | 21 | 156 | 0.0027368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4133-1_0_6_line_27 |  | 22 | 56 | 0.014399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4133-1_0_6_line_28 |  | 22 | 57 | 0.050583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4133-1_0_6_line_29 |  | 23 | 58 | 0.051899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4133-1_0_6_line_30 |  | 24 | 59 | 0.026446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4133-1_0_6_line_31 |  | 25 | 63 | 0.024146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4133-1_0_6_line_32 |  | 26 | 27 | 0.018492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4133-1_0_6_line_33 |  | 26 | 28 | 0.0066825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4133-1_0_6_line_34 |  | 27 | 29 | 0.0053492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4133-1_0_6_line_35 |  | 28 | 30 | 0.0068519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4133-1_0_6_line_36 |  | 29 | 31 | 0.0024472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4133-1_0_6_line_37 |  | 30 | 32 | 0.041945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4133-1_0_6_line_38 |  | 31 | 33 | 0.00033411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4133-1_0_6_line_39 |  | 32 | 34 | 0.00921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4133-1_0_6_line_40 |  | 34 | 35 | 0.0090086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4133-1_0_6_line_41 |  | 35 | 36 | 0.022893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4133-1_0_6_line_42 |  | 36 | 117 | 0.017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4133-1_0_6_line_43 |  | 37 | 38 | 0.0060431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_4133-1_0_6_line_44 |  | 38 | 121 | 0.032718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_4133-1_0_6_line_45 |  | 39 | 40 | 0.0056178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4133-1_0_6_line_46 |  | 39 | 41 | 0.04492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4133-1_0_6_line_47 |  | 40 | 42 | 0.043604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4133-1_0_6_line_48 |  | 41 | 43 | 0.018649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4133-1_0_6_line_49 |  | 41 | 44 | 0.018486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4133-1_0_6_line_50 |  | 41 | 45 | 0.015767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4133-1_0_6_line_51 |  | 43 | 53 | 0.0034172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4133-1_0_6_line_52 |  | 44 | 48 | 0.016962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4133-1_0_6_line_53 |  | 45 | 79 | 0.0026145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4133-1_0_6_line_54 |  | 46 | 47 | 0.018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4133-1_0_6_line_55 |  | 46 | 48 | 0.0077944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4133-1_0_6_line_56 |  | 47 | 80 | 0.0046498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4133-1_0_6_line_57 |  | 49 | 50 | 0.01203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4133-1_0_6_line_58 |  | 49 | 51 | 0.031443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4133-1_0_6_line_59 |  | 49 | 52 | 0.017592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4133-1_0_6_line_60 |  | 50 | 53 | 0.040096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4133-1_0_6_line_61 |  | 51 | 54 | 0.013988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4133-1_0_6_line_62 |  | 52 | 55 | 0.010608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4133-1_0_6_line_63 |  | 54 | 77 | 0.035419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4133-1_0_6_line_64 |  | 54 | 78 | 0.010864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4133-1_0_6_line_65 |  | 56 | 60 | 0.001013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4133-1_0_6_line_66 |  | 57 | 61 | 0.00078602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4133-1_0_6_line_67 |  | 59 | 62 | 0.015526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4133-1_0_6_line_68 |  | 60 | 154 | 0.034655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4133-1_0_6_line_69 |  | 61 | 109 | 0.015323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4133-1_0_6_line_70 |  | 61 | 108 | 0.021236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4133-1_0_6_line_71 |  | 62 | 112 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4133-1_0_6_line_72 |  | 64 | 65 | 0.010179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_4133-1_0_6_line_73 |  | 64 | 66 | 0.011229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_4133-1_0_6_line_74 |  | 65 | 67 | 0.026905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_4133-1_0_6_line_75 |  | 66 | 68 | 0.0094938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_4133-1_0_6_line_76 |  | 67 | 69 | 0.048567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_4133-1_0_6_line_77 |  | 67 | 70 | 0.022063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4133-1_0_6_line_78 |  | 68 | 71 | 0.0019122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_4133-1_0_6_line_79 |  | 68 | 72 | 0.020581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4133-1_0_6_line_80 |  | 69 | 73 | 0.0050416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_4133-1_0_6_line_81 |  | 70 | 74 | 0.044803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4133-1_0_6_line_82 |  | 71 | 75 | 0.022179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_4133-1_0_6_line_83 |  | 72 | 76 | 0.045848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4133-1_0_6_line_84 |  | 73 | 97 | 0.02336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_4133-1_0_6_line_85 |  | 74 | 94 | 0.021473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4133-1_0_6_line_86 |  | 75 | 93 | 0.0035711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_4133-1_0_6_line_87 |  | 77 | 86 | 0.032849 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4133-1_0_6_line_88 |  | 78 | 82 | 0.0032512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4133-1_0_6_line_89 |  | 80 | 81 | 0.017009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4133-1_0_6_line_90 |  | 82 | 83 | 0.021799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4133-1_0_6_line_91 |  | 83 | 84 | 0.0049922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4133-1_0_6_line_92 |  | 84 | 85 | 0.031885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4133-1_0_6_line_93 |  | 85 | 87 | 0.025423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4133-1_0_6_line_94 |  | 86 | 96 | 0.031659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4133-1_0_6_line_95 |  | 87 | 88 | 0.0014034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4133-1_0_6_line_96 |  | 88 | 89 | 0.021459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4133-1_0_6_line_97 |  | 89 | 90 | 0.0068057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_4133-1_0_6_line_98 |  | 89 | 91 | 0.011329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_4133-1_0_6_line_99 |  | 90 | 92 | 0.0048057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
100 | LV_4133-1_0_6_line_100 |  | 91 | 93 | 0.0031393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
101 | LV_4133-1_0_6_line_101 |  | 92 | 98 | 0.027582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
102 | LV_4133-1_0_6_line_102 |  | 94 | 95 | 0.018537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4133-1_0_6_line_103 |  | 97 | 146 | 0.0033725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_4133-1_0_6_line_104 |  | 98 | 125 | 0.0063394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4133-1_0_6_line_105 |  | 99 | 100 | 0.024195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4133-1_0_6_line_106 |  | 99 | 101 | 0.018582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4133-1_0_6_line_107 |  | 100 | 102 | 0.016291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4133-1_0_6_line_108 |  | 101 | 103 | 0.010712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4133-1_0_6_line_109 |  | 102 | 104 | 0.018257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4133-1_0_6_line_110 |  | 103 | 105 | 0.017331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4133-1_0_6_line_111 |  | 104 | 106 | 0.033066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4133-1_0_6_line_112 |  | 105 | 107 | 0.0054212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4133-1_0_6_line_113 |  | 106 | 142 | 0.016241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4133-1_0_6_line_114 |  | 107 | 108 | 0.011237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4133-1_0_6_line_115 |  | 109 | 110 | 0.0048769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4133-1_0_6_line_116 |  | 110 | 111 | 0.027062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4133-1_0_6_line_117 |  | 112 | 113 | 0.0013758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4133-1_0_6_line_118 |  | 114 | 115 | 0.024499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4133-1_0_6_line_119 |  | 114 | 116 | 0.015929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4133-1_0_6_line_120 |  | 115 | 148 | 0.030983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4133-1_0_6_line_121 |  | 116 | 143 | 0.015506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4133-1_0_6_line_122 |  | 117 | 118 | 0.0055582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4133-1_0_6_line_123 |  | 118 | 119 | 0.030884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4133-1_0_6_line_124 |  | 119 | 120 | 0.028232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4133-1_0_6_line_125 |  | 121 | 122 | 0.001689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
126 | LV_4133-1_0_6_line_126 |  | 122 | 123 | 0.017484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
127 | LV_4133-1_0_6_line_127 |  | 123 | 144 | 0.021196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
128 | LV_4133-1_0_6_line_128 |  | 123 | 145 | 0.016967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4133-1_0_6_line_129 |  | 124 | 125 | 0.026873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4133-1_0_6_line_130 |  | 124 | 126 | 0.0070669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4133-1_0_6_line_131 |  | 126 | 127 | 0.0027381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4133-1_0_6_line_132 |  | 127 | 128 | 0.026776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4133-1_0_6_line_133 |  | 128 | 129 | 0.017166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4133-1_0_6_line_134 |  | 129 | 158 | 0.035963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4133-1_0_6_line_135 |  | 130 | 131 | 0.0092255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4133-1_0_6_line_136 |  | 131 | 135 | 0.047955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4133-1_0_6_line_137 |  | 132 | 133 | 0.011374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4133-1_0_6_line_138 |  | 132 | 134 | 0.011795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4133-1_0_6_line_139 |  | 133 | 135 | 0.0059995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4133-1_0_6_line_140 |  | 134 | 136 | 0.019263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4133-1_0_6_line_141 |  | 134 | 137 | 0.015782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4133-1_0_6_line_142 |  | 136 | 138 | 0.049158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4133-1_0_6_line_143 |  | 137 | 139 | 0.018626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4133-1_0_6_line_144 |  | 138 | 140 | 0.012166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4133-1_0_6_line_145 |  | 139 | 141 | 0.02438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4133-1_0_6_line_146 |  | 140 | 151 | 0.017274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4133-1_0_6_line_147 |  | 140 | 152 | 0.019511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4133-1_0_6_line_148 |  | 141 | 149 | 0.048467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4133-1_0_6_line_149 |  | 141 | 157 | 0.03793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4133-1_0_6_line_150 |  | 144 | 146 | 0.010105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
151 | LV_4133-1_0_6_line_151 |  | 145 | 147 | 0.0017885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4133-1_0_6_line_152 |  | 147 | 150 | 0.018946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4133-1_0_6_line_153 |  | 148 | 149 | 0.027665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4133-1_0_6_line_154 |  | 150 | 159 | 0.0029432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4133-1_0_6_line_155 |  | 152 | 153 | 0.035991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4133-1_0_6_line_156 |  | 153 | 158 | 0.027907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4133-1_0_6_line_157 |  | 154 | 155 | 0.026682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4133-1_0_6_line_158 |  | 155 | 156 | 0.025332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4133-1_0_6_line_159 |  | 159 | 160 | 0.018002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4133-1_0_6_line_160 |  | 160 | 161 | 0.0039699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4133-1_0_6_line_161 |  | 161 | 162 | 0.017234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4133-1_0_6_line_162 |  | 162 | 163 | 0.0051629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4133-1_0_6_line_163 |  | 163 | 164 | 0.016106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4133-1_0_6_line_164 |  | 164 | 165 | 0.0055343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4133-1_0_6_trafo_22 | 0.63 MVA 20/0.4 kV | 166 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2655882.5194 | 1232354.7565 | 2655874.1248 | 1232365.0659 | 2655870.2794 | 1232368.9194
1 | 2655882.5194 | 1232354.7565 | 2655883.8459 | 1232353.1273 | 2655896.4691 | 1232338.5699 | 2655911.8857 | 1232314.7975
2 | 2655911.8857 | 1232314.7975 | 2655918.5207 | 1232304.5664 | 2655929.0976 | 1232286.8501
3 | 2655955.2862 | 1232242.835 | 2655954.818 | 1232243.7686 | 2655929.0976 | 1232286.8501
4 | 2655955.2862 | 1232242.835 | 2655970.9464 | 1232211.6079
5 | 2655970.9464 | 1232211.6079 | 2655971.8495 | 1232209.807 | 2655981.902 | 1232188.5735
6 | 2656323.7776 | 1232179.9322 | 2656323.855 | 1232172.5615 | 2656325.352 | 1232164.8151 | 2656334.8894 | 1232141.485
7 | 2656323.7776 | 1232179.9322 | 2656324.5617 | 1232187.4889 | 2656326.4616 | 1232196.3571 | 2656332.7569 | 1232207.2459 | 2656333.0868 | 1232207.6132
8 | 2656323.7776 | 1232179.9322 | 2656319.2373 | 1232178.0102 | 2656315.0188 | 1232178.893 | 2656314.3592 | 1232179.6437
9 | 2656343.087 | 1232092.0362 | 2656341.1062 | 1232075.0852
10 | 2656343.087 | 1232092.0362 | 2656326.649 | 1232097.3358
11 | 2656343.087 | 1232092.0362 | 2656348.8627 | 1232093.0471 | 2656356.0157 | 1232095.75 | 2656360.9936 | 1232099.0919
12 | 2656341.1062 | 1232075.0852 | 2656340.0983 | 1232066.4598
13 | 2656303.6785 | 1232103.7811 | 2656314.2088 | 1232101.3465 | 2656326.649 | 1232097.3358
14 | 2656362.4956 | 1232100.4704 | 2656361.2903 | 1232099.2911 | 2656360.9936 | 1232099.0919
15 | 2656353.9831 | 1232228.6719 | 2656342.2057 | 1232217.7644 | 2656333.0868 | 1232207.6132
16 | 2656314.3592 | 1232179.6437 | 2656309.7294 | 1232184.9135 | 2656305.0831 | 1232194.6691
17 | 2656339.8483 | 1232064.321 | 2656340.0983 | 1232066.4598
18 | 2656289.3778 | 1232107.0874 | 2656303.6785 | 1232103.7811
19 | 2656362.4956 | 1232100.4704 | 2656366.5572 | 1232104.4444 | 2656369.7315 | 1232108.6804
20 | 2656363.0084 | 1232199.9945 | 2656358.9991 | 1232210.7634 | 2656353.9831 | 1232228.6719
21 | 2656353.9831 | 1232228.6719 | 2656364.369 | 1232238.5269
22 | 2656353.9831 | 1232228.6719 | 2656347.3799 | 1232259.0866
23 | 2656305.0831 | 1232194.6691 | 2656304.0045 | 1232196.9337 | 2656294.2727 | 1232208.2822 | 2656290.5872 | 1232214.0877
24 | 2656339.8483 | 1232064.321 | 2656339.5219 | 1232061.5272 | 2656339.1671 | 1232051.8176 | 2656339.1297 | 1232044.6219
25 | 2656289.3778 | 1232107.0874 | 2656289.3549 | 1232107.0927 | 2656274.4516 | 1232105.5952 | 2656239.3454 | 1232095.3203
26 | 2656371.3726 | 1232110.8705 | 2656369.7315 | 1232108.6804
27 | 2656363.0084 | 1232199.9945 | 2656368.0332 | 1232186.5007
28 | 2656363.0084 | 1232199.9945 | 2656407.6323 | 1232223.814
29 | 2656402.0196 | 1232274.2474 | 2656374.5533 | 1232248.1905 | 2656364.369 | 1232238.5269
30 | 2656347.3799 | 1232259.0866 | 2656341.769 | 1232284.9309
31 | 2656280.9781 | 1232236.041 | 2656285.5097 | 1232222.086 | 2656290.5872 | 1232214.0877
32 | 2656343.2678 | 1232018.3883 | 2656339.8439 | 1232036.5601
33 | 2656344.5052 | 1232011.8213 | 2656343.2678 | 1232018.3883
34 | 2656339.1153 | 1232041.8406 | 2656339.1081 | 1232040.4653 | 2656339.8439 | 1232036.5601
35 | 2656344.5052 | 1232011.8213 | 2656344.9926 | 1232009.2343 | 2656346.0929 | 1232005.1609
36 | 2656339.1153 | 1232041.8406 | 2656339.128 | 1232044.2878
37 | 2656355.8223 | 1231964.3969 | 2656354.912 | 1231970.1475 | 2656353.1466 | 1231979.0477 | 2656346.0929 | 1232005.1609
38 | 2656339.128 | 1232044.2878 | 2656339.1297 | 1232044.6219
39 | 2656355.8223 | 1231964.3969 | 2656356.1367 | 1231955.194
40 | 2656356.1367 | 1231955.194 | 2656364.3954 | 1231958.7925
41 | 2656364.3954 | 1231958.7925 | 2656385.383 | 1231967.9374
42 | 2656401.1232 | 1231974.7958 | 2656385.383 | 1231967.9374
43 | 2656233.5456 | 1232093.6228 | 2656233.5456 | 1232093.6228 | 2656239.3454 | 1232095.3203
44 | 2656233.5456 | 1232093.6228 | 2656210.0747 | 1232078.0576 | 2656206.8117 | 1232074.8795
45 | 2655984.7337 | 1232076.6621 | 2655984.2851 | 1232080.1517 | 2655983.778 | 1232082.189
46 | 2656026.4011 | 1232096.3698 | 2655983.778 | 1232082.189
47 | 2655984.7337 | 1232076.6621 | 2655986.1481 | 1232065.6599 | 2655984.749 | 1232043.7548 | 2655986.5564 | 1232035.1663 | 2655987.2113 | 1232033.506
48 | 2656026.4011 | 1232096.3698 | 2656017.839 | 1232112.9373
49 | 2656026.4011 | 1232096.3698 | 2656032.3169 | 1232084.9293 | 2656034.6959 | 1232079.8523
50 | 2656026.4011 | 1232096.3698 | 2656040.1432 | 1232097.3554 | 2656042.0753 | 1232096.8819
51 | 2656017.839 | 1232112.9373 | 2656016.2701 | 1232115.9731
52 | 2656041.8931 | 1232064.4931 | 2656034.6959 | 1232079.8523
53 | 2656044.6146 | 1232096.2595 | 2656042.0753 | 1232096.8819
54 | 2656052.7065 | 1232040.7559 | 2656050.601 | 1232045.9098 | 2656045.2004 | 1232057.4352
55 | 2656041.8931 | 1232064.4931 | 2656045.2004 | 1232057.4352
56 | 2656054.4649 | 1232036.4514 | 2656052.7065 | 1232040.7559
57 | 2655993.9688 | 1232163.0851 | 2655998.6044 | 1232153.3002 | 2655999.1151 | 1232152.2118
58 | 2655993.9688 | 1232163.0851 | 2656024.3375 | 1232154.9375
59 | 2655993.9688 | 1232163.0851 | 2655986.4413 | 1232178.9853
60 | 2655999.1151 | 1232152.2118 | 2656014.6619 | 1232119.0849 | 2656016.2701 | 1232115.9731
61 | 2656037.8474 | 1232151.313 | 2656024.3375 | 1232154.9375
62 | 2655986.4413 | 1232178.9853 | 2655981.902 | 1232188.5735
63 | 2656037.8474 | 1232151.313 | 2656031.0964 | 1232168.6161 | 2656023.2494 | 1232183.5229
64 | 2656037.8474 | 1232151.313 | 2656048.3396 | 1232148.495
65 | 2656368.3867 | 1232185.5513 | 2656368.0332 | 1232186.5007
66 | 2656408.3257 | 1232224.1841 | 2656407.6323 | 1232223.814
67 | 2656341.769 | 1232284.9309 | 2656338.475 | 1232300.1032
68 | 2656380.4778 | 1232153.0744 | 2656375.4018 | 1232166.7127 | 2656368.3867 | 1232185.5513
69 | 2656408.3257 | 1232224.1841 | 2656415.7257 | 1232210.7663
70 | 2656408.3257 | 1232224.1841 | 2656426.6645 | 1232234.892
71 | 2656335.5534 | 1232313.5603 | 2656338.475 | 1232300.1032
72 | 2656115.0139 | 1232011.5515 | 2656116.2722 | 1232001.4503
73 | 2656115.0139 | 1232011.5515 | 2656114.4122 | 1232016.3813 | 2656114.261 | 1232022.7413
74 | 2656123.03 | 1231975.4363 | 2656116.6326 | 1231998.5575 | 2656116.2722 | 1232001.4503
75 | 2656114.0354 | 1232032.2324 | 2656114.261 | 1232022.7413
76 | 2656123.03 | 1231975.4363 | 2656153.083 | 1232003.727 | 2656157.8037 | 1232009.286
77 | 2656123.03 | 1231975.4363 | 2656125.2379 | 1231969.3754 | 2656130.5787 | 1231954.7053
78 | 2656114.0354 | 1232032.2324 | 2656113.9896 | 1232034.1441
79 | 2656114.0354 | 1232032.2324 | 2656106.2439 | 1232034.5826 | 2656097.8145 | 1232043.7353
80 | 2656157.8037 | 1232009.286 | 2656161.067 | 1232013.129
81 | 2656130.5787 | 1231954.7053 | 2656152.9071 | 1231963.0325 | 2656170.1776 | 1231974.9303
82 | 2656113.9896 | 1232034.1441 | 2656113.923 | 1232036.9232 | 2656114.8456 | 1232056.3 | 2656114.8456 | 1232056.3
83 | 2656082.0503 | 1232083.5137 | 2656082.2663 | 1232060.6177 | 2656097.8145 | 1232043.7353
84 | 2656161.067 | 1232013.129 | 2656164.8185 | 1232017.5467 | 2656175.2894 | 1232031.6488
85 | 2656170.1776 | 1231974.9303 | 2656187.861 | 1231987.1125
86 | 2656115.7808 | 1232059.7464 | 2656114.8456 | 1232056.3
87 | 2656006.8359 | 1232211.3996 | 2656012.8456 | 1232198.5301 | 2656016.8864 | 1232195.6107 | 2656023.2494 | 1232183.5229
88 | 2656051.4795 | 1232147.6517 | 2656048.3396 | 1232148.495
89 | 2656060.8973 | 1232020.7055 | 2656054.4649 | 1232036.4514
90 | 2656051.4795 | 1232147.6517 | 2656058.8834 | 1232145.6631 | 2656071.097 | 1232138.5528
91 | 2656075.4113 | 1232136.0412 | 2656071.097 | 1232138.5528
92 | 2656075.4113 | 1232136.0412 | 2656096.4895 | 1232123.7702 | 2656099.4377 | 1232116.8798
93 | 2656109.4386 | 1232093.5066 | 2656099.4377 | 1232116.8798
94 | 2655993.4404 | 1232240.0852 | 2656006.8359 | 1232211.3996
95 | 2656109.4386 | 1232093.5066 | 2656109.9907 | 1232092.2163
96 | 2656119.9682 | 1232073.5594 | 2656116.6217 | 1232076.7188 | 2656109.9907 | 1232092.2163
97 | 2656119.9682 | 1232073.5594 | 2656122.967 | 1232079.6688
98 | 2656119.9682 | 1232073.5594 | 2656118.9802 | 1232071.5377 | 2656116.6028 | 1232062.7762
99 | 2656125.0845 | 1232083.9828 | 2656122.967 | 1232079.6688
100 | 2656116.6028 | 1232062.7762 | 2656115.7808 | 1232059.7464
101 | 2656137.2381 | 1232108.7429 | 2656125.0845 | 1232083.9828
102 | 2656203.1265 | 1231997.6291 | 2656187.861 | 1231987.1125
103 | 2656177.2999 | 1232034.3564 | 2656175.2894 | 1232031.6488
104 | 2656137.2381 | 1232108.7429 | 2656140.0314 | 1232114.4337
105 | 2656447.2166 | 1232295.6416 | 2656457.611 | 1232273.7933
106 | 2656465.5249 | 1232256.9814 | 2656460.8487 | 1232266.9879 | 2656457.611 | 1232273.7933
107 | 2656440.2193 | 1232310.3534 | 2656445.141 | 1232300.0045 | 2656447.2166 | 1232295.6416
108 | 2656465.5249 | 1232256.9814 | 2656456.1619 | 1232251.7765
109 | 2656440.2193 | 1232310.3534 | 2656432.3223 | 1232326.8139
110 | 2656441.0504 | 1232243.2918 | 2656444.0576 | 1232245.0477 | 2656456.1619 | 1232251.7765
111 | 2656432.3223 | 1232326.8139 | 2656418.0195 | 1232356.6268
112 | 2656436.3688 | 1232240.5583 | 2656441.0504 | 1232243.2918
113 | 2656418.0195 | 1232356.6268 | 2656410.9943 | 1232371.2701
114 | 2656436.3688 | 1232240.5583 | 2656426.6645 | 1232234.892
115 | 2656415.7257 | 1232210.7663 | 2656418.081 | 1232206.4957
116 | 2656431.2031 | 1232182.8277 | 2656426.5399 | 1232191.1579 | 2656418.081 | 1232206.4957
117 | 2656335.5534 | 1232313.5603 | 2656335.2615 | 1232314.9048
118 | 2656327.2024 | 1232367.4855 | 2656316.1325 | 1232361.0543 | 2656307.6029 | 1232353.0515
119 | 2656329.4002 | 1232383.2609 | 2656327.2024 | 1232367.4855
120 | 2656285.0079 | 1232331.8519 | 2656307.6029 | 1232353.0515
121 | 2656329.4002 | 1232383.2609 | 2656343.7445 | 1232389.1497
122 | 2656406.2187 | 1231977.0161 | 2656401.1232 | 1231974.7958
123 | 2656406.2187 | 1231977.0161 | 2656421.7364 | 1231950.3132
124 | 2656421.7364 | 1231950.3132 | 2656422.0001 | 1231949.8594 | 2656440.0291 | 1231928.8207
125 | 2656206.8117 | 1232074.8795 | 2656205.6018 | 1232073.7011
126 | 2656193.4769 | 1232061.1454 | 2656195.7809 | 1232064.1358 | 2656205.6018 | 1232073.7011
127 | 2656193.4769 | 1232061.1454 | 2656182.5999 | 1232042.9533
128 | 2656193.4769 | 1232061.1454 | 2656207.443 | 1232051.5106
129 | 2656140.0314 | 1232114.4337 | 2656141.5432 | 1232117.5135 | 2656153.5475 | 1232137.6486
130 | 2656157.1664 | 1232143.7186 | 2656153.5475 | 1232137.6486
131 | 2656158.5685 | 1232146.0704 | 2656157.1664 | 1232143.7186
132 | 2656158.5685 | 1232146.0704 | 2656160.4073 | 1232172.7832
133 | 2656160.4073 | 1232172.7832 | 2656161.5861 | 1232189.9088
134 | 2656164.0854 | 1232225.7848 | 2656163.3625 | 1232215.7161 | 2656161.5861 | 1232189.9088
135 | 2656189.041 | 1232186.6208 | 2656194.5832 | 1232193.996
136 | 2656215.9844 | 1232235.7804 | 2656214.0718 | 1232223.0999 | 2656208.6872 | 1232212.7646 | 2656194.5832 | 1232193.996
137 | 2656218.4176 | 1232252.9806 | 2656217.7983 | 1232247.8066 | 2656216.8792 | 1232241.7128
138 | 2656219.8194 | 1232264.6921 | 2656218.4176 | 1232252.9806
139 | 2656215.9844 | 1232235.7804 | 2656216.8792 | 1232241.7128
140 | 2656219.8194 | 1232264.6921 | 2656211.3036 | 1232281.9702
141 | 2656219.8194 | 1232264.6921 | 2656222.5346 | 1232280.2389
142 | 2656182.8798 | 1232312.279 | 2656193.6163 | 1232315.5328 | 2656209.5051 | 1232285.6192 | 2656211.3036 | 1232281.9702
143 | 2656221.1933 | 1232298.7658 | 2656222.7731 | 1232285.4445 | 2656222.5346 | 1232280.2389
144 | 2656171.2368 | 1232308.7504 | 2656182.8798 | 1232312.279
145 | 2656220.2394 | 1232322.7557 | 2656218.8153 | 1232318.8175 | 2656221.1933 | 1232298.7658
146 | 2656163.8653 | 1232324.3797 | 2656171.2368 | 1232308.7504
147 | 2656171.2368 | 1232308.7504 | 2656168.2999 | 1232295.0138 | 2656168.0311 | 1232289.5566
148 | 2656220.2394 | 1232322.7557 | 2656223.7348 | 1232325.4683 | 2656228.3721 | 1232326.724 | 2656233.1367 | 1232325.7351 | 2656252.7281 | 1232313.468 | 2656258.0179 | 1232312.9955 | 2656263.112 | 1232313.9999 | 2656263.8087 | 1232314.2894
149 | 2656220.2394 | 1232322.7557 | 2656215.9412 | 1232326.473 | 2656206.4346 | 1232357.2867
150 | 2656177.2999 | 1232034.3564 | 2656178.1205 | 1232035.4616 | 2656182.5999 | 1232042.9533
151 | 2656208.9151 | 1232050.495 | 2656207.443 | 1232051.5106
152 | 2656208.9151 | 1232050.495 | 2656224.5098 | 1232039.7366
153 | 2656285.0079 | 1232331.8519 | 2656266.3703 | 1232315.3538 | 2656263.8087 | 1232314.2894
154 | 2656226.9325 | 1232038.0653 | 2656224.5098 | 1232039.7366
155 | 2656168.0311 | 1232289.5566 | 2656166.6481 | 1232261.4766 | 2656166.084 | 1232253.6202
156 | 2656164.0854 | 1232225.7848 | 2656166.084 | 1232253.6202
157 | 2656389.7846 | 1232128.0686 | 2656380.4778 | 1232153.0744
158 | 2656389.7846 | 1232128.0686 | 2656381.8356 | 1232122.2784 | 2656373.1525 | 1232113.2459 | 2656371.3726 | 1232110.8705
159 | 2656226.9325 | 1232038.0653 | 2656241.7505 | 1232027.8427
160 | 2656241.7505 | 1232027.8427 | 2656245.0183 | 1232025.5884
161 | 2656245.0183 | 1232025.5884 | 2656259.2042 | 1232015.8019
162 | 2656263.4539 | 1232012.8701 | 2656259.2042 | 1232015.8019
163 | 2656263.4539 | 1232012.8701 | 2656276.7115 | 1232003.724
164 | 2656281.267 | 1232000.5813 | 2656276.7115 | 1232003.724

## bus_geodata
| x | y | coords
0 | 2655882.5194 | 1232354.7565
1 | 2655870.2794 | 1232368.9194
2 | 2655911.8857 | 1232314.7975
3 | 2655929.0976 | 1232286.8501
4 | 2655955.2862 | 1232242.835
5 | 2655970.9464 | 1232211.6079
6 | 2656334.8894 | 1232141.485
7 | 2656323.7776 | 1232179.9322
8 | 2656343.087 | 1232092.0362
9 | 2656341.1062 | 1232075.0852
10 | 2656326.649 | 1232097.3358
11 | 2656360.9936 | 1232099.0919
12 | 2656333.0868 | 1232207.6132
13 | 2656314.3592 | 1232179.6437
14 | 2656340.0983 | 1232066.4598
15 | 2656303.6785 | 1232103.7811
16 | 2656362.4956 | 1232100.4704
17 | 2656353.9831 | 1232228.6719
18 | 2656305.0831 | 1232194.6691
19 | 2656339.8483 | 1232064.321
20 | 2656289.3778 | 1232107.0874
21 | 2656369.7315 | 1232108.6804
22 | 2656363.0084 | 1232199.9945
23 | 2656364.369 | 1232238.5269
24 | 2656347.3799 | 1232259.0866
25 | 2656290.5872 | 1232214.0877
26 | 2656343.2678 | 1232018.3883
27 | 2656339.8439 | 1232036.5601
28 | 2656344.5052 | 1232011.8213
29 | 2656339.1153 | 1232041.8406
30 | 2656346.0929 | 1232005.1609
31 | 2656339.128 | 1232044.2878
32 | 2656355.8223 | 1231964.3969
33 | 2656339.1297 | 1232044.6219
34 | 2656356.1367 | 1231955.194
35 | 2656364.3954 | 1231958.7925
36 | 2656385.383 | 1231967.9374
37 | 2656239.3454 | 1232095.3203
38 | 2656233.5456 | 1232093.6228
39 | 2655983.778 | 1232082.189
40 | 2655984.7337 | 1232076.6621
41 | 2656026.4011 | 1232096.3698
42 | 2655987.2113 | 1232033.506
43 | 2656017.839 | 1232112.9373
44 | 2656034.6959 | 1232079.8523
45 | 2656042.0753 | 1232096.8819
46 | 2656045.2004 | 1232057.4352
47 | 2656052.7065 | 1232040.7559
48 | 2656041.8931 | 1232064.4931
49 | 2655993.9688 | 1232163.0851
50 | 2655999.1152 | 1232152.2118
51 | 2656024.3375 | 1232154.9375
52 | 2655986.4413 | 1232178.9853
53 | 2656016.2701 | 1232115.9731
54 | 2656037.8474 | 1232151.313
55 | 2655981.902 | 1232188.5735
56 | 2656368.0332 | 1232186.5007
57 | 2656407.6323 | 1232223.814
58 | 2656402.0196 | 1232274.2474
59 | 2656341.769 | 1232284.9309
60 | 2656368.3867 | 1232185.5513
61 | 2656408.3257 | 1232224.1841
62 | 2656338.475 | 1232300.1032
63 | 2656280.9781 | 1232236.041
64 | 2656115.0139 | 1232011.5515
65 | 2656116.2722 | 1232001.4503
66 | 2656114.261 | 1232022.7413
67 | 2656123.03 | 1231975.4363
68 | 2656114.0354 | 1232032.2324
69 | 2656157.8037 | 1232009.286
70 | 2656130.5787 | 1231954.7053
71 | 2656113.9896 | 1232034.1441
72 | 2656097.8145 | 1232043.7353
73 | 2656161.067 | 1232013.129
74 | 2656170.1776 | 1231974.9303
75 | 2656114.8456 | 1232056.3
76 | 2656082.0503 | 1232083.5137
77 | 2656023.2494 | 1232183.5229
78 | 2656048.3396 | 1232148.495
79 | 2656044.6146 | 1232096.2595
80 | 2656054.4649 | 1232036.4514
81 | 2656060.8973 | 1232020.7055
82 | 2656051.4795 | 1232147.6517
83 | 2656071.097 | 1232138.5528
84 | 2656075.4113 | 1232136.0412
85 | 2656099.4377 | 1232116.8798
86 | 2656006.8359 | 1232211.3996
87 | 2656109.4386 | 1232093.5066
88 | 2656109.9907 | 1232092.2163
89 | 2656119.9682 | 1232073.5594
90 | 2656122.967 | 1232079.6688
91 | 2656116.6028 | 1232062.7762
92 | 2656125.0845 | 1232083.9828
93 | 2656115.7808 | 1232059.7464
94 | 2656187.8609 | 1231987.1125
95 | 2656203.1265 | 1231997.6291
96 | 2655993.4404 | 1232240.0852
97 | 2656175.2894 | 1232031.6488
98 | 2656137.2381 | 1232108.7429
99 | 2656457.611 | 1232273.7933
100 | 2656447.2166 | 1232295.6416
101 | 2656465.5249 | 1232256.9814
102 | 2656440.2193 | 1232310.3534
103 | 2656456.1619 | 1232251.7765
104 | 2656432.3223 | 1232326.8139
105 | 2656441.0504 | 1232243.2918
106 | 2656418.0195 | 1232356.6268
107 | 2656436.3688 | 1232240.5583
108 | 2656426.6645 | 1232234.892
109 | 2656415.7257 | 1232210.7663
110 | 2656418.081 | 1232206.4957
111 | 2656431.2031 | 1232182.8277
112 | 2656335.5534 | 1232313.5603
113 | 2656335.2615 | 1232314.9048
114 | 2656327.2024 | 1232367.4855
115 | 2656307.6029 | 1232353.0515
116 | 2656329.4002 | 1232383.2609
117 | 2656401.1232 | 1231974.7958
118 | 2656406.2187 | 1231977.0161
119 | 2656421.7364 | 1231950.3132
120 | 2656440.0291 | 1231928.8207
121 | 2656206.8117 | 1232074.8795
122 | 2656205.6018 | 1232073.7011
123 | 2656193.4769 | 1232061.1454
124 | 2656153.5475 | 1232137.6486
125 | 2656140.0314 | 1232114.4337
126 | 2656157.1664 | 1232143.7186
127 | 2656158.5686 | 1232146.0704
128 | 2656160.4073 | 1232172.7832
129 | 2656161.5861 | 1232189.9088
130 | 2656189.041 | 1232186.6208
131 | 2656194.5832 | 1232193.996
132 | 2656218.4176 | 1232252.9806
133 | 2656216.8792 | 1232241.7128
134 | 2656219.8194 | 1232264.6921
135 | 2656215.9844 | 1232235.7804
136 | 2656211.3036 | 1232281.9702
137 | 2656222.5346 | 1232280.2389
138 | 2656182.8798 | 1232312.279
139 | 2656221.1933 | 1232298.7658
140 | 2656171.2368 | 1232308.7504
141 | 2656220.2394 | 1232322.7557
142 | 2656410.9943 | 1232371.2701
143 | 2656343.7445 | 1232389.1497
144 | 2656182.5999 | 1232042.9533
145 | 2656207.443 | 1232051.5106
146 | 2656177.2999 | 1232034.3564
147 | 2656208.9151 | 1232050.495
148 | 2656285.0079 | 1232331.8519
149 | 2656263.8087 | 1232314.2894
150 | 2656224.5098 | 1232039.7366
151 | 2656163.8653 | 1232324.3797
152 | 2656168.0311 | 1232289.5566
153 | 2656166.084 | 1232253.6202
154 | 2656380.4778 | 1232153.0744
155 | 2656389.7846 | 1232128.0686
156 | 2656371.3726 | 1232110.8705
157 | 2656206.4346 | 1232357.2867
158 | 2656164.0854 | 1232225.7848
159 | 2656226.9325 | 1232038.0653
160 | 2656241.7505 | 1232027.8427
161 | 2656245.0183 | 1232025.5884
162 | 2656259.2042 | 1232015.8019
163 | 2656263.4539 | 1232012.8701
164 | 2656276.7115 | 1232003.724
165 | 2656281.267 | 1232000.5813
166 | 2656343.087 | 1232092.0362

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1