## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4139-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4139-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4139-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4139-6_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4139-6_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4139-6_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_4139-6_0_4_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_4139-6_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_4139-6_0_4_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_4139-6_0_4_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_4139-6_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_4139-6_0_4_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_4139-6_0_4_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_4139-6_0_4_node_23 | 0.4 | n |  | TRUE
14 | bus_LV_4139-6_0_4_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_4139-6_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4139-6_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_4139-6_0_4_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_4139-6_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_4139-6_0_4_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_4139-6_0_4_node_27 | 0.4 | n |  | TRUE
21 | bus_LV_4139-6_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_4139-6_0_4_node_28 | 0.4 | n |  | TRUE
23 | bus_LV_4139-6_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_4139-6_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_4139-6_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_4139-6_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_4139-6_0_4_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_4139-6_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_4139-6_0_4_node_66 | 0.4 | n |  | TRUE
30 | bus_LV_4139-6_0_4_node_33 | 0.4 | n |  | TRUE
31 | bus_LV_4139-6_0_4_node_65 | 0.4 | n |  | TRUE
32 | bus_LV_4139-6_0_4_node_48 | 0.4 | n |  | TRUE
33 | bus_LV_4139-6_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_4139-6_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_4139-6_0_4_node_83 | 0.4 | n |  | TRUE
36 | bus_LV_4139-6_0_4_node_86 | 0.4 | n |  | TRUE
37 | bus_LV_4139-6_0_4_node_81 | 0.4 | n |  | TRUE
38 | bus_LV_4139-6_0_4_node_87 | 0.4 | n |  | TRUE
39 | bus_LV_4139-6_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_4139-6_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_4139-6_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_4139-6_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_4139-6_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_4139-6_0_4_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_4139-6_0_4_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_4139-6_0_4_node_110 | 0.4 | n |  | TRUE
47 | bus_LV_4139-6_0_4_node_131 | 0.4 | n |  | TRUE
48 | bus_LV_4139-6_0_4_node_130 | 0.4 | n |  | TRUE
49 | bus_LV_4139-6_0_4_node_125 | 0.4 | n |  | TRUE
50 | bus_LV_4139-6_0_4_node_111 | 0.4 | n |  | TRUE
51 | bus_LV_4139-6_0_4_node_126 | 0.4 | n |  | TRUE
52 | bus_LV_4139-6_0_4_node_127 | 0.4 | n |  | TRUE
53 | bus_LV_4139-6_0_4_node_120 | 0.4 | n |  | TRUE
54 | bus_LV_4139-6_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_4139-6_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_4139-6_0_4_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_4139-6_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_4139-6_0_4_node_106 | 0.4 | n |  | TRUE
59 | bus_LV_4139-6_0_4_node_69 | 0.4 | n |  | TRUE
60 | bus_LV_4139-6_0_4_node_80 | 0.4 | n |  | TRUE
61 | bus_LV_4139-6_0_4_node_114 | 0.4 | n |  | TRUE
62 | bus_LV_4139-6_0_4_node_115 | 0.4 | n |  | TRUE
63 | bus_LV_4139-6_0_4_node_67 | 0.4 | n |  | TRUE
64 | bus_LV_4139-6_0_4_node_68 | 0.4 | n |  | TRUE
65 | bus_LV_4139-6_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_4139-6_0_4_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_4139-6_0_4_node_47 | 0.4 | n |  | TRUE
68 | bus_LV_4139-6_0_4_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_4139-6_0_4_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_4139-6_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_4139-6_0_4_node_53 | 0.4 | n |  | TRUE
72 | bus_LV_4139-6_0_4_node_54 | 0.4 | n |  | TRUE
73 | bus_LV_4139-6_0_4_node_55 | 0.4 | n |  | TRUE
74 | bus_LV_4139-6_0_4_node_56 | 0.4 | n |  | TRUE
75 | bus_LV_4139-6_0_4_node_57 | 0.4 | n |  | TRUE
76 | bus_LV_4139-6_0_4_node_58 | 0.4 | n |  | TRUE
77 | bus_LV_4139-6_0_4_node_59 | 0.4 | n |  | TRUE
78 | bus_LV_4139-6_0_4_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_4139-6_0_4_node_108 | 0.4 | n |  | TRUE
80 | bus_LV_4139-6_0_4_node_61 | 0.4 | n |  | TRUE
81 | bus_LV_4139-6_0_4_node_107 | 0.4 | n |  | TRUE
82 | bus_LV_4139-6_0_4_node_112 | 0.4 | n |  | TRUE
83 | bus_LV_4139-6_0_4_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_4139-6_0_4_node_109 | 0.4 | n |  | TRUE
85 | bus_LV_4139-6_0_4_node_70 | 0.4 | n |  | TRUE
86 | bus_LV_4139-6_0_4_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_4139-6_0_4_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_4139-6_0_4_node_73 | 0.4 | n |  | TRUE
89 | bus_LV_4139-6_0_4_node_74 | 0.4 | n |  | TRUE
90 | bus_LV_4139-6_0_4_node_104 | 0.4 | n |  | TRUE
91 | bus_LV_4139-6_0_4_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_4139-6_0_4_node_75 | 0.4 | n |  | TRUE
93 | bus_LV_4139-6_0_4_node_76 | 0.4 | n |  | TRUE
94 | bus_LV_4139-6_0_4_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_4139-6_0_4_node_78 | 0.4 | n |  | TRUE
96 | bus_LV_4139-6_0_4_node_79 | 0.4 | n |  | TRUE
97 | bus_LV_4139-6_0_4_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_4139-6_0_4_node_84 | 0.4 | n |  | TRUE
99 | bus_LV_4139-6_0_4_node_85 | 0.4 | n |  | TRUE
100 | bus_LV_4139-6_0_4_node_102 | 0.4 | n |  | TRUE
101 | bus_LV_4139-6_0_4_node_100 | 0.4 | n |  | TRUE
102 | bus_LV_4139-6_0_4_node_88 | 0.4 | n |  | TRUE
103 | bus_LV_4139-6_0_4_node_89 | 0.4 | n |  | TRUE
104 | bus_LV_4139-6_0_4_node_90 | 0.4 | n |  | TRUE
105 | bus_LV_4139-6_0_4_node_91 | 0.4 | n |  | TRUE
106 | bus_LV_4139-6_0_4_node_92 | 0.4 | n |  | TRUE
107 | bus_LV_4139-6_0_4_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_4139-6_0_4_node_95 | 0.4 | n |  | TRUE
109 | bus_LV_4139-6_0_4_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_4139-6_0_4_node_94 | 0.4 | n |  | TRUE
111 | bus_LV_4139-6_0_4_node_122 | 0.4 | n |  | TRUE
112 | bus_LV_4139-6_0_4_node_123 | 0.4 | n |  | TRUE
113 | bus_LV_4139-6_0_4_node_118 | 0.4 | n |  | TRUE
114 | bus_LV_4139-6_0_4_node_159 | 0.4 | n |  | TRUE
115 | bus_LV_4139-6_0_4_node_124 | 0.4 | n |  | TRUE
116 | bus_LV_4139-6_0_4_node_119 | 0.4 | n |  | TRUE
117 | bus_LV_4139-6_0_4_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_4139-6_0_4_node_98 | 0.4 | n |  | TRUE
119 | bus_LV_4139-6_0_4_node_99 | 0.4 | n |  | TRUE
120 | bus_LV_4139-6_0_4_node_101 | 0.4 | n |  | TRUE
121 | bus_LV_4139-6_0_4_node_103 | 0.4 | n |  | TRUE
122 | bus_LV_4139-6_0_4_node_113 | 0.4 | n |  | TRUE
123 | bus_LV_4139-6_0_4_node_117 | 0.4 | n |  | TRUE
124 | bus_LV_4139-6_0_4_node_116 | 0.4 | n |  | TRUE
125 | bus_LV_4139-6_0_4_node_121 | 0.4 | n |  | TRUE
126 | bus_LV_4139-6_0_4_node_128 | 0.4 | n |  | TRUE
127 | bus_LV_4139-6_0_4_node_129 | 0.4 | n |  | TRUE
128 | bus_LV_4139-6_0_4_node_132 | 0.4 | n |  | TRUE
129 | bus_LV_4139-6_0_4_node_136 | 0.4 | n |  | TRUE
130 | bus_LV_4139-6_0_4_node_133 | 0.4 | n |  | TRUE
131 | bus_LV_4139-6_0_4_node_137 | 0.4 | n |  | TRUE
132 | bus_LV_4139-6_0_4_node_134 | 0.4 | n |  | TRUE
133 | bus_LV_4139-6_0_4_node_135 | 0.4 | n |  | TRUE
134 | bus_LV_4139-6_0_4_node_160 | 0.4 | n |  | TRUE
135 | bus_LV_4139-6_0_4_node_154 | 0.4 | n |  | TRUE
136 | bus_LV_4139-6_0_4_node_157 | 0.4 | n |  | TRUE
137 | bus_LV_4139-6_0_4_node_152 | 0.4 | n |  | TRUE
138 | bus_LV_4139-6_0_4_node_138 | 0.4 | n |  | TRUE
139 | bus_LV_4139-6_0_4_node_139 | 0.4 | n |  | TRUE
140 | bus_LV_4139-6_0_4_node_163 | 0.4 | n |  | TRUE
141 | bus_LV_4139-6_0_4_node_161 | 0.4 | n |  | TRUE
142 | bus_LV_4139-6_0_4_node_170 | 0.4 | n |  | TRUE
143 | bus_LV_4139-6_0_4_node_177 | 0.4 | n |  | TRUE
144 | bus_LV_4139-6_0_4_node_162 | 0.4 | n |  | TRUE
145 | bus_LV_4139-6_0_4_node_140 | 0.4 | n |  | TRUE
146 | bus_LV_4139-6_0_4_node_141 | 0.4 | n |  | TRUE
147 | bus_LV_4139-6_0_4_node_142 | 0.4 | n |  | TRUE
148 | bus_LV_4139-6_0_4_node_143 | 0.4 | n |  | TRUE
149 | bus_LV_4139-6_0_4_node_144 | 0.4 | n |  | TRUE
150 | bus_LV_4139-6_0_4_node_145 | 0.4 | n |  | TRUE
151 | bus_LV_4139-6_0_4_node_164 | 0.4 | n |  | TRUE
152 | bus_LV_4139-6_0_4_node_146 | 0.4 | n |  | TRUE
153 | bus_LV_4139-6_0_4_node_156 | 0.4 | n |  | TRUE
154 | bus_LV_4139-6_0_4_node_165 | 0.4 | n |  | TRUE
155 | bus_LV_4139-6_0_4_node_166 | 0.4 | n |  | TRUE
156 | bus_LV_4139-6_0_4_node_167 | 0.4 | n |  | TRUE
157 | bus_LV_4139-6_0_4_node_153 | 0.4 | n |  | TRUE
158 | bus_LV_4139-6_0_4_node_147 | 0.4 | n |  | TRUE
159 | bus_LV_4139-6_0_4_node_148 | 0.4 | n |  | TRUE
160 | bus_LV_4139-6_0_4_node_150 | 0.4 | n |  | TRUE
161 | bus_LV_4139-6_0_4_node_151 | 0.4 | n |  | TRUE
162 | bus_LV_4139-6_0_4_node_168 | 0.4 | n |  | TRUE
163 | bus_LV_4139-6_0_4_node_155 | 0.4 | n |  | TRUE
164 | bus_LV_4139-6_0_4_node_158 | 0.4 | n |  | TRUE
165 | bus_LV_4139-6_0_4_node_176 | 0.4 | n |  | TRUE
166 | bus_LV_4139-6_0_4_node_169 | 0.4 | n |  | TRUE
167 | bus_LV_4139-6_0_4_node_171 | 0.4 | n |  | TRUE
168 | bus_LV_4139-6_0_4_node_173 | 0.4 | n |  | TRUE
169 | bus_LV_4139-6_0_4_node_174 | 0.4 | n |  | TRUE
170 | bus_LV_4139-6_0_4_node_175 | 0.4 | n |  | TRUE
171 | bus_MV_473_1_node_134 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4139-6_0_4_load_0 | 0 | 0.0040945 | 0.0010262 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4139-6_0_4_load_1 | 1 | 0.0019094 | 0.00047854 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4139-6_0_4_load_3 | 3 | 0.0085996 | 0.0021553 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4139-6_0_4_load_4 | 4 | 0.0019445 | 0.00048733 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4139-6_0_4_load_6 | 5 | 0.0022715 | 0.00056928 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4139-6_0_4_load_7 | 7 | 0.0023379 | 0.00058592 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4139-6_0_4_load_25 | 8 | 0.0052209 | 0.0013085 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4139-6_0_4_load_26 | 9 | 0.0034077 | 0.00085405 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4139-6_0_4_load_16 | 10 | 0.0057597 | 0.0014435 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4139-6_0_4_load_14 | 11 | 0.0020065 | 0.00050288 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4139-6_0_4_load_9 | 12 | 0.0071336 | 0.0017879 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4139-6_0_4_load_8 | 14 | 0.0066717 | 0.0016721 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4139-6_0_4_load_12 | 16 | 0.0022652 | 0.00056772 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4139-6_0_4_load_13 | 17 | 0.0093117 | 0.0023337 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4139-6_0_4_load_15 | 18 | 0.012845 | 0.0032192 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4139-6_0_4_load_20 | 19 | 0.0038732 | 0.0009707 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4139-6_0_4_load_18 | 21 | 0.0022023 | 0.00055196 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4139-6_0_4_load_17 | 23 | 0.0027997 | 0.00070167 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4139-6_0_4_load_21 | 25 | 0.006252 | 0.0015669 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4139-6_0_4_load_22 | 26 | 0.0013415 | 0.00033621 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4139-6_0_4_load_24 | 27 | 0.0023153 | 0.00058028 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4139-6_0_4_load_66 | 29 | 0.0069119 | 0.0017323 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4139-6_0_4_load_33 | 30 | 0.0020594 | 0.00051614 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4139-6_0_4_load_65 | 31 | 0.0035146 | 0.00088085 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4139-6_0_4_load_48 | 32 | 0.01226 | 0.0030728 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4139-6_0_4_load_31 | 33 | 0.0014148 | 0.00035458 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4139-6_0_4_load_32 | 34 | 0.0012939 | 0.00032428 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4139-6_0_4_load_83 | 35 | 0.0014804 | 0.00037103 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4139-6_0_4_load_86 | 36 | 0.0019803 | 0.00049631 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4139-6_0_4_load_81 | 37 | 0.0020613 | 0.0005166 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4139-6_0_4_load_87 | 38 | 0.0023532 | 0.00058977 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4139-6_0_4_load_34 | 39 | 0.0014718 | 0.00036886 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4139-6_0_4_load_35 | 40 | 0.001509 | 0.0003782 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4139-6_0_4_load_36 | 41 | 0.0016872 | 0.00042286 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4139-6_0_4_load_37 | 42 | 0.0023975 | 0.00060086 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4139-6_0_4_load_38 | 43 | 0.0026708 | 0.00066938 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4139-6_0_4_load_39 | 44 | 0.00049944 | 0.00012517 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4139-6_0_4_load_40 | 45 | 0.00052877 | 0.00013252 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4139-6_0_4_load_110 | 46 | 0.00067885 | 0.00017014 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4139-6_0_4_load_131 | 47 | 0.0042381 | 0.0010622 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4139-6_0_4_load_130 | 48 | 0.0009313 | 0.00023341 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4139-6_0_4_load_126 | 51 | 0.0014168 | 0.00035508 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4139-6_0_4_load_127 | 52 | 0.00053847 | 0.00013495 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4139-6_0_4_load_120 | 53 | 0.0013178 | 0.00033026 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4139-6_0_4_load_41 | 54 | 0.002192 | 0.00054937 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4139-6_0_4_load_42 | 55 | 0.00040099 | 0.0001005 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4139-6_0_4_load_43 | 56 | 0.0070475 | 0.0017663 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4139-6_0_4_load_44 | 57 | 0.00028151 | 7.0553e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4139-6_0_4_load_106 | 58 | 0.002289 | 0.00057367 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4139-6_0_4_load_80 | 60 | 0.00029589 | 7.4158e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4139-6_0_4_load_67 | 63 | 0.0043509 | 0.0010905 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4139-6_0_4_load_68 | 64 | 0.0040487 | 0.0010147 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4139-6_0_4_load_51 | 65 | 0.0020234 | 0.00050711 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4139-6_0_4_load_47 | 67 | 0.024585 | 0.0061617 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4139-6_0_4_load_52 | 68 | 0.0013719 | 0.00034384 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4139-6_0_4_load_62 | 69 | 0.0035593 | 0.00089205 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4139-6_0_4_load_63 | 70 | 0.008676 | 0.0021744 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4139-6_0_4_load_53 | 71 | 0.0068698 | 0.0017217 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4139-6_0_4_load_54 | 72 | 0.0028694 | 0.00071913 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4139-6_0_4_load_55 | 73 | 0.0022986 | 0.00057609 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4139-6_0_4_load_56 | 74 | 0.0039662 | 0.00099403 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4139-6_0_4_load_57 | 75 | 0.0030457 | 0.00076332 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4139-6_0_4_load_58 | 76 | 0.0030204 | 0.00075698 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4139-6_0_4_load_59 | 77 | 0.0023722 | 0.00059454 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4139-6_0_4_load_60 | 78 | 0.0041383 | 0.0010372 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4139-6_0_4_load_108 | 79 | 0.00068441 | 0.00017153 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4139-6_0_4_load_61 | 80 | 0.0034265 | 0.00085877 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4139-6_0_4_load_112 | 82 | 0.0067158 | 0.0016831 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4139-6_0_4_load_64 | 83 | 0.0050951 | 0.0012769 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4139-6_0_4_load_109 | 84 | 0.0015089 | 0.00037817 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4139-6_0_4_load_70 | 85 | 0.0052868 | 0.001325 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4139-6_0_4_load_71 | 86 | 0.0034963 | 0.00087626 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4139-6_0_4_load_72 | 87 | 0.010171 | 0.0025491 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4139-6_0_4_load_73 | 88 | 0.0050857 | 0.0012746 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4139-6_0_4_load_74 | 89 | 0.0062097 | 0.0015563 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4139-6_0_4_load_104 | 90 | 0.0033872 | 0.0008489 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4139-6_0_4_load_75 | 92 | 0.0013767 | 0.00034504 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4139-6_0_4_load_76 | 93 | 0.0013122 | 0.00032886 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4139-6_0_4_load_77 | 94 | 0.00024618 | 6.1699e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4139-6_0_4_load_78 | 95 | 0.00231 | 0.00057894 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4139-6_0_4_load_79 | 96 | 0.00025095 | 6.2893e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4139-6_0_4_load_82 | 97 | 0.0032815 | 0.00082241 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4139-6_0_4_load_85 | 99 | 0.0028574 | 0.00071613 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4139-6_0_4_load_102 | 100 | 0.0017782 | 0.00044565 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4139-6_0_4_load_100 | 101 | 0.0026524 | 0.00066476 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4139-6_0_4_load_88 | 102 | 0.0049925 | 0.0012512 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4139-6_0_4_load_89 | 103 | 0.00067377 | 0.00016886 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4139-6_0_4_load_90 | 104 | 0.0022954 | 0.00057529 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4139-6_0_4_load_93 | 107 | 0.0092696 | 0.0023232 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4139-6_0_4_load_95 | 108 | 0.0086092 | 0.0021577 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4139-6_0_4_load_96 | 109 | 0.007323 | 0.0018353 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4139-6_0_4_load_122 | 111 | 0.0019166 | 0.00048034 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4139-6_0_4_load_118 | 113 | 0.01059 | 0.0026542 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4139-6_0_4_load_159 | 114 | 0.0017897 | 0.00044855 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4139-6_0_4_load_124 | 115 | 0.0018996 | 0.00047608 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4139-6_0_4_load_97 | 117 | 0.0026841 | 0.00067269 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4139-6_0_4_load_98 | 118 | 0.0029786 | 0.00074651 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4139-6_0_4_load_99 | 119 | 0.013976 | 0.0035028 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4139-6_0_4_load_103 | 121 | 0.0066653 | 0.0016705 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4139-6_0_4_load_113 | 122 | 0.0026905 | 0.00067431 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4139-6_0_4_load_117 | 123 | 0.0079107 | 0.0019826 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4139-6_0_4_load_116 | 124 | 0.0030761 | 0.00077095 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4139-6_0_4_load_121 | 125 | 0.00079217 | 0.00019854 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4139-6_0_4_load_128 | 126 | 0.021118 | 0.0052927 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4139-6_0_4_load_129 | 127 | 0.00081855 | 0.00020515 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4139-6_0_4_load_132 | 128 | 0.0004497 | 0.0001127 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4139-6_0_4_load_136 | 129 | 0.00051008 | 0.00012784 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4139-6_0_4_load_133 | 130 | 0.0007965 | 0.00019962 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4139-6_0_4_load_134 | 132 | 0.0037063 | 0.00092888 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4139-6_0_4_load_135 | 133 | 0.00037537 | 9.4076e-05 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4139-6_0_4_load_160 | 134 | 0.0051956 | 0.0013022 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4139-6_0_4_load_157 | 136 | 0.0018217 | 0.00045656 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4139-6_0_4_load_152 | 137 | 0.00068334 | 0.00017126 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4139-6_0_4_load_138 | 138 | 0.0020883 | 0.00052338 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4139-6_0_4_load_139 | 139 | 0.00086539 | 0.00021689 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4139-6_0_4_load_161 | 141 | 0.00094486 | 0.0002368 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4139-6_0_4_load_177 | 143 | 0.00028034 | 7.026e-05 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4139-6_0_4_load_162 | 144 | 0.0041493 | 0.0010399 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4139-6_0_4_load_140 | 145 | 0.00076628 | 0.00019205 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4139-6_0_4_load_141 | 146 | 0.001109 | 0.00027795 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4139-6_0_4_load_143 | 148 | 0.00071501 | 0.0001792 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4139-6_0_4_load_144 | 149 | 0.0015759 | 0.00039495 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4139-6_0_4_load_145 | 150 | 0.00073946 | 0.00018533 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4139-6_0_4_load_146 | 152 | 0.0012015 | 0.00030112 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4139-6_0_4_load_165 | 154 | 0.0024539 | 0.000615 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4139-6_0_4_load_166 | 155 | 0.0012561 | 0.00031482 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4139-6_0_4_load_167 | 156 | 0.0014473 | 0.00036272 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4139-6_0_4_load_147 | 158 | 0.00016275 | 4.0788e-05 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4139-6_0_4_load_148 | 159 | 0.002934 | 0.00073533 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4139-6_0_4_load_150 | 160 | 0.0040485 | 0.0010147 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4139-6_0_4_load_151 | 161 | 0.00071644 | 0.00017956 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4139-6_0_4_load_168 | 162 | 0.0020114 | 0.00050409 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4139-6_0_4_load_155 | 163 | 0.00038664 | 9.6902e-05 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4139-6_0_4_load_158 | 164 | 0.0012873 | 0.00032262 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4139-6_0_4_load_176 | 165 | 0.0002241 | 5.6164e-05 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4139-6_0_4_load_169 | 166 | 0.0016151 | 0.00040477 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4139-6_0_4_load_171 | 167 | 0.004121 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4139-6_0_4_load_173 | 168 | 0.00055762 | 0.00013975 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4139-6_0_4_load_174 | 169 | 0.0025222 | 0.00063213 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4139-6_0_4_load_175 | 170 | 0.00084076 | 0.00021071 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 75 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4139-6_0_4_line_0 |  | 0 | 1 | 0.022155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4139-6_0_4_line_1 |  | 0 | 2 | 0.013137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4139-6_0_4_line_2 |  | 1 | 3 | 0.019246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4139-6_0_4_line_3 |  | 2 | 4 | 0.029335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4139-6_0_4_line_4 |  | 3 | 5 | 5.9427e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4139-6_0_4_line_5 |  | 5 | 6 | 0.018563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4139-6_0_4_line_6 |  | 6 | 11 | 0.0043609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_4139-6_0_4_line_7 |  | 6 | 12 | 0.019812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_4139-6_0_4_line_8 |  | 7 | 8 | 0.013904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4139-6_0_4_line_9 |  | 8 | 13 | 0.011477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4139-6_0_4_line_10 |  | 9 | 10 | 0.021223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4139-6_0_4_line_11 |  | 10 | 17 | 0.0012235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4139-6_0_4_line_12 |  | 11 | 19 | 0.0044235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_4139-6_0_4_line_13 |  | 12 | 14 | 0.017048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_4139-6_0_4_line_14 |  | 13 | 28 | 0.022446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4139-6_0_4_line_15 |  | 13 | 25 | 0.021091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4139-6_0_4_line_16 |  | 14 | 15 | 0.024182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_4139-6_0_4_line_17 |  | 15 | 16 | 0.0057452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4139-6_0_4_line_18 |  | 15 | 17 | 0.024839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4139-6_0_4_line_19 |  | 16 | 18 | 0.050219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4139-6_0_4_line_20 |  | 18 | 20 | 0.00019941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4139-6_0_4_line_21 |  | 19 | 21 | 0.010224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_4139-6_0_4_line_22 |  | 20 | 22 | 0.020933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4139-6_0_4_line_23 |  | 21 | 23 | 0.012521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_4139-6_0_4_line_24 |  | 22 | 33 | 0.022777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4139-6_0_4_line_25 |  | 22 | 34 | 0.013278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4139-6_0_4_line_26 |  | 23 | 24 | 0.02626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_4139-6_0_4_line_27 |  | 24 | 25 | 0.014579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4139-6_0_4_line_28 |  | 24 | 26 | 0.03709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_4139-6_0_4_line_29 |  | 26 | 27 | 0.0045687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_4139-6_0_4_line_30 |  | 27 | 29 | 0.017284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_4139-6_0_4_line_31 |  | 28 | 30 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4139-6_0_4_line_32 |  | 29 | 31 | 0.022023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_4139-6_0_4_line_33 |  | 29 | 32 | 0.077537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4139-6_0_4_line_34 |  | 31 | 63 | 0.069652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_4139-6_0_4_line_35 |  | 32 | 66 | 0.01914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4139-6_0_4_line_36 |  | 32 | 67 | 0.0024988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4139-6_0_4_line_37 |  | 33 | 35 | 0.014015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4139-6_0_4_line_38 |  | 34 | 36 | 0.0025626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4139-6_0_4_line_39 |  | 35 | 37 | 0.00021787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4139-6_0_4_line_40 |  | 36 | 38 | 0.018393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4139-6_0_4_line_41 |  | 38 | 102 | 0.012449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4139-6_0_4_line_42 |  | 39 | 40 | 0.030463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_4139-6_0_4_line_43 |  | 39 | 41 | 0.015453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_4139-6_0_4_line_44 |  | 40 | 42 | 0.0081095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_4139-6_0_4_line_45 |  | 41 | 43 | 0.0089612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_4139-6_0_4_line_46 |  | 42 | 44 | 0.002399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_4139-6_0_4_line_47 |  | 43 | 45 | 0.013933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_4139-6_0_4_line_48 |  | 44 | 46 | 0.025566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
49 | LV_4139-6_0_4_line_49 |  | 45 | 49 | 0.020534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_4139-6_0_4_line_50 |  | 46 | 50 | 0.023652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_4139-6_0_4_line_51 |  | 47 | 48 | 0.019256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4139-6_0_4_line_52 |  | 48 | 95 | 0.038508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4139-6_0_4_line_53 |  | 49 | 51 | 0.036673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4139-6_0_4_line_54 |  | 49 | 52 | 0.021485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4139-6_0_4_line_55 |  | 49 | 53 | 0.01747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_4139-6_0_4_line_56 |  | 50 | 82 | 0.0574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4139-6_0_4_line_57 |  | 50 | 80 | 0.012928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_4139-6_0_4_line_58 |  | 51 | 126 | 0.02221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4139-6_0_4_line_59 |  | 52 | 127 | 0.026393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4139-6_0_4_line_60 |  | 53 | 116 | 0.013405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_4139-6_0_4_line_61 |  | 54 | 55 | 0.037184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4139-6_0_4_line_62 |  | 54 | 56 | 0.046534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4139-6_0_4_line_63 |  | 55 | 57 | 0.012168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4139-6_0_4_line_64 |  | 57 | 61 | 0.070515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4139-6_0_4_line_65 |  | 58 | 59 | 0.018995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4139-6_0_4_line_66 |  | 58 | 60 | 0.039673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4139-6_0_4_line_67 |  | 59 | 81 | 0.005478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_4139-6_0_4_line_68 |  | 59 | 64 | 0.017482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_4139-6_0_4_line_69 |  | 60 | 96 | 0.018117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4139-6_0_4_line_70 |  | 61 | 62 | 0.032372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4139-6_0_4_line_71 |  | 62 | 115 | 0.067149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4139-6_0_4_line_72 |  | 63 | 64 | 0.013073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_4139-6_0_4_line_73 |  | 65 | 66 | 0.035916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4139-6_0_4_line_74 |  | 66 | 68 | 0.0012956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4139-6_0_4_line_75 |  | 68 | 69 | 0.025788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4139-6_0_4_line_76 |  | 69 | 70 | 0.034716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4139-6_0_4_line_77 |  | 70 | 83 | 0.03432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4139-6_0_4_line_78 |  | 71 | 72 | 0.037895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_4139-6_0_4_line_79 |  | 71 | 73 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_4139-6_0_4_line_80 |  | 72 | 74 | 0.00090425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
81 | LV_4139-6_0_4_line_81 |  | 73 | 75 | 0.019371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_4139-6_0_4_line_82 |  | 74 | 76 | 0.011112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
83 | LV_4139-6_0_4_line_83 |  | 75 | 77 | 0.02455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
84 | LV_4139-6_0_4_line_84 |  | 76 | 78 | 0.0084855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_4139-6_0_4_line_85 |  | 77 | 79 | 0.029389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_4139-6_0_4_line_86 |  | 78 | 80 | 0.0049115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_4139-6_0_4_line_87 |  | 79 | 81 | 0.027913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_4139-6_0_4_line_88 |  | 81 | 84 | 0.014495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4139-6_0_4_line_89 |  | 82 | 122 | 0.005544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4139-6_0_4_line_90 |  | 84 | 124 | 0.0097938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4139-6_0_4_line_91 |  | 85 | 86 | 0.0034262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4139-6_0_4_line_92 |  | 85 | 87 | 0.017177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4139-6_0_4_line_93 |  | 86 | 88 | 0.012018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4139-6_0_4_line_94 |  | 88 | 89 | 0.038124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4139-6_0_4_line_95 |  | 89 | 90 | 0.034623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4139-6_0_4_line_96 |  | 90 | 91 | 0.026445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4139-6_0_4_line_97 |  | 91 | 123 | 0.019079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4139-6_0_4_line_98 |  | 91 | 124 | 0.025626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4139-6_0_4_line_99 |  | 92 | 93 | 0.0099878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4139-6_0_4_line_100 |  | 92 | 94 | 0.031206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4139-6_0_4_line_101 |  | 93 | 95 | 0.021059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4139-6_0_4_line_102 |  | 94 | 96 | 0.019673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4139-6_0_4_line_103 |  | 97 | 98 | 0.023309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4139-6_0_4_line_104 |  | 98 | 99 | 0.0054837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4139-6_0_4_line_105 |  | 99 | 100 | 0.0033286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4139-6_0_4_line_106 |  | 100 | 101 | 0.036852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4139-6_0_4_line_107 |  | 101 | 118 | 0.033871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4139-6_0_4_line_108 |  | 103 | 104 | 0.013284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
109 | LV_4139-6_0_4_line_109 |  | 103 | 105 | 0.071361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
110 | LV_4139-6_0_4_line_110 |  | 104 | 106 | 0.014518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_4139-6_0_4_line_111 |  | 105 | 107 | 0.022813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4139-6_0_4_line_112 |  | 106 | 108 | 0.0080066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
113 | LV_4139-6_0_4_line_113 |  | 107 | 109 | 0.03883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4139-6_0_4_line_114 |  | 108 | 113 | 0.040247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_4139-6_0_4_line_115 |  | 109 | 114 | 0.015262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4139-6_0_4_line_116 |  | 110 | 111 | 0.031005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4139-6_0_4_line_117 |  | 110 | 112 | 0.078988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4139-6_0_4_line_118 |  | 111 | 114 | 0.037743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4139-6_0_4_line_119 |  | 112 | 115 | 0.0058095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4139-6_0_4_line_120 |  | 113 | 116 | 0.013208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_4139-6_0_4_line_121 |  | 116 | 125 | 0.028984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4139-6_0_4_line_122 |  | 117 | 118 | 0.045932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4139-6_0_4_line_123 |  | 117 | 119 | 0.0061832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4139-6_0_4_line_124 |  | 119 | 120 | 0.02014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4139-6_0_4_line_125 |  | 120 | 121 | 0.0016127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4139-6_0_4_line_126 |  | 121 | 122 | 0.016255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4139-6_0_4_line_127 |  | 126 | 128 | 0.0030301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4139-6_0_4_line_128 |  | 127 | 129 | 0.012121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4139-6_0_4_line_129 |  | 128 | 130 | 0.025866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4139-6_0_4_line_130 |  | 129 | 131 | 0.010509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4139-6_0_4_line_131 |  | 130 | 132 | 0.019236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4139-6_0_4_line_132 |  | 130 | 133 | 0.0035191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4139-6_0_4_line_133 |  | 131 | 138 | 0.06396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4139-6_0_4_line_134 |  | 131 | 139 | 0.017051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4139-6_0_4_line_135 |  | 132 | 134 | 0.029777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4139-6_0_4_line_136 |  | 133 | 135 | 0.026291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4139-6_0_4_line_137 |  | 135 | 136 | 0.025987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4139-6_0_4_line_138 |  | 135 | 137 | 0.0035666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4139-6_0_4_line_139 |  | 137 | 157 | 0.023373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4139-6_0_4_line_140 |  | 138 | 140 | 0.023902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4139-6_0_4_line_141 |  | 139 | 141 | 0.014085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4139-6_0_4_line_142 |  | 140 | 142 | 0.017847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4139-6_0_4_line_143 |  | 140 | 143 | 0.012485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4139-6_0_4_line_144 |  | 141 | 144 | 0.0078615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4139-6_0_4_line_145 |  | 142 | 162 | 0.042356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4139-6_0_4_line_146 |  | 142 | 161 | 0.039707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4139-6_0_4_line_147 |  | 143 | 165 | 0.021636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4139-6_0_4_line_148 |  | 145 | 146 | 0.020895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4139-6_0_4_line_149 |  | 145 | 147 | 0.033743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4139-6_0_4_line_150 |  | 147 | 148 | 0.0032387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4139-6_0_4_line_151 |  | 147 | 149 | 0.027285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4139-6_0_4_line_152 |  | 148 | 150 | 0.013689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4139-6_0_4_line_153 |  | 150 | 151 | 0.025145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4139-6_0_4_line_154 |  | 151 | 154 | 0.034959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4139-6_0_4_line_155 |  | 151 | 155 | 0.065801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4139-6_0_4_line_156 |  | 151 | 156 | 0.054443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4139-6_0_4_line_157 |  | 152 | 153 | 0.020977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4139-6_0_4_line_158 |  | 153 | 157 | 0.059825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4139-6_0_4_line_159 |  | 154 | 162 | 0.043276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4139-6_0_4_line_160 |  | 155 | 166 | 0.0048743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4139-6_0_4_line_161 |  | 157 | 163 | 0.016527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4139-6_0_4_line_162 |  | 158 | 159 | 0.017961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4139-6_0_4_line_163 |  | 159 | 160 | 0.01055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4139-6_0_4_line_164 |  | 160 | 161 | 0.031869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4139-6_0_4_line_165 |  | 163 | 164 | 0.016075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4139-6_0_4_line_166 |  | 165 | 169 | 0.030515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4139-6_0_4_line_167 |  | 166 | 167 | 0.028118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4139-6_0_4_line_168 |  | 168 | 169 | 0.0083772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4139-6_0_4_line_169 |  | 168 | 170 | 0.0040959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4139-6_0_4_trafo_57 | 0.63 MVA 20/0.4 kV | 171 | 75 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2656481.8845 | 1232224.0549 | 2656491.6152 | 1232204.1513
1 | 2656476.1145 | 1232235.8572 | 2656481.8845 | 1232224.0549
2 | 2656491.6152 | 1232204.1513 | 2656500.0681 | 1232186.8611
3 | 2656476.1145 | 1232235.8572 | 2656482.016 | 1232236.3691 | 2656505.0593 | 1232232.2325
4 | 2656500.0681 | 1232186.8611 | 2656500.0942 | 1232186.8077
5 | 2656508.2472 | 1232170.1311 | 2656500.0942 | 1232186.8077
6 | 2656508.2472 | 1232170.1311 | 2656512.2896 | 1232171.7672
7 | 2656508.2472 | 1232170.1311 | 2656490.7681 | 1232160.8046
8 | 2656546.3221 | 1232224.8252 | 2656560.0069 | 1232222.3686
9 | 2656571.372 | 1232220.7861 | 2656562.0694 | 1232221.9984 | 2656560.0069 | 1232222.3686
10 | 2656441.5701 | 1232164.3089 | 2656431.2031 | 1232182.8277
11 | 2656442.1677 | 1232163.2414 | 2656441.5701 | 1232164.3089
12 | 2656512.2896 | 1232171.7672 | 2656516.39 | 1232173.4267
13 | 2656475.7269 | 1232152.7789 | 2656490.7681 | 1232160.8046
14 | 2656571.372 | 1232220.7861 | 2656571.6311 | 1232229.3607 | 2656585.4922 | 1232228.9368
15 | 2656571.372 | 1232220.7861 | 2656571.6484 | 1232199.6973
16 | 2656454.3012 | 1232141.5671 | 2656475.6398 | 1232152.7324 | 2656475.7269 | 1232152.7789
17 | 2656454.3012 | 1232141.5671 | 2656449.2103 | 1232138.9042
18 | 2656454.3012 | 1232141.5671 | 2656442.1677 | 1232163.2414
19 | 2656400.398 | 1232128.6429 | 2656410.9243 | 1232129.092 | 2656428.5 | 1232132.2496 | 2656445.5984 | 1232137.0149 | 2656449.2103 | 1232138.9042
20 | 2656400.1987 | 1232128.6344 | 2656400.398 | 1232128.6429
21 | 2656525.8674 | 1232177.2623 | 2656516.39 | 1232173.4267
22 | 2656399.3067 | 1232107.7236 | 2656400.1987 | 1232128.6344
23 | 2656525.8674 | 1232177.2623 | 2656535.3952 | 1232181.1184 | 2656537.5247 | 1232181.8219
24 | 2656399.3067 | 1232107.7236 | 2656399.1519 | 1232104.0864 | 2656396.7163 | 1232085.1058
25 | 2656399.3067 | 1232107.7236 | 2656412.5823 | 1232107.4643
26 | 2656562.9143 | 1232188.1179 | 2656551.8208 | 1232186.5447 | 2656537.5247 | 1232181.8219
27 | 2656562.9143 | 1232188.1179 | 2656568.0257 | 1232193.6701 | 2656571.6484 | 1232199.6973
28 | 2656562.9143 | 1232188.1179 | 2656574.2212 | 1232152.7933
29 | 2656574.2212 | 1232152.7933 | 2656575.614 | 1232148.4421
30 | 2656575.614 | 1232148.4421 | 2656579.9589 | 1232134.8679 | 2656580.6916 | 1232131.9269
31 | 2656585.4922 | 1232228.9368 | 2656594.3468 | 1232228.6542 | 2656596.7726 | 1232232.4109
32 | 2656585.8302 | 1232110.513 | 2656583.1396 | 1232122.1011 | 2656580.6916 | 1232131.9269
33 | 2656580.6916 | 1232131.9269 | 2656655.8855 | 1232150.8454
34 | 2656585.8302 | 1232110.513 | 2656595.9234 | 1232067.0428 | 2656599.0553 | 1232042.2138
35 | 2656660.4848 | 1232132.2661 | 2656655.8855 | 1232150.8454
36 | 2656658.3048 | 1232151.4709 | 2656655.8855 | 1232150.8454
37 | 2656396.7163 | 1232085.1058 | 2656394.9326 | 1232071.2047
38 | 2656415.1445 | 1232107.4142 | 2656412.5823 | 1232107.4643
39 | 2656394.9326 | 1232071.2047 | 2656394.9048 | 1232070.9886
40 | 2656415.1445 | 1232107.4142 | 2656423.8229 | 1232107.2447 | 2656433.5352 | 1232107.126
41 | 2656445.3774 | 1232104.4696 | 2656440.2113 | 1232107.0445 | 2656433.5352 | 1232107.126
42 | 2656626.5494 | 1231747.1265 | 2656615.5241 | 1231758.9976 | 2656607.5419 | 1231770.8169
43 | 2656626.5494 | 1231747.1265 | 2656637.0657 | 1231735.8033
44 | 2656603.0032 | 1231777.5373 | 2656607.5419 | 1231770.8169
45 | 2656643.164 | 1231729.2372 | 2656637.0657 | 1231735.8033
46 | 2656603.0032 | 1231777.5373 | 2656601.6606 | 1231779.5254
47 | 2656652.6456 | 1231719.0282 | 2656643.164 | 1231729.2372
48 | 2656587.4874 | 1231800.8027 | 2656601.2143 | 1231780.1862 | 2656601.6606 | 1231779.5254
49 | 2656666.6196 | 1231703.9821 | 2656652.6456 | 1231719.0282
50 | 2656574.3791 | 1231820.4901 | 2656587.4874 | 1231800.8027
51 | 2656646.7833 | 1231806.0144 | 2656652.1995 | 1231815.372 | 2656654.1299 | 1231823.5922
52 | 2656643.3934 | 1231860.5728 | 2656654.1299 | 1231823.5922
53 | 2656666.6196 | 1231703.9821 | 2656672.978 | 1231696.3266 | 2656683.3973 | 1231671.72
54 | 2656666.6196 | 1231703.9821 | 2656658.0844 | 1231684.2649
55 | 2656666.6196 | 1231703.9821 | 2656679.4944 | 1231715.7901
56 | 2656574.3791 | 1231820.4901 | 2656557.5316 | 1231828.2683 | 2656540.5201 | 1231840.5478 | 2656527.1559 | 1231852.4014
57 | 2656574.3791 | 1231820.4901 | 2656579.2156 | 1231828.7081 | 2656579.7795 | 1231832.0531
58 | 2656683.3973 | 1231671.72 | 2656692.0575 | 1231651.2676
59 | 2656658.0844 | 1231684.2649 | 2656654.9048 | 1231676.9197 | 2656651.574 | 1231668.8495 | 2656646.0998 | 1231660.8918
60 | 2656691.7098 | 1231721.3101 | 2656679.4944 | 1231715.7901
61 | 2656718.6357 | 1232015.9073 | 2656727.12 | 1231979.7045
62 | 2656718.6357 | 1232015.9073 | 2656712.3223 | 1232042.847 | 2656723.2347 | 1232053.1021 | 2656724.6379 | 1232056.7296
63 | 2656727.12 | 1231979.7045 | 2656729.8965 | 1231967.8572
64 | 2656787.9488 | 1231927.8278 | 2656729.8965 | 1231967.8572
65 | 2656602.0072 | 1232011.8429 | 2656613.367 | 1231996.619 | 2656613.367 | 1231996.619
66 | 2656613.367 | 1231996.619 | 2656623.651 | 1231967.9428 | 2656625.057 | 1231958.8421
67 | 2656600.5202 | 1232006.5698 | 2656602.0072 | 1232011.8429
68 | 2656602.0072 | 1232011.8429 | 2656601.9846 | 1232018.9917 | 2656600.6914 | 1232029.2436
69 | 2656627.8231 | 1231940.938 | 2656625.057 | 1231958.8421
70 | 2656805.1185 | 1231913.2823 | 2656793.3744 | 1231910.8019 | 2656788.8021 | 1231912.2259 | 2656788.673 | 1231914.6484 | 2656788.3791 | 1231920.0491 | 2656787.9488 | 1231927.8278
71 | 2656805.1185 | 1231913.2823 | 2656818.808 | 1231847.5437
72 | 2656600.6914 | 1232029.2436 | 2656599.0553 | 1232042.2138
73 | 2656660.4848 | 1232132.2661 | 2656695.2561 | 1232141.2613
74 | 2656660.4848 | 1232132.2661 | 2656661.0658 | 1232131.1081
75 | 2656672.6294 | 1232108.0577 | 2656661.0658 | 1232131.1081
76 | 2656672.6294 | 1232108.0577 | 2656688.1962 | 1232077.0279
77 | 2656693.3661 | 1232043.0998 | 2656688.1962 | 1232077.0279
78 | 2656582.8277 | 1231895.1252 | 2656583.1144 | 1231886.8938 | 2656582.6278 | 1231857.2392
79 | 2656582.8277 | 1231895.1252 | 2656582.3636 | 1231908.4477
80 | 2656582.6129 | 1231856.3351 | 2656582.6278 | 1231857.2392
81 | 2656582.3636 | 1231908.4477 | 2656581.6892 | 1231927.8071
82 | 2656582.0069 | 1231845.2636 | 2656582.477 | 1231848.0516 | 2656582.6129 | 1231856.3351
83 | 2656581.6892 | 1231927.8071 | 2656581.2076 | 1231941.6331 | 2656582.0195 | 1231951.0024 | 2656582.3331 | 1231952.2755
84 | 2656582.0069 | 1231845.2636 | 2656580.5961 | 1231836.8962
85 | 2656591.2126 | 1231980.2546 | 2656584.8192 | 1231962.3697 | 2656582.3331 | 1231952.2755
86 | 2656579.7795 | 1231832.0531 | 2656580.5961 | 1231836.8962
87 | 2656600.5202 | 1232006.5698 | 2656597.4175 | 1231997.6123 | 2656591.2126 | 1231980.2546
88 | 2656600.5202 | 1232006.5698 | 2656587.5347 | 1232000.1281
89 | 2656527.1559 | 1231852.4014 | 2656523.0083 | 1231856.0802
90 | 2656578.4213 | 1231996.5597 | 2656586.2152 | 1231999.4735 | 2656587.5347 | 1232000.1281
91 | 2656506.1361 | 1232083.3443 | 2656507.2699 | 1232080.1112
92 | 2656502.0457 | 1232100.0048 | 2656504.9121 | 1232086.8347 | 2656506.1361 | 1232083.3443
93 | 2656513.5919 | 1232069.9173 | 2656507.5662 | 1232079.2661 | 2656507.2699 | 1232080.1112
94 | 2656513.5919 | 1232069.9173 | 2656513.5919 | 1232069.9173 | 2656524.502 | 1232058.9473 | 2656534.2824 | 1232054.4929 | 2656538.1123 | 1232051.4941 | 2656540.436 | 1232044.8476
95 | 2656540.436 | 1232044.8476 | 2656542.3391 | 1232039.4042 | 2656538.9636 | 1232026.4749 | 2656541.0178 | 1232018.3003 | 2656543.8431 | 1232011.8243
96 | 2656554.4179 | 1231987.5857 | 2656543.8431 | 1232011.8243
97 | 2656554.4179 | 1231987.5857 | 2656536.5047 | 1231980.8777
98 | 2656554.4179 | 1231987.5857 | 2656578.4213 | 1231996.5597
99 | 2656636.0198 | 1231890.7313 | 2656638.3919 | 1231881.0292
100 | 2656636.0198 | 1231890.7313 | 2656635.4742 | 1231892.9627 | 2656630.8678 | 1231921.502
101 | 2656643.3934 | 1231860.5728 | 2656638.3919 | 1231881.0292
102 | 2656627.8231 | 1231940.938 | 2656629.8892 | 1231927.5651 | 2656630.8678 | 1231921.502
103 | 2656406.2187 | 1231977.0161 | 2656399.5267 | 1231999.3438
104 | 2656406.2187 | 1231977.0161 | 2656408.974 | 1231972.2748
105 | 2656410.6465 | 1231969.3968 | 2656408.974 | 1231972.2748
106 | 2656410.6465 | 1231969.3968 | 2656422.0001 | 1231949.8594 | 2656431.2763 | 1231939.0347
107 | 2656454.073 | 1231914.0037 | 2656442.2156 | 1231926.2693 | 2656431.2763 | 1231939.0347
108 | 2656745.7718 | 1231718.6461 | 2656746.7504 | 1231731.8941
109 | 2656785.1361 | 1231666.5771 | 2656767.975 | 1231674.6074 | 2656758.2548 | 1231682.9756 | 2656752.7553 | 1231689.4828 | 2656746.6864 | 1231699.3201 | 2656745.0468 | 1231707.6543 | 2656745.674 | 1231717.3221 | 2656745.7718 | 1231718.6461
110 | 2656747.82 | 1231746.3724 | 2656746.7504 | 1231731.8941
111 | 2656785.1361 | 1231666.5771 | 2656800.6642 | 1231663.8125 | 2656807.6934 | 1231663.4043
112 | 2656747.82 | 1231746.3724 | 2656740.54 | 1231743.0395
113 | 2656807.6934 | 1231663.4043 | 2656818.7508 | 1231662.7623 | 2656824.611 | 1231666.0649 | 2656825.4167 | 1231687.077
114 | 2656740.54 | 1231743.0395 | 2656704.986 | 1231726.7624 | 2656703.9278 | 1231726.3278
115 | 2656826.0015 | 1231702.3281 | 2656825.4167 | 1231687.077
116 | 2656828.6359 | 1231771.0265 | 2656827.4478 | 1231740.0439
117 | 2656819.9923 | 1231841.8562 | 2656836.5758 | 1231773.0258 | 2656828.6359 | 1231771.0265
118 | 2656826.0015 | 1231702.3281 | 2656827.4478 | 1231740.0439
119 | 2656819.9923 | 1231841.8562 | 2656818.808 | 1231847.5437
120 | 2656691.7098 | 1231721.3101 | 2656703.9278 | 1231726.3278
121 | 2656691.7098 | 1231721.3101 | 2656687.6321 | 1231736.7701 | 2656686.6967 | 1231749.7317
122 | 2656488.4124 | 1231883.5747 | 2656485.391 | 1231885.9755 | 2656462.4514 | 1231905.3368 | 2656454.073 | 1231914.0037
123 | 2656488.4124 | 1231883.5747 | 2656493.2535 | 1231879.7281
124 | 2656509.0219 | 1231867.1989 | 2656493.2535 | 1231879.7281
125 | 2656509.0219 | 1231867.1989 | 2656510.2843 | 1231866.1954
126 | 2656510.2843 | 1231866.1954 | 2656523.0083 | 1231856.0802 | 2656523.0083 | 1231856.0802
127 | 2656693.239 | 1231648.4773 | 2656692.0575 | 1231651.2676
128 | 2656639.2301 | 1231650.9055 | 2656646.0998 | 1231660.8918
129 | 2656703.3246 | 1231624.6586 | 2656693.239 | 1231648.4773
130 | 2656633.2738 | 1231642.247 | 2656639.2301 | 1231650.9055
131 | 2656703.3246 | 1231624.6586 | 2656708.881 | 1231628.0582 | 2656720.4453 | 1231633.3602
132 | 2656703.3246 | 1231624.6586 | 2656704.9875 | 1231621.5572
133 | 2656633.2738 | 1231642.247 | 2656589.0256 | 1231596.0628
134 | 2656633.2738 | 1231642.247 | 2656619.1437 | 1231651.7912
135 | 2656748.2557 | 1231643.6104 | 2656736.9899 | 1231640.9456 | 2656720.4453 | 1231633.3602
136 | 2656717.411 | 1231598.3871 | 2656704.9875 | 1231621.5572
137 | 2656717.411 | 1231598.3871 | 2656743.1217 | 1231602.1691
138 | 2656717.411 | 1231598.3871 | 2656719.0973 | 1231595.2443
139 | 2656730.1481 | 1231574.6488 | 2656719.0973 | 1231595.2443
140 | 2656576.2149 | 1231575.8835 | 2656589.0256 | 1231596.0628
141 | 2656619.1437 | 1231651.7912 | 2656607.4714 | 1231659.6753
142 | 2656568.416 | 1231559.8213 | 2656576.2149 | 1231575.8835
143 | 2656576.2149 | 1231575.8835 | 2656567.561 | 1231584.8828
144 | 2656600.9568 | 1231664.0757 | 2656607.4714 | 1231659.6753
145 | 2656568.416 | 1231559.8213 | 2656567.3259 | 1231547.0471 | 2656568.3359 | 1231529.2453 | 2656572.3395 | 1231518.2466
146 | 2656568.416 | 1231559.8213 | 2656556.7554 | 1231558.0426 | 2656532.8471 | 1231552.4895 | 2656529.538 | 1231551.87
147 | 2656552.3735 | 1231600.2841 | 2656555.9688 | 1231596.9379 | 2656567.561 | 1231584.8828
148 | 2656667.5083 | 1231433.5944 | 2656663.4204 | 1231442.9615 | 2656658.2727 | 1231452.3131
149 | 2656638.3844 | 1231479.4242 | 2656653.448 | 1231461.0781 | 2656658.2727 | 1231452.3131
150 | 2656638.3844 | 1231479.4242 | 2656636.0306 | 1231477.1997
151 | 2656638.3844 | 1231479.4242 | 2656652.3529 | 1231492.5546 | 2656659.3337 | 1231496.6904
152 | 2656626.0812 | 1231467.7971 | 2656636.0306 | 1231477.1997
153 | 2656609.0291 | 1231449.3922 | 2656617.016 | 1231459.2301 | 2656626.0812 | 1231467.7971
154 | 2656609.0291 | 1231449.3922 | 2656590.7774 | 1231479.2087
155 | 2656609.0291 | 1231449.3922 | 2656603.3283 | 1231430.9149 | 2656597.4359 | 1231417.4391 | 2656595.9028 | 1231416.1904 | 2656581.3616 | 1231404.3222 | 2656571.2969 | 1231399.8609
156 | 2656609.0291 | 1231449.3922 | 2656617.3097 | 1231441.9106 | 2656626.0592 | 1231425.7502 | 2656634.3856 | 1231407.1063 | 2656635.0823 | 1231402.6736
157 | 2656751.3028 | 1231518.7813 | 2656730.6855 | 1231514.9148
158 | 2656730.1481 | 1231574.6488 | 2656735.4872 | 1231563.5259 | 2656748.0233 | 1231530.7133 | 2656751.3028 | 1231518.7813
159 | 2656590.7774 | 1231479.2087 | 2656585.7661 | 1231487.3953 | 2656576.1279 | 1231507.839 | 2656572.3395 | 1231518.2466
160 | 2656571.2969 | 1231399.8609 | 2656566.8407 | 1231397.8857
161 | 2656730.1481 | 1231574.6488 | 2656715.0785 | 1231567.8634
162 | 2656469.6076 | 1231547.376 | 2656479.1818 | 1231546.398 | 2656487.5062 | 1231546.8549
163 | 2656498.0408 | 1231547.4331 | 2656487.5062 | 1231546.8549
164 | 2656498.0408 | 1231547.4331 | 2656509.0722 | 1231548.0385 | 2656529.538 | 1231551.87
165 | 2656700.0748 | 1231565.2116 | 2656705.905 | 1231563.7329 | 2656715.0785 | 1231567.8634
166 | 2656552.3735 | 1231600.2841 | 2656530.0366 | 1231621.0736
167 | 2656541.1334 | 1231386.4943 | 2656560.9319 | 1231395.2665 | 2656566.8407 | 1231397.8857
168 | 2656535.6792 | 1231627.2653 | 2656530.0366 | 1231621.0736 | 2656530.0366 | 1231621.0736
169 | 2656538.4382 | 1231630.2927 | 2656535.6792 | 1231627.2653

## bus_geodata
| x | y | coords
0 | 2656481.8845 | 1232224.0549
1 | 2656491.6152 | 1232204.1513
2 | 2656476.1145 | 1232235.8572
3 | 2656500.0681 | 1232186.8611
4 | 2656505.0593 | 1232232.2325
5 | 2656500.0942 | 1232186.8077
6 | 2656508.2472 | 1232170.1311
7 | 2656546.3221 | 1232224.8252
8 | 2656560.0069 | 1232222.3686
9 | 2656431.2031 | 1232182.8277
10 | 2656441.5701 | 1232164.3089
11 | 2656512.2896 | 1232171.7672
12 | 2656490.7681 | 1232160.8046
13 | 2656571.372 | 1232220.7861
14 | 2656475.7269 | 1232152.7789
15 | 2656454.3012 | 1232141.5671
16 | 2656449.2103 | 1232138.9042
17 | 2656442.1677 | 1232163.2414
18 | 2656400.398 | 1232128.6429
19 | 2656516.39 | 1232173.4267
20 | 2656400.1987 | 1232128.6344
21 | 2656525.8674 | 1232177.2623
22 | 2656399.3067 | 1232107.7236
23 | 2656537.5247 | 1232181.8219
24 | 2656562.9143 | 1232188.1179
25 | 2656571.6484 | 1232199.6973
26 | 2656574.2212 | 1232152.7933
27 | 2656575.614 | 1232148.4421
28 | 2656585.4922 | 1232228.9368
29 | 2656580.6916 | 1232131.9269
30 | 2656596.7726 | 1232232.4109
31 | 2656585.8302 | 1232110.513
32 | 2656655.8855 | 1232150.8454
33 | 2656396.7163 | 1232085.1058
34 | 2656412.5823 | 1232107.4643
35 | 2656394.9326 | 1232071.2047
36 | 2656415.1445 | 1232107.4142
37 | 2656394.9048 | 1232070.9886
38 | 2656433.5352 | 1232107.126
39 | 2656626.5494 | 1231747.1265
40 | 2656607.5419 | 1231770.8169
41 | 2656637.0657 | 1231735.8033
42 | 2656603.0032 | 1231777.5373
43 | 2656643.164 | 1231729.2372
44 | 2656601.6606 | 1231779.5254
45 | 2656652.6456 | 1231719.0282
46 | 2656587.4874 | 1231800.8027
47 | 2656646.7833 | 1231806.0144
48 | 2656654.1299 | 1231823.5922
49 | 2656666.6196 | 1231703.9821
50 | 2656574.3791 | 1231820.4901
51 | 2656683.3973 | 1231671.72
52 | 2656658.0844 | 1231684.2649
53 | 2656679.4944 | 1231715.7901
54 | 2656718.6357 | 1232015.9073
55 | 2656727.12 | 1231979.7045
56 | 2656724.6379 | 1232056.7296
57 | 2656729.8965 | 1231967.8572
58 | 2656613.367 | 1231996.619
59 | 2656602.0072 | 1232011.8429
60 | 2656625.057 | 1231958.8421
61 | 2656787.9488 | 1231927.8278
62 | 2656805.1185 | 1231913.2824
63 | 2656599.0553 | 1232042.2138
64 | 2656600.6914 | 1232029.2436
65 | 2656695.2561 | 1232141.2613
66 | 2656660.4848 | 1232132.2661
67 | 2656658.3048 | 1232151.4709
68 | 2656661.0658 | 1232131.1081
69 | 2656672.6294 | 1232108.0577
70 | 2656688.1962 | 1232077.0279
71 | 2656582.8277 | 1231895.1252
72 | 2656582.6278 | 1231857.2392
73 | 2656582.3636 | 1231908.4477
74 | 2656582.6129 | 1231856.3351
75 | 2656581.6892 | 1231927.8071
76 | 2656582.0069 | 1231845.2636
77 | 2656582.3331 | 1231952.2755
78 | 2656580.5961 | 1231836.8962
79 | 2656591.2126 | 1231980.2546
80 | 2656579.7795 | 1231832.0531
81 | 2656600.5202 | 1232006.5698
82 | 2656527.1559 | 1231852.4014
83 | 2656693.3661 | 1232043.0998
84 | 2656587.5347 | 1232000.1281
85 | 2656506.1361 | 1232083.3443
86 | 2656507.2699 | 1232080.1112
87 | 2656502.0457 | 1232100.0048
88 | 2656513.5919 | 1232069.9173
89 | 2656540.436 | 1232044.8476
90 | 2656543.8431 | 1232011.8243
91 | 2656554.4179 | 1231987.5857
92 | 2656636.0198 | 1231890.7313
93 | 2656638.3919 | 1231881.0292
94 | 2656630.8678 | 1231921.502
95 | 2656643.3934 | 1231860.5728
96 | 2656627.8231 | 1231940.938
97 | 2656399.5267 | 1231999.3438
98 | 2656406.2187 | 1231977.0161
99 | 2656408.974 | 1231972.2748
100 | 2656410.6465 | 1231969.3968
101 | 2656431.2763 | 1231939.0347
102 | 2656445.3774 | 1232104.4696
103 | 2656745.7718 | 1231718.6461
104 | 2656746.7504 | 1231731.8941
105 | 2656785.1361 | 1231666.5771
106 | 2656747.82 | 1231746.3724
107 | 2656807.6934 | 1231663.4043
108 | 2656740.54 | 1231743.0395
109 | 2656825.4167 | 1231687.077
110 | 2656828.6359 | 1231771.0265
111 | 2656827.4478 | 1231740.0439
112 | 2656819.9923 | 1231841.8562
113 | 2656703.9278 | 1231726.3278
114 | 2656826.0015 | 1231702.3281
115 | 2656818.808 | 1231847.5437
116 | 2656691.7098 | 1231721.3101
117 | 2656488.4124 | 1231883.5747
118 | 2656454.073 | 1231914.0037
119 | 2656493.2535 | 1231879.7281
120 | 2656509.0219 | 1231867.1989
121 | 2656510.2843 | 1231866.1954
122 | 2656523.0083 | 1231856.0802
123 | 2656536.5047 | 1231980.8777
124 | 2656578.4213 | 1231996.5597
125 | 2656686.6967 | 1231749.7317
126 | 2656692.0575 | 1231651.2676
127 | 2656646.0998 | 1231660.8918
128 | 2656693.239 | 1231648.4773
129 | 2656639.2301 | 1231650.9055
130 | 2656703.3246 | 1231624.6586
131 | 2656633.2738 | 1231642.247
132 | 2656720.4453 | 1231633.3602
133 | 2656704.9875 | 1231621.5572
134 | 2656748.2557 | 1231643.6104
135 | 2656717.411 | 1231598.3871
136 | 2656743.1217 | 1231602.1691
137 | 2656719.0973 | 1231595.2443
138 | 2656589.0256 | 1231596.0628
139 | 2656619.1437 | 1231651.7912
140 | 2656576.2149 | 1231575.8835
141 | 2656607.4714 | 1231659.6753
142 | 2656568.416 | 1231559.8213
143 | 2656567.561 | 1231584.8828
144 | 2656600.9568 | 1231664.0757
145 | 2656658.2727 | 1231452.3131
146 | 2656667.5083 | 1231433.5944
147 | 2656638.3844 | 1231479.4242
148 | 2656636.0306 | 1231477.1997
149 | 2656659.3337 | 1231496.6904
150 | 2656626.0812 | 1231467.7971
151 | 2656609.0291 | 1231449.3922
152 | 2656730.6855 | 1231514.9148
153 | 2656751.3028 | 1231518.7813
154 | 2656590.7774 | 1231479.2087
155 | 2656571.2969 | 1231399.8609
156 | 2656635.0823 | 1231402.6736
157 | 2656730.1481 | 1231574.6488
158 | 2656469.6076 | 1231547.376
159 | 2656487.5062 | 1231546.8549
160 | 2656498.0408 | 1231547.4331
161 | 2656529.538 | 1231551.87
162 | 2656572.3395 | 1231518.2466
163 | 2656715.0785 | 1231567.8634
164 | 2656700.0748 | 1231565.2116
165 | 2656552.3735 | 1231600.2841
166 | 2656566.8407 | 1231397.8857
167 | 2656541.1334 | 1231386.4943
168 | 2656535.6792 | 1231627.2653
169 | 2656530.0366 | 1231621.0736
170 | 2656538.4382 | 1231630.2927
171 | 2656600.5202 | 1232006.5698

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1