## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_420-12_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_420-12_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_420-12_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_420-12_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_420-12_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_420-12_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_420-12_0_4_node_79 | 0.4 | n |  | TRUE
7 | bus_LV_420-12_0_4_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_420-12_0_4_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_420-12_0_4_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_420-12_0_4_node_78 | 0.4 | n |  | TRUE
11 | bus_LV_420-12_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_420-12_0_4_node_76 | 0.4 | n |  | TRUE
13 | bus_LV_420-12_0_4_node_75 | 0.4 | n |  | TRUE
14 | bus_LV_420-12_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_420-12_0_4_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_420-12_0_4_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_420-12_0_4_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_420-12_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_420-12_0_4_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_420-12_0_4_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_420-12_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_420-12_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_420-12_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_420-12_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_420-12_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_420-12_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_420-12_0_4_node_32 | 0.4 | n |  | TRUE
28 | bus_LV_420-12_0_4_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_420-12_0_4_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_420-12_0_4_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_420-12_0_4_node_71 | 0.4 | n |  | TRUE
32 | bus_LV_420-12_0_4_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_420-12_0_4_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_420-12_0_4_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_420-12_0_4_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_420-12_0_4_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_420-12_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_420-12_0_4_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_420-12_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_420-12_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_420-12_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_420-12_0_4_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_420-12_0_4_node_57 | 0.4 | n |  | TRUE
44 | bus_LV_420-12_0_4_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_420-12_0_4_node_33 | 0.4 | n |  | TRUE
46 | bus_LV_420-12_0_4_node_34 | 0.4 | n |  | TRUE
47 | bus_LV_420-12_0_4_node_35 | 0.4 | n |  | TRUE
48 | bus_LV_420-12_0_4_node_36 | 0.4 | n |  | TRUE
49 | bus_LV_420-12_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_420-12_0_4_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_420-12_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_420-12_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_420-12_0_4_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_420-12_0_4_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_420-12_0_4_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_420-12_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_420-12_0_4_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_420-12_0_4_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_420-12_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_420-12_0_4_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_420-12_0_4_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_420-12_0_4_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_420-12_0_4_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_420-12_0_4_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_420-12_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_420-12_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_420-12_0_4_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_420-12_0_4_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_420-12_0_4_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_420-12_0_4_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_420-12_0_4_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_420-12_0_4_node_63 | 0.4 | n |  | TRUE
73 | bus_LV_420-12_0_4_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_420-12_0_4_node_66 | 0.4 | n |  | TRUE
75 | bus_LV_420-12_0_4_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_420-12_0_4_node_68 | 0.4 | n |  | TRUE
77 | bus_MV_446_0_node_115 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_420-12_0_4_load_0 | 0 | 0.0051337 | 0.0012866 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_420-12_0_4_load_1 | 1 | 0.0057147 | 0.0014322 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_420-12_0_4_load_79 | 6 | 0.0071752 | 0.0017983 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_420-12_0_4_load_15 | 9 | 0.0071811 | 0.0017998 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_420-12_0_4_load_78 | 10 | 0.012052 | 0.0030204 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_420-12_0_4_load_76 | 12 | 0.0043697 | 0.0010951 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_420-12_0_4_load_22 | 15 | 0.0055712 | 0.0013963 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_420-12_0_4_load_13 | 16 | 0.0087641 | 0.0021965 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_420-12_0_4_load_74 | 17 | 0.010333 | 0.0025896 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_420-12_0_4_load_12 | 18 | 0.0058452 | 0.0014649 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_420-12_0_4_load_7 | 19 | 0.0059576 | 0.0014931 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_420-12_0_4_load_10 | 21 | 0.0060147 | 0.0015074 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_420-12_0_4_load_11 | 22 | 0.005884 | 0.0014747 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_420-12_0_4_load_14 | 23 | 0.0057118 | 0.0014315 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_420-12_0_4_load_16 | 24 | 0.01061 | 0.002659 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_420-12_0_4_load_17 | 25 | 0.0056353 | 0.0014123 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_420-12_0_4_load_19 | 26 | 0.0067342 | 0.0016878 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_420-12_0_4_load_27 | 28 | 0.0065839 | 0.0016501 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_420-12_0_4_load_20 | 29 | 0.0083549 | 0.0020939 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_420-12_0_4_load_70 | 30 | 0.0064543 | 0.0016176 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_420-12_0_4_load_71 | 31 | 0.026095 | 0.0065401 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_420-12_0_4_load_21 | 33 | 0.0091393 | 0.0022905 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_420-12_0_4_load_23 | 34 | 0.012239 | 0.0030673 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_420-12_0_4_load_51 | 35 | 0.0050817 | 0.0012736 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_420-12_0_4_load_38 | 36 | 0.0046553 | 0.0011667 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_420-12_0_4_load_26 | 37 | 0.0058406 | 0.0014638 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_420-12_0_4_load_28 | 39 | 0.007147 | 0.0017912 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_420-12_0_4_load_29 | 40 | 0.0062074 | 0.0015557 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_420-12_0_4_load_30 | 41 | 0.0045798 | 0.0011478 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_420-12_0_4_load_31 | 42 | 0.0056597 | 0.0014184 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_420-12_0_4_load_37 | 44 | 0.0095742 | 0.0023995 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_420-12_0_4_load_33 | 45 | 0.0069533 | 0.0017427 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_420-12_0_4_load_34 | 46 | 0.00668 | 0.0016742 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_420-12_0_4_load_35 | 47 | 0.01079 | 0.0027042 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_420-12_0_4_load_36 | 48 | 0.0056924 | 0.0014267 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_420-12_0_4_load_39 | 49 | 0.0044919 | 0.0011258 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_420-12_0_4_load_40 | 50 | 0.0046795 | 0.0011728 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_420-12_0_4_load_42 | 52 | 0.0045482 | 0.0011399 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_420-12_0_4_load_43 | 53 | 0.0090119 | 0.0022586 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_420-12_0_4_load_44 | 54 | 0.0032912 | 0.00082485 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_420-12_0_4_load_45 | 55 | 0.0063018 | 0.0015794 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_420-12_0_4_load_48 | 56 | 0.0076081 | 0.0019068 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_420-12_0_4_load_46 | 57 | 0.0058768 | 0.0014729 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_420-12_0_4_load_47 | 58 | 0.0045822 | 0.0011484 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_420-12_0_4_load_52 | 59 | 0.004088 | 0.0010245 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_420-12_0_4_load_49 | 60 | 0.0041463 | 0.0010392 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_420-12_0_4_load_50 | 61 | 0.0031213 | 0.00078226 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_420-12_0_4_load_53 | 62 | 0.0028868 | 0.0007235 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_420-12_0_4_load_58 | 64 | 0.025237 | 0.006325 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_420-12_0_4_load_55 | 65 | 0.017256 | 0.0043248 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_420-12_0_4_load_64 | 67 | 0.0064047 | 0.0016052 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_420-12_0_4_load_61 | 68 | 0.0025094 | 0.00062892 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_420-12_0_4_load_59 | 70 | 0.016743 | 0.0041961 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_420-12_0_4_load_60 | 71 | 0.0037031 | 0.00092808 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_420-12_0_4_load_65 | 73 | 0.015927 | 0.0039916 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_420-12_0_4_load_67 | 75 | 0.0099111 | 0.002484 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_420-12_0_4_load_68 | 76 | 0.0030039 | 0.00075284 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 36 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_420-12_0_4_line_0 |  | 0 | 1 | 0.024995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_420-12_0_4_line_1 |  | 0 | 2 | 0.0054852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_420-12_0_4_line_2 |  | 1 | 3 | 0.017474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_420-12_0_4_line_3 |  | 2 | 4 | 0.008626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_420-12_0_4_line_4 |  | 3 | 5 | 0.07819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_420-12_0_4_line_5 |  | 4 | 6 | 0.007563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_420-12_0_4_line_6 |  | 5 | 10 | 0.014737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_420-12_0_4_line_7 |  | 5 | 11 | 0.002212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_420-12_0_4_line_8 |  | 5 | 7 | 0.077561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_420-12_0_4_line_9 |  | 7 | 8 | 0.055344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_420-12_0_4_line_10 |  | 7 | 9 | 0.018772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_420-12_0_4_line_11 |  | 8 | 14 | 0.049518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_420-12_0_4_line_12 |  | 8 | 15 | 0.021726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_420-12_0_4_line_13 |  | 9 | 16 | 0.00035618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_420-12_0_4_line_14 |  | 11 | 18 | 0.012352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_420-12_0_4_line_15 |  | 11 | 19 | 0.01239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_420-12_0_4_line_16 |  | 12 | 13 | 0.011669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_420-12_0_4_line_17 |  | 13 | 17 | 0.061726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_420-12_0_4_line_18 |  | 14 | 27 | 0.063779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_420-12_0_4_line_19 |  | 14 | 28 | 0.021902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_420-12_0_4_line_20 |  | 15 | 29 | 0.0020731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_420-12_0_4_line_21 |  | 16 | 23 | 0.023077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_420-12_0_4_line_22 |  | 17 | 32 | 0.0071281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_420-12_0_4_line_23 |  | 19 | 20 | 0.0099549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_420-12_0_4_line_24 |  | 20 | 21 | 0.013492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_420-12_0_4_line_25 |  | 20 | 22 | 0.012391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_420-12_0_4_line_26 |  | 23 | 24 | 0.0021632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_420-12_0_4_line_27 |  | 24 | 25 | 0.021643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_420-12_0_4_line_28 |  | 25 | 26 | 0.0042689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_420-12_0_4_line_29 |  | 27 | 35 | 0.0228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_420-12_0_4_line_30 |  | 27 | 36 | 0.016898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_420-12_0_4_line_31 |  | 28 | 37 | 0.00051334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_420-12_0_4_line_32 |  | 29 | 33 | 0.027902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_420-12_0_4_line_33 |  | 30 | 31 | 0.063276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_420-12_0_4_line_34 |  | 30 | 32 | 0.025496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_420-12_0_4_line_35 |  | 31 | 38 | 0.042673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_420-12_0_4_line_36 |  | 33 | 34 | 0.017505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_420-12_0_4_line_37 |  | 35 | 43 | 0.097929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_420-12_0_4_line_38 |  | 36 | 44 | 0.0062032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_420-12_0_4_line_39 |  | 37 | 39 | 0.026227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_420-12_0_4_line_40 |  | 38 | 71 | 0.21825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_420-12_0_4_line_41 |  | 39 | 40 | 0.0033557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_420-12_0_4_line_42 |  | 40 | 41 | 0.02431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_420-12_0_4_line_43 |  | 41 | 42 | 0.00023198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_420-12_0_4_line_44 |  | 43 | 64 | 0.021556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_420-12_0_4_line_45 |  | 43 | 63 | 0.048718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_420-12_0_4_line_46 |  | 44 | 47 | 0.025253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_420-12_0_4_line_47 |  | 45 | 46 | 0.024739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_420-12_0_4_line_48 |  | 45 | 47 | 0.00069181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_420-12_0_4_line_49 |  | 46 | 48 | 0.00066567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_420-12_0_4_line_50 |  | 49 | 50 | 0.00089492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_420-12_0_4_line_51 |  | 49 | 51 | 0.015065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_420-12_0_4_line_52 |  | 50 | 52 | 0.011319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_420-12_0_4_line_53 |  | 51 | 53 | 0.019765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_420-12_0_4_line_54 |  | 51 | 54 | 0.019772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_420-12_0_4_line_55 |  | 52 | 55 | 0.009851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_420-12_0_4_line_56 |  | 54 | 56 | 0.00103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_420-12_0_4_line_57 |  | 55 | 57 | 0.0223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_420-12_0_4_line_58 |  | 56 | 58 | 0.011706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_420-12_0_4_line_59 |  | 57 | 59 | 0.022135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_420-12_0_4_line_60 |  | 58 | 60 | 0.021199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_420-12_0_4_line_61 |  | 60 | 61 | 0.021209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_420-12_0_4_line_62 |  | 61 | 62 | 0.020378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_420-12_0_4_line_63 |  | 62 | 63 | 0.01779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_420-12_0_4_line_64 |  | 63 | 66 | 0.097553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_420-12_0_4_line_65 |  | 63 | 65 | 0.0099811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_420-12_0_4_line_66 |  | 64 | 70 | 0.037669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_420-12_0_4_line_67 |  | 66 | 67 | 0.02789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_420-12_0_4_line_68 |  | 66 | 68 | 0.033378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_420-12_0_4_line_69 |  | 68 | 69 | 0.073902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_420-12_0_4_line_70 |  | 69 | 72 | 0.088362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_420-12_0_4_line_71 |  | 70 | 71 | 0.019224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_420-12_0_4_line_72 |  | 72 | 73 | 0.082304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_420-12_0_4_line_73 |  | 73 | 74 | 0.022306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_420-12_0_4_line_74 |  | 74 | 75 | 0.024886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_420-12_0_4_line_75 |  | 74 | 76 | 0.099829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_420-12_0_4_trafo_38 | 0.63 MVA 20/0.4 kV | 77 | 36 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2609765.3865 | 1215661.1437 | 2609749.0096 | 1215642.2613
1 | 2609768.9805 | 1215665.2875 | 2609765.3865 | 1215661.1437
2 | 2609737.5602 | 1215629.0604 | 2609749.0096 | 1215642.2613
3 | 2609775.9597 | 1215668.9787 | 2609772.1331 | 1215668.928 | 2609768.9805 | 1215665.2875
4 | 2609737.5602 | 1215629.0604 | 2609783.2087 | 1215600.3739 | 2609799.169 | 1215618.6659
5 | 2609775.9597 | 1215668.9787 | 2609780.8399 | 1215674.7677
6 | 2609799.169 | 1215618.6659 | 2609788.2725 | 1215628.6204
7 | 2609800.6241 | 1215620.3359 | 2609799.169 | 1215618.6659
8 | 2609821.0818 | 1215562.8924 | 2609783.2087 | 1215600.3739 | 2609799.169 | 1215618.6659
9 | 2609821.0818 | 1215562.8924 | 2609861.4391 | 1215524.9038
10 | 2609821.0818 | 1215562.8924 | 2609833.1783 | 1215577.2472
11 | 2609899.7816 | 1215493.438 | 2609861.4391 | 1215524.9038
12 | 2609861.4391 | 1215524.9038 | 2609875.3629 | 1215541.5815
13 | 2609833.1783 | 1215577.2472 | 2609833.4078 | 1215577.5195
14 | 2609809.6202 | 1215611.8458 | 2609800.6241 | 1215620.3359
15 | 2609800.6241 | 1215620.3359 | 2609808.7722 | 1215629.6699
16 | 2609644.1637 | 1215411.1531 | 2609632.9739 | 1215414.4622
17 | 2609644.1637 | 1215411.1531 | 2609657.1999 | 1215407.0161 | 2609675.1104 | 1215398.4179 | 2609696.2904 | 1215379.8275
18 | 2609899.7816 | 1215493.438 | 2609940.9474 | 1215458.4196 | 2609948.7549 | 1215452.6071
19 | 2609899.7816 | 1215493.438 | 2609913.907 | 1215510.1758
20 | 2609876.6915 | 1215543.1729 | 2609875.3629 | 1215541.5815
21 | 2609833.4078 | 1215577.5195 | 2609848.2785 | 1215595.1664
22 | 2609701.6476 | 1215375.1254 | 2609696.2904 | 1215379.8275
23 | 2609815.3188 | 1215637.1694 | 2609808.7722 | 1215629.6699
24 | 2609815.3188 | 1215637.1694 | 2609806.4415 | 1215647.3495
25 | 2609826.2846 | 1215631.3396 | 2609815.3188 | 1215637.1694
26 | 2609849.6724 | 1215596.8206 | 2609848.2785 | 1215595.1664
27 | 2609849.6724 | 1215596.8206 | 2609863.6191 | 1215613.3711
28 | 2609866.37 | 1215616.6354 | 2609863.6191 | 1215613.3711
29 | 2609948.7549 | 1215452.6071 | 2609966.2862 | 1215438.0297
30 | 2609948.7549 | 1215452.6071 | 2609959.532 | 1215465.6228
31 | 2609914.2381 | 1215510.5681 | 2609913.907 | 1215510.1758
32 | 2609876.6915 | 1215543.1729 | 2609894.5734 | 1215564.5916
33 | 2609720.044 | 1215357.4816 | 2609733.5077 | 1215342.4585 | 2609750.366 | 1215322.6969 | 2609760.0549 | 1215308.574
34 | 2609701.6476 | 1215375.1254 | 2609718.644 | 1215359.0438 | 2609720.044 | 1215357.4816
35 | 2609778.9631 | 1215270.4806 | 2609766.2504 | 1215299.543 | 2609760.0549 | 1215308.574
36 | 2609905.7921 | 1215578.0291 | 2609894.5734 | 1215564.5916
37 | 2610039.6763 | 1215373.2025 | 2609976.4694 | 1215429.5623 | 2609966.2862 | 1215438.0297
38 | 2609959.532 | 1215465.6228 | 2609963.4881 | 1215470.4007
39 | 2609914.2381 | 1215510.5681 | 2609931.1529 | 1215530.6112
40 | 2609993.4714 | 1215310.7097 | 2609778.9631 | 1215270.4806
41 | 2609933.3172 | 1215533.1758 | 2609931.1529 | 1215530.6112
42 | 2609933.3172 | 1215533.1758 | 2609948.9959 | 1215551.7541
43 | 2609949.1455 | 1215551.9314 | 2609948.9959 | 1215551.7541
44 | 2610039.6763 | 1215373.2025 | 2610025.3623 | 1215357.0851
45 | 2610039.6763 | 1215373.2025 | 2610060.2071 | 1215360.0517 | 2610077.0569 | 1215377.6121
46 | 2609979.5932 | 1215489.8512 | 2609963.4881 | 1215470.4007
47 | 2609980.0344 | 1215490.3841 | 2609995.812 | 1215509.439
48 | 2609980.0344 | 1215490.3841 | 2609979.5932 | 1215489.8512
49 | 2609996.2365 | 1215509.9517 | 2609995.812 | 1215509.439
50 | 2610036.6356 | 1215447.1756 | 2610035.9717 | 1215447.7757
51 | 2610024.4596 | 1215455.1678 | 2610026.5609 | 1215456.2831 | 2610035.9717 | 1215447.7757
52 | 2610045.0319 | 1215439.5854 | 2610036.6356 | 1215447.1756
53 | 2610024.4596 | 1215455.1678 | 2610019.4261 | 1215463.8866 | 2610025.0544 | 1215471.8005
54 | 2610024.4596 | 1215455.1678 | 2610022.7072 | 1215454.2311 | 2610011.1312 | 1215440.7289
55 | 2610045.0319 | 1215439.5854 | 2610052.3396 | 1215432.9793
56 | 2610010.4609 | 1215439.947 | 2610011.1312 | 1215440.7289
57 | 2610052.3396 | 1215432.9793 | 2610068.8824 | 1215418.0246
58 | 2610016.245 | 1215430.4757 | 2610011.6013 | 1215434.5125 | 2610010.4609 | 1215439.947 | 2610010.4609 | 1215439.947
59 | 2610068.8824 | 1215418.0246 | 2610085.3024 | 1215403.181
60 | 2610016.245 | 1215430.4757 | 2610032.244 | 1215416.5678
61 | 2610032.244 | 1215416.5678 | 2610048.2509 | 1215402.653
62 | 2610048.2509 | 1215402.653 | 2610063.6306 | 1215389.2836
63 | 2610077.0569 | 1215377.6121 | 2610063.6306 | 1215389.2836
64 | 2610121.2095 | 1215319.5648 | 2610091.6998 | 1215339.3929 | 2610060.2071 | 1215360.0517 | 2610077.0569 | 1215377.6121
65 | 2610077.0569 | 1215377.6121 | 2610084.2987 | 1215384.4807
66 | 2610025.3623 | 1215357.0851 | 2610005.7007 | 1215334.9464 | 2610001.586 | 1215328.0158
67 | 2610121.2095 | 1215319.5648 | 2610140.0031 | 1215332.5594 | 2610144.472 | 1215330.11
68 | 2610121.2095 | 1215319.5648 | 2610134.8469 | 1215310.4048 | 2610148.6527 | 1215300.5721
69 | 2610207.2944 | 1215255.8524 | 2610202.2356 | 1215261.3247 | 2610194.0688 | 1215268.2258 | 2610148.6527 | 1215300.5721
70 | 2610207.2944 | 1215255.8524 | 2610210.799 | 1215262.3398 | 2610216.9514 | 1215274.5683 | 2610220.7162 | 1215279.8333 | 2610217.3845 | 1215296.6371 | 2610211.6325 | 1215321.319 | 2610208.2456 | 1215339.3568
71 | 2610001.586 | 1215328.0158 | 2609996.2132 | 1215318.966 | 2609993.4714 | 1215310.7097
72 | 2610208.2456 | 1215339.3568 | 2610198.5153 | 1215350.4354 | 2610189.9557 | 1215360.6599 | 2610183.3688 | 1215371.8217 | 2610177.5911 | 1215389.3774 | 2610177.3812 | 1215401.2059 | 2610179.627 | 1215411.9247
73 | 2610192.8765 | 1215429.1147 | 2610184.392 | 1215422.0852 | 2610180.0399 | 1215413.8954 | 2610179.627 | 1215411.9247
74 | 2610192.8765 | 1215429.1147 | 2610187.2297 | 1215432.2068 | 2610183.3567 | 1215437.0697 | 2610180.758 | 1215442.6462 | 2610179.2635 | 1215448.5381
75 | 2610192.8765 | 1215429.1147 | 2610199.966 | 1215426.0361 | 2610241.4736 | 1215409.9977 | 2610249.393 | 1215405.6199 | 2610257.8778 | 1215399.1641 | 2610269.3693 | 1215388.3332 | 2610278.725 | 1215380.6595

## bus_geodata
| x | y | coords
0 | 2609765.3865 | 1215661.1437
1 | 2609749.0096 | 1215642.2613
2 | 2609768.9805 | 1215665.2875
3 | 2609737.5602 | 1215629.0604
4 | 2609775.9597 | 1215668.9787
5 | 2609799.169 | 1215618.6659
6 | 2609780.8399 | 1215674.7677
7 | 2609821.0818 | 1215562.8924
8 | 2609861.4391 | 1215524.9038
9 | 2609833.1783 | 1215577.2472
10 | 2609788.2725 | 1215628.6204
11 | 2609800.6241 | 1215620.3359
12 | 2609632.9739 | 1215414.4622
13 | 2609644.1637 | 1215411.1531
14 | 2609899.7816 | 1215493.438
15 | 2609875.3629 | 1215541.5815
16 | 2609833.4078 | 1215577.5195
17 | 2609696.2904 | 1215379.8275
18 | 2609809.6202 | 1215611.8458
19 | 2609808.7722 | 1215629.6699
20 | 2609815.3188 | 1215637.1694
21 | 2609806.4415 | 1215647.3495
22 | 2609826.2846 | 1215631.3396
23 | 2609848.2785 | 1215595.1664
24 | 2609849.6724 | 1215596.8206
25 | 2609863.6191 | 1215613.3711
26 | 2609866.37 | 1215616.6354
27 | 2609948.7549 | 1215452.6071
28 | 2609913.907 | 1215510.1758
29 | 2609876.6915 | 1215543.1729
30 | 2609720.044 | 1215357.4816
31 | 2609760.0549 | 1215308.574
32 | 2609701.6476 | 1215375.1254
33 | 2609894.5734 | 1215564.5916
34 | 2609905.7921 | 1215578.0291
35 | 2609966.2862 | 1215438.0297
36 | 2609959.532 | 1215465.6228
37 | 2609914.2381 | 1215510.5681
38 | 2609778.9631 | 1215270.4806
39 | 2609931.1529 | 1215530.6112
40 | 2609933.3172 | 1215533.1758
41 | 2609948.9959 | 1215551.7541
42 | 2609949.1455 | 1215551.9314
43 | 2610039.6763 | 1215373.2025
44 | 2609963.4881 | 1215470.4007
45 | 2609980.0344 | 1215490.3841
46 | 2609995.812 | 1215509.439
47 | 2609979.5932 | 1215489.8512
48 | 2609996.2365 | 1215509.9517
49 | 2610035.9717 | 1215447.7757
50 | 2610036.6356 | 1215447.1756
51 | 2610024.4596 | 1215455.1678
52 | 2610045.0319 | 1215439.5854
53 | 2610025.0544 | 1215471.8005
54 | 2610011.1312 | 1215440.7289
55 | 2610052.3396 | 1215432.9793
56 | 2610010.4609 | 1215439.947
57 | 2610068.8824 | 1215418.0246
58 | 2610016.245 | 1215430.4757
59 | 2610085.3024 | 1215403.181
60 | 2610032.244 | 1215416.5678
61 | 2610048.2509 | 1215402.653
62 | 2610063.6306 | 1215389.2835
63 | 2610077.0569 | 1215377.6121
64 | 2610025.3623 | 1215357.0851
65 | 2610084.2987 | 1215384.4807
66 | 2610121.2095 | 1215319.5648
67 | 2610144.472 | 1215330.11
68 | 2610148.6527 | 1215300.5721
69 | 2610207.2944 | 1215255.8524
70 | 2610001.586 | 1215328.0158
71 | 2609993.4714 | 1215310.7097
72 | 2610208.2456 | 1215339.3568
73 | 2610179.627 | 1215411.9247
74 | 2610192.8765 | 1215429.1147
75 | 2610179.2635 | 1215448.5381
76 | 2610278.725 | 1215380.6595
77 | 2609948.7549 | 1215452.6071

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1