## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_420-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_420-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_420-7_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_420-7_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_420-7_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_420-7_0_6_node_61 | 0.4 | n |  | TRUE
6 | bus_LV_420-7_0_6_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_420-7_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_420-7_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_420-7_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_420-7_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_420-7_0_6_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_420-7_0_6_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_420-7_0_6_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_420-7_0_6_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_420-7_0_6_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_420-7_0_6_node_39 | 0.4 | n |  | TRUE
17 | bus_LV_420-7_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_420-7_0_6_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_420-7_0_6_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_420-7_0_6_node_42 | 0.4 | n |  | TRUE
21 | bus_LV_420-7_0_6_node_45 | 0.4 | n |  | TRUE
22 | bus_LV_420-7_0_6_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_420-7_0_6_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_420-7_0_6_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_420-7_0_6_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_420-7_0_6_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_420-7_0_6_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_420-7_0_6_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_420-7_0_6_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_420-7_0_6_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_420-7_0_6_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_420-7_0_6_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_420-7_0_6_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_420-7_0_6_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_420-7_0_6_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_420-7_0_6_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_420-7_0_6_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_420-7_0_6_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_420-7_0_6_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_420-7_0_6_node_62 | 0.4 | n |  | TRUE
41 | bus_LV_420-7_0_6_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_420-7_0_6_node_18 | 0.4 | n |  | TRUE
43 | bus_LV_420-7_0_6_node_19 | 0.4 | n |  | TRUE
44 | bus_LV_420-7_0_6_node_20 | 0.4 | n |  | TRUE
45 | bus_LV_420-7_0_6_node_21 | 0.4 | n |  | TRUE
46 | bus_LV_420-7_0_6_node_59 | 0.4 | n |  | TRUE
47 | bus_LV_420-7_0_6_node_60 | 0.4 | n |  | TRUE
48 | bus_LV_420-7_0_6_node_57 | 0.4 | n |  | TRUE
49 | bus_LV_420-7_0_6_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_420-7_0_6_node_53 | 0.4 | n |  | TRUE
51 | bus_LV_420-7_0_6_node_25 | 0.4 | n |  | TRUE
52 | bus_LV_420-7_0_6_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_420-7_0_6_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_420-7_0_6_node_49 | 0.4 | n |  | TRUE
55 | bus_LV_420-7_0_6_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_420-7_0_6_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_420-7_0_6_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_420-7_0_6_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_420-7_0_6_node_63 | 0.4 | n |  | TRUE
60 | bus_MV_446_1_node_131 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_420-7_0_6_load_0 | 0 | 0.0051927 | 0.0013014 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_420-7_0_6_load_1 | 1 | 0.0048263 | 0.0012096 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_420-7_0_6_load_3 | 3 | 0.0085734 | 0.0021487 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_420-7_0_6_load_4 | 4 | 0.030304 | 0.007595 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_420-7_0_6_load_61 | 5 | 0.0099894 | 0.0025036 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_420-7_0_6_load_5 | 7 | 0.0061005 | 0.0015289 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_420-7_0_6_load_7 | 9 | 0.013062 | 0.0032737 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_420-7_0_6_load_9 | 12 | 0.0072435 | 0.0018154 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_420-7_0_6_load_16 | 13 | 0.0065017 | 0.0016295 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_420-7_0_6_load_33 | 14 | 0.070663 | 0.01771 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_420-7_0_6_load_14 | 15 | 0.0048311 | 0.0012108 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_420-7_0_6_load_39 | 16 | 0.024661 | 0.0061806 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_420-7_0_6_load_10 | 17 | 0.012309 | 0.003085 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_420-7_0_6_load_11 | 18 | 0.022125 | 0.0055451 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_420-7_0_6_load_45 | 21 | 0.0099003 | 0.0024813 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_420-7_0_6_load_13 | 22 | 0.0069486 | 0.0017415 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_420-7_0_6_load_15 | 23 | 0.0090408 | 0.0022658 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_420-7_0_6_load_26 | 25 | 0.0052065 | 0.0013049 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_420-7_0_6_load_23 | 26 | 0.0098243 | 0.0024622 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_420-7_0_6_load_29 | 27 | 0.024133 | 0.0060483 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_420-7_0_6_load_30 | 28 | 0.0081301 | 0.0020376 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_420-7_0_6_load_32 | 29 | 0.012548 | 0.0031449 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_420-7_0_6_load_37 | 30 | 0.0082113 | 0.0020579 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_420-7_0_6_load_35 | 31 | 0.020847 | 0.0052247 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_420-7_0_6_load_36 | 32 | 0.023012 | 0.0057675 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_420-7_0_6_load_38 | 33 | 0.014832 | 0.0037173 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_420-7_0_6_load_41 | 34 | 0.014841 | 0.0037196 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_420-7_0_6_load_43 | 35 | 0.017412 | 0.0043639 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_420-7_0_6_load_44 | 36 | 0.0071823 | 0.0018001 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_420-7_0_6_load_46 | 37 | 0.010432 | 0.0026146 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_420-7_0_6_load_47 | 38 | 0.0056676 | 0.0014204 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_420-7_0_6_load_48 | 39 | 0.033323 | 0.0083516 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_420-7_0_6_load_62 | 40 | 0.0061145 | 0.0015324 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_420-7_0_6_load_24 | 41 | 0.010707 | 0.0026834 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_420-7_0_6_load_18 | 42 | 0.0067275 | 0.0016861 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_420-7_0_6_load_19 | 43 | 0.0088151 | 0.0022093 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_420-7_0_6_load_20 | 44 | 0.0048563 | 0.0012171 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_420-7_0_6_load_59 | 46 | 0.0048168 | 0.0012072 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_420-7_0_6_load_60 | 47 | 0.0077066 | 0.0019315 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_420-7_0_6_load_53 | 50 | 0.010203 | 0.0025571 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_420-7_0_6_load_25 | 51 | 0.0082573 | 0.0020695 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_420-7_0_6_load_27 | 52 | 0.017241 | 0.004321 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_420-7_0_6_load_34 | 53 | 0.015131 | 0.0037922 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_420-7_0_6_load_49 | 54 | 0.0064261 | 0.0016105 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_420-7_0_6_load_52 | 56 | 0.0048431 | 0.0012138 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_420-7_0_6_load_55 | 58 | 0.0059349 | 0.0014874 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_420-7_0_6_load_63 | 59 | 0.021279 | 0.0053331 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_420-7_0_6_line_0 |  | 0 | 1 | 0.053928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_420-7_0_6_line_1 |  | 0 | 2 | 0.038512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_420-7_0_6_line_2 |  | 1 | 3 | 0.023941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_420-7_0_6_line_3 |  | 2 | 4 | 0.082099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_420-7_0_6_line_4 |  | 3 | 5 | 0.009996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_420-7_0_6_line_5 |  | 5 | 6 | 0.023385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_420-7_0_6_line_6 |  | 6 | 48 | 0.008064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_420-7_0_6_line_7 |  | 6 | 44 | 0.015117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_420-7_0_6_line_8 |  | 7 | 8 | 0.03005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_420-7_0_6_line_9 |  | 7 | 9 | 0.0062152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_420-7_0_6_line_10 |  | 8 | 10 | 0.068943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_420-7_0_6_line_11 |  | 10 | 11 | 0.014873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_420-7_0_6_line_12 |  | 10 | 12 | 0.0051502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_420-7_0_6_line_13 |  | 11 | 16 | 0.016999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_420-7_0_6_line_14 |  | 12 | 17 | 0.014212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_420-7_0_6_line_15 |  | 13 | 14 | 0.071022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_420-7_0_6_line_16 |  | 13 | 15 | 0.00059217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_420-7_0_6_line_17 |  | 14 | 30 | 0.067793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_420-7_0_6_line_18 |  | 15 | 22 | 0.025036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_420-7_0_6_line_19 |  | 17 | 18 | 0.025413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_420-7_0_6_line_20 |  | 18 | 19 | 0.023723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_420-7_0_6_line_21 |  | 19 | 20 | 0.032218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_420-7_0_6_line_22 |  | 19 | 21 | 0.020746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_420-7_0_6_line_23 |  | 20 | 36 | 0.0051245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_420-7_0_6_line_24 |  | 20 | 34 | 0.035126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_420-7_0_6_line_25 |  | 21 | 33 | 0.0025735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_420-7_0_6_line_26 |  | 22 | 23 | 0.0020825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_420-7_0_6_line_27 |  | 23 | 24 | 0.01389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_420-7_0_6_line_28 |  | 24 | 25 | 0.0070833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_420-7_0_6_line_29 |  | 24 | 26 | 0.013672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_420-7_0_6_line_30 |  | 25 | 40 | 0.031389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_420-7_0_6_line_31 |  | 26 | 41 | 0.021925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_420-7_0_6_line_32 |  | 27 | 28 | 0.038962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_420-7_0_6_line_33 |  | 28 | 29 | 0.030681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_420-7_0_6_line_34 |  | 28 | 30 | 0.037816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_420-7_0_6_line_35 |  | 29 | 53 | 0.024861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_420-7_0_6_line_36 |  | 30 | 31 | 0.01362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_420-7_0_6_line_37 |  | 31 | 32 | 0.0050274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_420-7_0_6_line_38 |  | 32 | 33 | 0.03429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_420-7_0_6_line_39 |  | 34 | 35 | 0.01246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_420-7_0_6_line_40 |  | 36 | 37 | 0.019774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_420-7_0_6_line_41 |  | 37 | 38 | 5.0256e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_420-7_0_6_line_42 |  | 38 | 39 | 0.009451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_420-7_0_6_line_43 |  | 40 | 47 | 0.0017607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_420-7_0_6_line_44 |  | 41 | 51 | 0.00032409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_420-7_0_6_line_45 |  | 42 | 43 | 0.0084068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_420-7_0_6_line_46 |  | 42 | 44 | 0.025097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_420-7_0_6_line_47 |  | 43 | 45 | 0.025824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_420-7_0_6_line_48 |  | 45 | 46 | 0.01192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_420-7_0_6_line_49 |  | 45 | 47 | 0.0074352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_420-7_0_6_line_50 |  | 48 | 49 | 0.008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_420-7_0_6_line_51 |  | 48 | 50 | 0.0086937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_420-7_0_6_line_52 |  | 49 | 59 | 0.022474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_420-7_0_6_line_53 |  | 50 | 55 | 0.029264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_420-7_0_6_line_54 |  | 51 | 52 | 0.01725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_420-7_0_6_line_55 |  | 54 | 55 | 0.014737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_420-7_0_6_line_56 |  | 55 | 56 | 0.01026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_420-7_0_6_line_57 |  | 56 | 57 | 0.019265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_420-7_0_6_line_58 |  | 57 | 58 | 0.016047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_420-7_0_6_trafo_33 | 0.63 MVA 20/0.4 kV | 60 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2610814.5964 | 1214839.1264 | 2610773.7435 | 1214874.33
1 | 2610843.7706 | 1214813.9866 | 2610814.5964 | 1214839.1264
2 | 2610755.6075 | 1214889.9581 | 2610773.7435 | 1214874.33
3 | 2610816.8013 | 1214879.2969 | 2610827.2886 | 1214870.6109 | 2610848.7248 | 1214845.8579 | 2610853.9757 | 1214835.4171 | 2610851.3748 | 1214824.9732 | 2610843.7706 | 1214813.9866
4 | 2610755.6075 | 1214889.9581 | 2610748.0351 | 1214896.4833
5 | 2610730.32 | 1214911.7488 | 2610748.0351 | 1214896.4833
6 | 2610730.32 | 1214911.7488 | 2610724.1143 | 1214916.9184
7 | 2610730.32 | 1214911.7488 | 2610726.0677 | 1214907.4276 | 2610719.8626 | 1214900.8335
8 | 2610659.509 | 1214536.2663 | 2610635.7485 | 1214554.6636
9 | 2610629.8051 | 1214555.3466 | 2610634.7259 | 1214555.4554 | 2610635.7485 | 1214554.6636
10 | 2610659.509 | 1214536.2663 | 2610662.919 | 1214540.4081 | 2610675.2424 | 1214549.9131 | 2610686.5987 | 1214556.6705 | 2610683.8925 | 1214562.4467 | 2610678.8676 | 1214569.6863 | 2610670.8152 | 1214575.4752 | 2610662.9453 | 1214581.1311
11 | 2610662.9453 | 1214581.1311 | 2610668.1123 | 1214592.2243 | 2610668.8064 | 1214594.7714
12 | 2610662.9453 | 1214581.1311 | 2610658.7626 | 1214584.1361
13 | 2610668.8064 | 1214594.7714 | 2610670.6472 | 1214601.5896 | 2610670.7285 | 1214607.1262 | 2610668.4156 | 1214610.8681
14 | 2610647.2202 | 1214592.4286 | 2610658.7626 | 1214584.1361
15 | 2610688.0349 | 1214798.1014 | 2610696.1541 | 1214727.5449
16 | 2610688.4432 | 1214798.5303 | 2610688.0349 | 1214798.1014
17 | 2610659.0648 | 1214670.7969 | 2610696.1541 | 1214727.5449
18 | 2610705.7049 | 1214816.6642 | 2610688.4432 | 1214798.5303
19 | 2610647.2202 | 1214592.4286 | 2610630.0973 | 1214604.7305 | 2610626.36 | 1214606.9146
20 | 2610605.8778 | 1214618.8845 | 2610626.36 | 1214606.9146
21 | 2610576.9195 | 1214633.1747 | 2610605.8778 | 1214618.8845
22 | 2610605.8778 | 1214618.8845 | 2610611.8735 | 1214629.4344 | 2610617.065 | 1214636.3051
23 | 2610576.9195 | 1214633.1747 | 2610572.081 | 1214634.8627
24 | 2610576.9195 | 1214633.1747 | 2610597.7949 | 1214661.425
25 | 2610617.065 | 1214636.3051 | 2610618.6164 | 1214638.3584
26 | 2610705.7049 | 1214816.6642 | 2610707.1408 | 1214818.1725
27 | 2610716.7173 | 1214828.2329 | 2610707.1408 | 1214818.1725
28 | 2610716.7173 | 1214828.2329 | 2610711.2112 | 1214832.6889
29 | 2610716.7173 | 1214828.2329 | 2610726.8799 | 1214819.0869
30 | 2610711.2112 | 1214832.6889 | 2610703.1201 | 1214839.237 | 2610687.4715 | 1214850.849 | 2610686.3163 | 1214851.7963
31 | 2610726.8799 | 1214819.0869 | 2610727.6774 | 1214818.3691 | 2610739.6965 | 1214801.3291
32 | 2610642.5949 | 1214731.0116 | 2610672.5687 | 1214706.1195
33 | 2610672.5687 | 1214706.1195 | 2610696.1719 | 1214686.518
34 | 2610659.0648 | 1214670.7969 | 2610672.5687 | 1214706.1195
35 | 2610696.1719 | 1214686.518 | 2610715.2975 | 1214670.6349
36 | 2610659.0648 | 1214670.7969 | 2610647.1751 | 1214664.1533
37 | 2610647.1751 | 1214664.1533 | 2610642.7864 | 1214661.701
38 | 2610642.7864 | 1214661.701 | 2610631.4807 | 1214655.3837 | 2610618.6164 | 1214638.3584
39 | 2610605.2 | 1214671.4463 | 2610597.7949 | 1214661.425
40 | 2610572.081 | 1214634.8627 | 2610553.4103 | 1214641.3761
41 | 2610553.3629 | 1214641.3927 | 2610553.4103 | 1214641.3761
42 | 2610553.3629 | 1214641.3927 | 2610544.4393 | 1214644.5058
43 | 2610684.9547 | 1214852.9127 | 2610686.3163 | 1214851.7963
44 | 2610739.8833 | 1214801.0642 | 2610739.6965 | 1214801.3291
45 | 2610696.9023 | 1214876.4337 | 2610702.6635 | 1214882.5561
46 | 2610719.8626 | 1214900.8335 | 2610702.6635 | 1214882.5561
47 | 2610679.2051 | 1214857.627 | 2610696.9023 | 1214876.4337
48 | 2610679.2051 | 1214857.627 | 2610669.8779 | 1214865.0486
49 | 2610679.2051 | 1214857.627 | 2610684.9547 | 1214852.9127
50 | 2610719.956 | 1214923.7592 | 2610724.1143 | 1214916.9184
51 | 2610724.1143 | 1214916.9184 | 2610720.4305 | 1214917.4454 | 2610716.3119 | 1214920.2313
52 | 2610719.956 | 1214923.7592 | 2610733.2883 | 1214941.8517
53 | 2610692.0722 | 1214936.6278 | 2610716.3119 | 1214920.2313
54 | 2610739.8833 | 1214801.0642 | 2610743.4974 | 1214795.9404 | 2610750.575 | 1214787.5458
55 | 2610692.0722 | 1214936.6278 | 2610680.2803 | 1214945.4675
56 | 2610692.0722 | 1214936.6278 | 2610689.3739 | 1214933.7992 | 2610684.9351 | 1214929.2571
57 | 2610671.4705 | 1214915.4792 | 2610684.9351 | 1214929.2571
58 | 2610671.4705 | 1214915.4792 | 2610678.3167 | 1214908.7654 | 2610679.293 | 1214906.3324 | 2610679.1142 | 1214904.3977 | 2610677.9095 | 1214902.9169

## bus_geodata
| x | y | coords
0 | 2610814.5964 | 1214839.1264
1 | 2610773.7435 | 1214874.33
2 | 2610843.7706 | 1214813.9866
3 | 2610755.6075 | 1214889.9581
4 | 2610816.8013 | 1214879.2969
5 | 2610748.0351 | 1214896.4833
6 | 2610730.32 | 1214911.7488
7 | 2610635.7485 | 1214554.6636
8 | 2610659.509 | 1214536.2663
9 | 2610629.8051 | 1214555.3466
10 | 2610662.9453 | 1214581.1311
11 | 2610668.8064 | 1214594.7714
12 | 2610658.7626 | 1214584.1361
13 | 2610688.0349 | 1214798.1014
14 | 2610696.1541 | 1214727.5449
15 | 2610688.4432 | 1214798.5303
16 | 2610668.4156 | 1214610.8681
17 | 2610647.2202 | 1214592.4286
18 | 2610626.36 | 1214606.9146
19 | 2610605.8778 | 1214618.8845
20 | 2610576.9195 | 1214633.1747
21 | 2610617.065 | 1214636.3051
22 | 2610705.7049 | 1214816.6642
23 | 2610707.1408 | 1214818.1725
24 | 2610716.7173 | 1214828.2329
25 | 2610711.2112 | 1214832.6889
26 | 2610726.8799 | 1214819.0869
27 | 2610642.5949 | 1214731.0116
28 | 2610672.5687 | 1214706.1195
29 | 2610696.1719 | 1214686.518
30 | 2610659.0648 | 1214670.7969
31 | 2610647.1751 | 1214664.1533
32 | 2610642.7864 | 1214661.701
33 | 2610618.6164 | 1214638.3584
34 | 2610597.7949 | 1214661.425
35 | 2610605.2 | 1214671.4463
36 | 2610572.081 | 1214634.8627
37 | 2610553.4103 | 1214641.3761
38 | 2610553.3629 | 1214641.3927
39 | 2610544.4393 | 1214644.5058
40 | 2610686.3163 | 1214851.7963
41 | 2610739.6965 | 1214801.3291
42 | 2610702.6635 | 1214882.5561
43 | 2610696.9023 | 1214876.4337
44 | 2610719.8626 | 1214900.8335
45 | 2610679.2051 | 1214857.627
46 | 2610669.8779 | 1214865.0486
47 | 2610684.9547 | 1214852.9127
48 | 2610724.1143 | 1214916.9184
49 | 2610719.956 | 1214923.7592
50 | 2610716.3119 | 1214920.2313
51 | 2610739.8833 | 1214801.0642
52 | 2610750.575 | 1214787.5458
53 | 2610715.2975 | 1214670.6349
54 | 2610680.2803 | 1214945.4675
55 | 2610692.0722 | 1214936.6278
56 | 2610684.9351 | 1214929.2571
57 | 2610671.4705 | 1214915.4792
58 | 2610677.9095 | 1214902.9169
59 | 2610733.2883 | 1214941.8517
60 | 2610623.5576 | 1214746.8212

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1