## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4201-26_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4201-26_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4201-26_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4201-26_0_6_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_4201-26_0_6_node_107 | 0.4 | n |  | TRUE
5 | bus_LV_4201-26_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_4201-26_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4201-26_0_6_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_4201-26_0_6_node_109 | 0.4 | n |  | TRUE
9 | bus_LV_4201-26_0_6_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_4201-26_0_6_node_105 | 0.4 | n |  | TRUE
11 | bus_LV_4201-26_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_4201-26_0_6_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_4201-26_0_6_node_16 | 0.4 | n |  | TRUE
14 | bus_LV_4201-26_0_6_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_4201-26_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4201-26_0_6_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_4201-26_0_6_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_4201-26_0_6_node_76 | 0.4 | n |  | TRUE
19 | bus_LV_4201-26_0_6_node_75 | 0.4 | n |  | TRUE
20 | bus_LV_4201-26_0_6_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_4201-26_0_6_node_55 | 0.4 | n |  | TRUE
22 | bus_LV_4201-26_0_6_node_56 | 0.4 | n |  | TRUE
23 | bus_LV_4201-26_0_6_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_4201-26_0_6_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_4201-26_0_6_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_4201-26_0_6_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_4201-26_0_6_node_41 | 0.4 | n |  | TRUE
28 | bus_LV_4201-26_0_6_node_51 | 0.4 | n |  | TRUE
29 | bus_LV_4201-26_0_6_node_108 | 0.4 | n |  | TRUE
30 | bus_LV_4201-26_0_6_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_4201-26_0_6_node_106 | 0.4 | n |  | TRUE
32 | bus_LV_4201-26_0_6_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_4201-26_0_6_node_101 | 0.4 | n |  | TRUE
34 | bus_LV_4201-26_0_6_node_103 | 0.4 | n |  | TRUE
35 | bus_LV_4201-26_0_6_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_4201-26_0_6_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_4201-26_0_6_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_4201-26_0_6_node_19 | 0.4 | n |  | TRUE
39 | bus_LV_4201-26_0_6_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_4201-26_0_6_node_54 | 0.4 | n |  | TRUE
41 | bus_LV_4201-26_0_6_node_64 | 0.4 | n |  | TRUE
42 | bus_LV_4201-26_0_6_node_65 | 0.4 | n |  | TRUE
43 | bus_LV_4201-26_0_6_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_4201-26_0_6_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_4201-26_0_6_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_4201-26_0_6_node_18 | 0.4 | n |  | TRUE
47 | bus_LV_4201-26_0_6_node_25 | 0.4 | n |  | TRUE
48 | bus_LV_4201-26_0_6_node_23 | 0.4 | n |  | TRUE
49 | bus_LV_4201-26_0_6_node_100 | 0.4 | n |  | TRUE
50 | bus_LV_4201-26_0_6_node_104 | 0.4 | n |  | TRUE
51 | bus_LV_4201-26_0_6_node_24 | 0.4 | n |  | TRUE
52 | bus_LV_4201-26_0_6_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_4201-26_0_6_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_4201-26_0_6_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_4201-26_0_6_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_4201-26_0_6_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_4201-26_0_6_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_4201-26_0_6_node_78 | 0.4 | n |  | TRUE
59 | bus_LV_4201-26_0_6_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_4201-26_0_6_node_49 | 0.4 | n |  | TRUE
61 | bus_LV_4201-26_0_6_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_4201-26_0_6_node_46 | 0.4 | n |  | TRUE
63 | bus_LV_4201-26_0_6_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_4201-26_0_6_node_58 | 0.4 | n |  | TRUE
65 | bus_LV_4201-26_0_6_node_59 | 0.4 | n |  | TRUE
66 | bus_LV_4201-26_0_6_node_60 | 0.4 | n |  | TRUE
67 | bus_LV_4201-26_0_6_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_4201-26_0_6_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_4201-26_0_6_node_69 | 0.4 | n |  | TRUE
70 | bus_LV_4201-26_0_6_node_83 | 0.4 | n |  | TRUE
71 | bus_LV_4201-26_0_6_node_81 | 0.4 | n |  | TRUE
72 | bus_LV_4201-26_0_6_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_4201-26_0_6_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_4201-26_0_6_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_4201-26_0_6_node_110 | 0.4 | n |  | TRUE
76 | bus_LV_4201-26_0_6_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_4201-26_0_6_node_87 | 0.4 | n |  | TRUE
78 | bus_LV_4201-26_0_6_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_4201-26_0_6_node_86 | 0.4 | n |  | TRUE
80 | bus_LV_4201-26_0_6_node_84 | 0.4 | n |  | TRUE
81 | bus_LV_4201-26_0_6_node_79 | 0.4 | n |  | TRUE
82 | bus_LV_4201-26_0_6_node_70 | 0.4 | n |  | TRUE
83 | bus_LV_4201-26_0_6_node_71 | 0.4 | n |  | TRUE
84 | bus_LV_4201-26_0_6_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_4201-26_0_6_node_74 | 0.4 | n |  | TRUE
86 | bus_LV_4201-26_0_6_node_80 | 0.4 | n |  | TRUE
87 | bus_LV_4201-26_0_6_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_4201-26_0_6_node_85 | 0.4 | n |  | TRUE
89 | bus_LV_4201-26_0_6_node_91 | 0.4 | n |  | TRUE
90 | bus_LV_4201-26_0_6_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_4201-26_0_6_node_88 | 0.4 | n |  | TRUE
92 | bus_LV_4201-26_0_6_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_4201-26_0_6_node_96 | 0.4 | n |  | TRUE
94 | bus_LV_4201-26_0_6_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_4201-26_0_6_node_92 | 0.4 | n |  | TRUE
96 | bus_LV_4201-26_0_6_node_93 | 0.4 | n |  | TRUE
97 | bus_LV_4201-26_0_6_node_97 | 0.4 | n |  | TRUE
98 | bus_LV_4201-26_0_6_node_98 | 0.4 | n |  | TRUE
99 | bus_LV_4201-26_0_6_node_102 | 0.4 | n |  | TRUE
100 | bus_LV_4201-26_0_6_node_99 | 0.4 | n |  | TRUE
101 | bus_MV_484_0_node_53 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4201-26_0_6_load_0 | 0 | 0.0033098 | 0.0008295 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4201-26_0_6_load_107 | 4 | 0.0044361 | 0.0011118 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4201-26_0_6_load_109 | 8 | 0.016416 | 0.0041143 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4201-26_0_6_load_105 | 10 | 0.0048957 | 0.001227 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4201-26_0_6_load_40 | 14 | 0.00083656 | 0.00020966 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4201-26_0_6_load_29 | 17 | 0.0010065 | 0.00025225 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4201-26_0_6_load_76 | 18 | 0.0014717 | 0.00036883 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4201-26_0_6_load_75 | 19 | 0.00024558 | 6.1547e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4201-26_0_6_load_56 | 22 | 0.0019658 | 0.00049266 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4201-26_0_6_load_32 | 23 | 0.0011833 | 0.00029657 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4201-26_0_6_load_30 | 24 | 0.0005016 | 0.00012571 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4201-26_0_6_load_28 | 25 | 0.018022 | 0.0045167 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4201-26_0_6_load_17 | 26 | 0.0066708 | 0.0016719 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4201-26_0_6_load_51 | 28 | 0.0099605 | 0.0024963 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4201-26_0_6_load_108 | 29 | 0.011057 | 0.0027711 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4201-26_0_6_load_106 | 31 | 0.0015932 | 0.0003993 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4201-26_0_6_load_101 | 33 | 0.0025759 | 0.00064558 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4201-26_0_6_load_103 | 34 | 0.0025123 | 0.00062963 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4201-26_0_6_load_57 | 35 | 0.0030733 | 0.00077024 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4201-26_0_6_load_21 | 37 | 0.025838 | 0.0064756 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4201-26_0_6_load_19 | 38 | 0.0060098 | 0.0015062 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4201-26_0_6_load_27 | 39 | 0.0088984 | 0.0022301 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4201-26_0_6_load_54 | 40 | 0.01203 | 0.0030149 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4201-26_0_6_load_64 | 41 | 0.00078889 | 0.00019772 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4201-26_0_6_load_65 | 42 | 0.0010273 | 0.00025746 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4201-26_0_6_load_26 | 43 | 0.0026612 | 0.00066696 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4201-26_0_6_load_18 | 46 | 0.013492 | 0.0033813 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4201-26_0_6_load_25 | 47 | 0.0060532 | 0.0015171 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4201-26_0_6_load_23 | 48 | 0.0029465 | 0.00073846 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4201-26_0_6_load_104 | 50 | 0.0026169 | 0.00065586 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4201-26_0_6_load_24 | 51 | 0.0021829 | 0.00054708 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4201-26_0_6_load_37 | 53 | 0.0062976 | 0.0015783 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4201-26_0_6_load_39 | 54 | 0.0074814 | 0.001875 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4201-26_0_6_load_38 | 55 | 0.0027285 | 0.00068383 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4201-26_0_6_load_35 | 56 | 0.057628 | 0.014443 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4201-26_0_6_load_78 | 58 | 0.0010523 | 0.00026374 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4201-26_0_6_load_53 | 59 | 0.0088977 | 0.00223 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4201-26_0_6_load_49 | 60 | 0.0041429 | 0.0010383 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4201-26_0_6_load_44 | 61 | 0.013478 | 0.0033778 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4201-26_0_6_load_47 | 63 | 0.030344 | 0.007605 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4201-26_0_6_load_58 | 64 | 0.0023317 | 0.00058438 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4201-26_0_6_load_59 | 65 | 0.0029255 | 0.00073319 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4201-26_0_6_load_61 | 67 | 0.00099747 | 0.00024999 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4201-26_0_6_load_62 | 68 | 0.0034354 | 0.00086099 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4201-26_0_6_load_83 | 70 | 0.0033624 | 0.00084269 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4201-26_0_6_load_81 | 71 | 0.0024301 | 0.00060903 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4201-26_0_6_load_68 | 74 | 0.0037812 | 0.00094765 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4201-26_0_6_load_110 | 75 | 0.0038436 | 0.00096331 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4201-26_0_6_load_77 | 76 | 0.0018062 | 0.00045267 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4201-26_0_6_load_87 | 77 | 0.0030151 | 0.00075567 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4201-26_0_6_load_73 | 78 | 0.00089565 | 0.00022447 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4201-26_0_6_load_86 | 79 | 0.0043313 | 0.0010855 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4201-26_0_6_load_84 | 80 | 0.0037548 | 0.00094105 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4201-26_0_6_load_79 | 81 | 0.0028228 | 0.00070747 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4201-26_0_6_load_70 | 82 | 0.0021402 | 0.00053639 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4201-26_0_6_load_71 | 83 | 0.002629 | 0.00065889 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4201-26_0_6_load_72 | 84 | 0.0023148 | 0.00058015 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4201-26_0_6_load_74 | 85 | 0.0046695 | 0.0011703 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4201-26_0_6_load_80 | 86 | 0.0021867 | 0.00054803 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4201-26_0_6_load_82 | 87 | 0.014467 | 0.0036259 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4201-26_0_6_load_91 | 89 | 0.0010478 | 0.00026261 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4201-26_0_6_load_90 | 90 | 0.002417 | 0.00060575 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4201-26_0_6_load_88 | 91 | 0.0042399 | 0.0010626 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4201-26_0_6_load_89 | 92 | 0.0030077 | 0.0007538 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4201-26_0_6_load_96 | 93 | 0.0029356 | 0.00073573 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4201-26_0_6_load_93 | 96 | 0.0033327 | 0.00083526 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4201-26_0_6_load_97 | 97 | 0.0024179 | 0.00060597 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4201-26_0_6_load_98 | 98 | 0.0026456 | 0.00066305 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4201-26_0_6_load_102 | 99 | 0.004246 | 0.0010642 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4201-26_0_6_load_99 | 100 | 0.0029829 | 0.00074759 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 55 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4201-26_0_6_line_0 |  | 0 | 1 | 0.020147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4201-26_0_6_line_1 |  | 1 | 2 | 0.012259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4201-26_0_6_line_2 |  | 2 | 3 | 0.070276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4201-26_0_6_line_3 |  | 2 | 4 | 0.02675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4201-26_0_6_line_4 |  | 3 | 6 | 0.037039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_4201-26_0_6_line_5 |  | 3 | 9 | 0.043229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4201-26_0_6_line_6 |  | 5 | 6 | 0.036983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_4201-26_0_6_line_7 |  | 5 | 7 | 0.019581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
8 | LV_4201-26_0_6_line_8 |  | 5 | 8 | 0.0077731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4201-26_0_6_line_9 |  | 6 | 10 | 0.020467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4201-26_0_6_line_10 |  | 7 | 18 | 0.12134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4201-26_0_6_line_11 |  | 7 | 19 | 0.017082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_4201-26_0_6_line_12 |  | 9 | 29 | 0.01466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4201-26_0_6_line_13 |  | 9 | 30 | 0.009561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4201-26_0_6_line_14 |  | 10 | 31 | 0.05956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4201-26_0_6_line_15 |  | 11 | 12 | 0.033048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_4201-26_0_6_line_16 |  | 11 | 13 | 0.057071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_4201-26_0_6_line_17 |  | 11 | 14 | 0.018458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4201-26_0_6_line_18 |  | 12 | 23 | 0.014711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_4201-26_0_6_line_19 |  | 12 | 24 | 0.027139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_4201-26_0_6_line_20 |  | 12 | 20 | 0.047477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4201-26_0_6_line_21 |  | 13 | 25 | 0.032326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4201-26_0_6_line_22 |  | 13 | 15 | 0.009848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
23 | LV_4201-26_0_6_line_23 |  | 15 | 16 | 0.022336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
24 | LV_4201-26_0_6_line_24 |  | 15 | 17 | 0.062858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4201-26_0_6_line_25 |  | 16 | 19 | 0.004714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
26 | LV_4201-26_0_6_line_26 |  | 17 | 39 | 0.040201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4201-26_0_6_line_27 |  | 20 | 21 | 0.010426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4201-26_0_6_line_28 |  | 20 | 22 | 0.069994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4201-26_0_6_line_29 |  | 21 | 40 | 0.013506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4201-26_0_6_line_30 |  | 23 | 43 | 0.10416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
31 | LV_4201-26_0_6_line_31 |  | 24 | 44 | 0.058229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_4201-26_0_6_line_32 |  | 26 | 27 | 0.029282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4201-26_0_6_line_33 |  | 26 | 28 | 0.093307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4201-26_0_6_line_34 |  | 27 | 45 | 0.075987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4201-26_0_6_line_35 |  | 30 | 63 | 0.032411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4201-26_0_6_line_36 |  | 30 | 61 | 0.041709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4201-26_0_6_line_37 |  | 32 | 33 | 0.032223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
38 | LV_4201-26_0_6_line_38 |  | 32 | 34 | 0.02133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4201-26_0_6_line_39 |  | 32 | 35 | 0.0058951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4201-26_0_6_line_40 |  | 32 | 36 | 0.075851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_4201-26_0_6_line_41 |  | 33 | 49 | 0.018789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_4201-26_0_6_line_42 |  | 34 | 50 | 0.020253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4201-26_0_6_line_43 |  | 36 | 37 | 0.11393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_4201-26_0_6_line_44 |  | 36 | 38 | 0.016237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4201-26_0_6_line_45 |  | 37 | 47 | 0.067138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_4201-26_0_6_line_46 |  | 38 | 46 | 0.019153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4201-26_0_6_line_47 |  | 41 | 42 | 0.017824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4201-26_0_6_line_48 |  | 42 | 72 | 0.030052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4201-26_0_6_line_49 |  | 43 | 51 | 0.021824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_4201-26_0_6_line_50 |  | 44 | 52 | 0.020074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_4201-26_0_6_line_51 |  | 45 | 58 | 0.024463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4201-26_0_6_line_52 |  | 45 | 59 | 0.033776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4201-26_0_6_line_53 |  | 47 | 48 | 0.044526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_4201-26_0_6_line_54 |  | 48 | 51 | 0.02048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
55 | LV_4201-26_0_6_line_55 |  | 49 | 99 | 0.01982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4201-26_0_6_line_56 |  | 49 | 100 | 0.042889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
57 | LV_4201-26_0_6_line_57 |  | 52 | 53 | 0.013647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4201-26_0_6_line_58 |  | 52 | 54 | 0.028986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_4201-26_0_6_line_59 |  | 54 | 55 | 0.0068458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_4201-26_0_6_line_60 |  | 55 | 57 | 0.030578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4201-26_0_6_line_61 |  | 56 | 57 | 0.015032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4201-26_0_6_line_62 |  | 59 | 60 | 0.11264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4201-26_0_6_line_63 |  | 60 | 62 | 0.0030509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4201-26_0_6_line_64 |  | 61 | 62 | 0.026946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4201-26_0_6_line_65 |  | 64 | 65 | 0.027532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4201-26_0_6_line_66 |  | 64 | 66 | 0.018169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4201-26_0_6_line_67 |  | 65 | 67 | 0.048529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4201-26_0_6_line_68 |  | 66 | 68 | 0.048468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4201-26_0_6_line_69 |  | 67 | 69 | 0.056923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4201-26_0_6_line_70 |  | 69 | 70 | 0.028742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4201-26_0_6_line_71 |  | 69 | 71 | 0.013743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4201-26_0_6_line_72 |  | 70 | 80 | 0.0288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4201-26_0_6_line_73 |  | 71 | 81 | 0.0035975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4201-26_0_6_line_74 |  | 72 | 73 | 0.014493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4201-26_0_6_line_75 |  | 72 | 74 | 0.044173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4201-26_0_6_line_76 |  | 73 | 75 | 0.018031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4201-26_0_6_line_77 |  | 73 | 76 | 0.0078671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4201-26_0_6_line_78 |  | 74 | 77 | 0.029628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4201-26_0_6_line_79 |  | 76 | 78 | 0.0098764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4201-26_0_6_line_80 |  | 77 | 79 | 0.020885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4201-26_0_6_line_81 |  | 78 | 83 | 0.020028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4201-26_0_6_line_82 |  | 79 | 91 | 0.01251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4201-26_0_6_line_83 |  | 80 | 88 | 0.031812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4201-26_0_6_line_84 |  | 81 | 86 | 0.0054179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4201-26_0_6_line_85 |  | 82 | 83 | 0.00017501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4201-26_0_6_line_86 |  | 82 | 84 | 0.010145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4201-26_0_6_line_87 |  | 84 | 85 | 0.0064104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4201-26_0_6_line_88 |  | 86 | 87 | 0.017543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4201-26_0_6_line_89 |  | 88 | 89 | 0.043925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_4201-26_0_6_line_90 |  | 89 | 90 | 0.0035285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_4201-26_0_6_line_91 |  | 90 | 95 | 0.059875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
92 | LV_4201-26_0_6_line_92 |  | 91 | 92 | 0.031259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4201-26_0_6_line_93 |  | 92 | 93 | 0.033683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
94 | LV_4201-26_0_6_line_94 |  | 93 | 94 | 0.014066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
95 | LV_4201-26_0_6_line_95 |  | 94 | 97 | 0.018139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
96 | LV_4201-26_0_6_line_96 |  | 94 | 95 | 0.010919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
97 | LV_4201-26_0_6_line_97 |  | 95 | 96 | 0.035894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4201-26_0_6_line_98 |  | 97 | 98 | 0.020976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
99 | LV_4201-26_0_6_line_99 |  | 98 | 100 | 0.018269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4201-26_0_6_trafo_38 | 0.63 MVA 20/0.4 kV | 101 | 55 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2655765.6361 | 1249377.3307 | 2655760.2306 | 1249390.122 | 2655760.4119 | 1249396.3793
1 | 2655765.6361 | 1249377.3307 | 2655772.149 | 1249380.861 | 2655771.2501 | 1249376.0938
2 | 2655771.2501 | 1249376.0938 | 2655772.149 | 1249380.861 | 2655781.3363 | 1249385.017 | 2655806.5975 | 1249396.4625 | 2655814.2622 | 1249397.9468 | 2655821.5352 | 1249397.715 | 2655821.7277 | 1249400.5299 | 2655822.3915 | 1249410.2095
3 | 2655771.2501 | 1249376.0938 | 2655766.2869 | 1249349.8084
4 | 2655822.3915 | 1249410.2095 | 2655821.7277 | 1249400.5299 | 2655821.5352 | 1249397.715 | 2655831.7955 | 1249394.565 | 2655839.7907 | 1249390.6153 | 2655837.8622 | 1249386.1497
5 | 2655822.3915 | 1249410.2095 | 2655827.3657 | 1249424.7885 | 2655833.0409 | 1249439.4965 | 2655837.3895 | 1249450.7452
6 | 2655837.8622 | 1249386.1497 | 2655839.7907 | 1249390.6153 | 2655850.0031 | 1249384.5407 | 2655861.1639 | 1249375.5729 | 2655862.3777 | 1249381.3661
7 | 2655874.3702 | 1249365.8684 | 2655868.2446 | 1249374.1275 | 2655862.3777 | 1249381.3661
8 | 2655862.3777 | 1249381.3661 | 2655859.5912 | 1249388.6227
9 | 2655837.8622 | 1249386.1497 | 2655833.6281 | 1249376.3586 | 2655836.3968 | 1249366.9582
10 | 2655874.3702 | 1249365.8684 | 2655882.2662 | 1249375.6496 | 2655889.0869 | 1249385.7652 | 2655890.5485 | 1249396.5086 | 2655877.0433 | 1249459.5358 | 2655872.2433 | 1249480.251
11 | 2655874.3702 | 1249365.8684 | 2655874.6615 | 1249365.4042 | 2655878.1261 | 1249359.8997 | 2655883.7749 | 1249354.9718 | 2655886.2096 | 1249354.2718
12 | 2655837.3895 | 1249450.7452 | 2655850.0249 | 1249443.3109
13 | 2655837.3895 | 1249450.7452 | 2655838.0773 | 1249460.2805
14 | 2655836.3968 | 1249366.9582 | 2655838.1676 | 1249360.9463 | 2655836.9976 | 1249349.6942 | 2655817.7582 | 1249317.7467 | 2655816.0776 | 1249313.372
15 | 2655964.8484 | 1249343.1726 | 2655964.9902 | 1249348.9445 | 2655986.0802 | 1249348.7435 | 2655986.1804 | 1249354.9264
16 | 2655921.5337 | 1249357.4182 | 2655921.7455 | 1249349.3703 | 2655964.9902 | 1249348.9445 | 2655964.8484 | 1249343.1726
17 | 2655964.8484 | 1249343.1726 | 2655983.3059 | 1249343.0187
18 | 2655986.1804 | 1249354.9264 | 2655993.6488 | 1249354.808 | 2656000.8895 | 1249354.7079
19 | 2655986.1804 | 1249354.9264 | 2655986.5032 | 1249374.2984 | 2655985.7766 | 1249382.0291
20 | 2655986.1804 | 1249354.9264 | 2655986.0802 | 1249348.7435 | 2656010.9093 | 1249348.3665 | 2656017.8263 | 1249348.2651 | 2656027.3701 | 1249348.2441
21 | 2655921.5337 | 1249357.4182 | 2655921.0517 | 1249389.7403
22 | 2655921.5337 | 1249357.4182 | 2655911.7087 | 1249358.4263
23 | 2655911.7087 | 1249358.4263 | 2655910.0791 | 1249358.2997 | 2655901.2027 | 1249353.2015 | 2655890.7401 | 1249352.9694
24 | 2655911.7087 | 1249358.4263 | 2655910.6918 | 1249361.3743 | 2655908.7319 | 1249394.6565 | 2655906.9101 | 1249406.8922 | 2655905.0541 | 1249417.9601 | 2655904.6017 | 1249420.7302
25 | 2655890.7401 | 1249352.9694 | 2655886.2096 | 1249354.2718
26 | 2655904.6017 | 1249420.7302 | 2655903.3953 | 1249428.1181 | 2655901.5278 | 1249443.6112 | 2655902.5441 | 1249451.9265 | 2655907.9462 | 1249453.9343 | 2655910.9027 | 1249454.2136
27 | 2656037.8275 | 1249348.2318 | 2656027.3701 | 1249348.2441
28 | 2656027.3701 | 1249348.2441 | 2656027.7158 | 1249356.4086 | 2656024.3431 | 1249364.9493 | 2656023.31 | 1249373.601 | 2656024.2401 | 1249410.1905 | 2656023.9689 | 1249417.5103
29 | 2656037.8275 | 1249348.2318 | 2656037.7327 | 1249334.7261
30 | 2656000.8895 | 1249354.7079 | 2656011.3339 | 1249354.5637 | 2656013.2043 | 1249359.5737 | 2656014.5921 | 1249396.4789 | 2656014.6172 | 1249422.5859 | 2656013.2559 | 1249447.88
31 | 2655968.4579 | 1249436.671 | 2655969.4126 | 1249426.7287 | 2655973.1515 | 1249414.5667 | 2655979.3652 | 1249404.196 | 2655984.7657 | 1249392.7836 | 2655985.7766 | 1249382.0291
32 | 2655731.5889 | 1249656.2582 | 2655732.6304 | 1249641.8469 | 2655733.3101 | 1249627.0294
33 | 2655733.3101 | 1249627.0294 | 2655640.2908 | 1249619.7014
34 | 2655805.9593 | 1249663.8961 | 2655743.3684 | 1249652.066 | 2655731.5889 | 1249656.2582
35 | 2655838.0773 | 1249460.2805 | 2655808.3662 | 1249473.232
36 | 2655838.0773 | 1249460.2805 | 2655839.6358 | 1249479.9865 | 2655838.1012 | 1249501.8742
37 | 2656002.7417 | 1249657.3799 | 2656014.8932 | 1249659.3961 | 2656034.7075 | 1249661.2952
38 | 2656002.7417 | 1249657.3799 | 2656001.2802 | 1249662.6364 | 2655997.4473 | 1249663.9789 | 2655995.0877 | 1249666.803 | 2655992.6161 | 1249674.5511
39 | 2656002.7417 | 1249657.3799 | 2656004.5544 | 1249652.5159 | 2656004.1755 | 1249651.9222
40 | 2655970.7876 | 1249711.2376 | 2655975.3107 | 1249712.7591 | 2655981.6354 | 1249694.5952 | 2655987.5615 | 1249673.8813 | 2655991.473 | 1249655.4277 | 2656002.7417 | 1249657.3799
41 | 2656053.4337 | 1249662.7848 | 2656045.7821 | 1249662.3566 | 2656034.7075 | 1249661.2952
42 | 2655986.4612 | 1249693.8458 | 2655992.6161 | 1249674.5511
43 | 2655970.7876 | 1249711.2376 | 2655982.9421 | 1249677.7515 | 2655992.1119 | 1249640.5457 | 2655997.3574 | 1249608.7623 | 2655998.5236 | 1249601.0805
44 | 2655970.7876 | 1249711.2376 | 2655969.0642 | 1249710.6543 | 2655968.0456 | 1249707.3869 | 2655971.4835 | 1249696.9429
45 | 2656006.4843 | 1249534.441 | 2656006.1702 | 1249538.2525 | 2656002.7678 | 1249573.1221 | 2655998.5236 | 1249601.0805
46 | 2655975.3189 | 1249678.4052 | 2655975.321 | 1249685.2847 | 2655971.4835 | 1249696.9429
47 | 2656086.5097 | 1249332.2366 | 2656086.1151 | 1249336.7137 | 2656084.6445 | 1249349.9619
48 | 2656078.079 | 1249379.2781 | 2656080.6229 | 1249368.9617 | 2656084.5221 | 1249351.064 | 2656084.6445 | 1249349.9619
49 | 2656011.8455 | 1249469.6566 | 2656012.5107 | 1249461.7263 | 2656013.2559 | 1249447.88
50 | 2655968.4579 | 1249436.671 | 2655967.9287 | 1249456.7353
51 | 2655805.9593 | 1249663.8961 | 2655824.1882 | 1249667.5369 | 2655829.9329 | 1249668.7614
52 | 2655805.9593 | 1249663.8961 | 2655805.9642 | 1249630.1197
53 | 2656010.1408 | 1249490.0651 | 2656006.4843 | 1249534.441
54 | 2656010.1408 | 1249490.0651 | 2656010.5452 | 1249485.1572 | 2656011.8455 | 1249469.6566
55 | 2656053.4337 | 1249662.7848 | 2656054.6335 | 1249682.5689
56 | 2656053.4337 | 1249662.7848 | 2656051.3237 | 1249619.9474
57 | 2655967.9287 | 1249456.7353 | 2655954.3549 | 1249455.3226
58 | 2655967.9287 | 1249456.7353 | 2655967.2701 | 1249485.7136
59 | 2655967.2701 | 1249485.7136 | 2655967.1146 | 1249492.5575
60 | 2655965.0298 | 1249523.0536 | 2655966.934 | 1249500.5005 | 2655967.1146 | 1249492.5575
61 | 2655965.0298 | 1249523.0536 | 2655963.5042 | 1249538.0083
62 | 2655835.9177 | 1249531.7907 | 2655830.4059 | 1249587.7627 | 2655805.9682 | 1249602.0091 | 2655805.9642 | 1249630.1197
63 | 2655836.2166 | 1249528.7545 | 2655835.9177 | 1249531.7907
64 | 2655836.2166 | 1249528.7545 | 2655838.1012 | 1249501.8742
65 | 2656177.2997 | 1249330.5838 | 2656177.3464 | 1249341.447 | 2656177.814 | 1249358.1095
66 | 2656177.2215 | 1249312.4148 | 2656177.2997 | 1249330.5838
67 | 2656177.814 | 1249358.1095 | 2656178.6333 | 1249387.3019 | 2656178.2747 | 1249391.6793 | 2656171.2296 | 1249404.8455
68 | 2656177.2215 | 1249312.4148 | 2656158.3037 | 1249312.847 | 2656151.3136 | 1249311.8802 | 2656145.9873 | 1249310.6289 | 2656141.8169 | 1249311.7012 | 2656137.1439 | 1249314.0253 | 2656135.1426 | 1249314.073 | 2656132.4972 | 1249312.7693 | 2656131.8712 | 1249310.3061
69 | 2656146.8184 | 1249455.6254 | 2656146.7298 | 1249450.6323 | 2656171.2296 | 1249404.8455
70 | 2656146.8184 | 1249455.6254 | 2656147.0784 | 1249469.6264 | 2656147.2535 | 1249484.3639
71 | 2656146.8184 | 1249455.6254 | 2656133.0928 | 1249454.9264
72 | 2656147.2535 | 1249484.3639 | 2656147.5955 | 1249513.1615
73 | 2656130.2177 | 1249453.8639 | 2656130.4575 | 1249454.7922 | 2656133.0928 | 1249454.9264
74 | 2656078.079 | 1249379.2781 | 2656092.4171 | 1249381.6598
75 | 2656078.079 | 1249379.2781 | 2656068.1702 | 1249417.0882 | 2656067.1564 | 1249422.0722
76 | 2656092.4171 | 1249381.6598 | 2656089.116 | 1249399.3852
77 | 2656092.4171 | 1249381.6598 | 2656100.2841 | 1249381.7009 | 2656100.2841 | 1249381.7009
78 | 2656067.1564 | 1249422.0722 | 2656061.2509 | 1249451.1056
79 | 2656105.6676 | 1249373.6936 | 2656102.4812 | 1249380.1094 | 2656100.2841 | 1249381.7009
80 | 2656057.088 | 1249471.5714 | 2656061.2509 | 1249451.1056
81 | 2656105.6676 | 1249373.6936 | 2656109.6318 | 1249365.7116 | 2656113.2583 | 1249362.2658 | 2656119.3386 | 1249361.6326
82 | 2656057.088 | 1249471.5714 | 2656056.7597 | 1249473.1856 | 2656055.0772 | 1249483.9177
83 | 2656149.3171 | 1249544.9217 | 2656147.658 | 1249518.4211 | 2656147.5955 | 1249513.1615
84 | 2656130.2177 | 1249453.8639 | 2656128.8628 | 1249448.6182
85 | 2656119.5126 | 1249361.6145 | 2656119.3386 | 1249361.6326
86 | 2656119.5126 | 1249361.6145 | 2656126.8623 | 1249360.8491 | 2656129.1936 | 1249359.3805
87 | 2656134.6175 | 1249355.9636 | 2656129.1936 | 1249359.3805
88 | 2656115.3251 | 1249443.0187 | 2656127.5296 | 1249443.4567 | 2656128.8628 | 1249448.6182
89 | 2656149.3171 | 1249544.9217 | 2656142.1953 | 1249545.9439 | 2656116.4221 | 1249537.672 | 2656107.2451 | 1249534.6477
90 | 2656103.8939 | 1249533.5432 | 2656107.2451 | 1249534.6477
91 | 2656059.946 | 1249559.3751 | 2656065.7149 | 1249559.3074 | 2656072.286 | 1249555.8449 | 2656077.1826 | 1249549.8204 | 2656078.4213 | 1249537.8016 | 2656097.5604 | 1249531.456 | 2656103.8939 | 1249533.5432
92 | 2656055.0772 | 1249483.9177 | 2656051.6897 | 1249505.5266 | 2656051.1127 | 1249514.8953
93 | 2656051.1127 | 1249514.8953 | 2656050.1108 | 1249531.1627 | 2656049.5598 | 1249544.7224 | 2656049.5736 | 1249548.5358
94 | 2656049.6247 | 1249562.602 | 2656049.5736 | 1249548.5358
95 | 2656049.6247 | 1249562.602 | 2656049.6959 | 1249580.7412
96 | 2656049.6247 | 1249562.602 | 2656053.1834 | 1249562.3243 | 2656059.946 | 1249559.3751
97 | 2656059.946 | 1249559.3751 | 2656063.709 | 1249555.8527 | 2656068.1751 | 1249549.8463 | 2656069.6668 | 1249543.8007 | 2656071.4127 | 1249526.85
98 | 2656049.6959 | 1249580.7412 | 2656049.7221 | 1249587.4311 | 2656050.425 | 1249601.7003
99 | 2656050.425 | 1249601.7003 | 2656051.3237 | 1249619.9474

## bus_geodata
| x | y | coords
0 | 2655760.4119 | 1249396.3793
1 | 2655765.6361 | 1249377.3307
2 | 2655771.2501 | 1249376.0938
3 | 2655822.3915 | 1249410.2095
4 | 2655766.2869 | 1249349.8084
5 | 2655862.3777 | 1249381.3661
6 | 2655837.8622 | 1249386.1497
7 | 2655874.3702 | 1249365.8684
8 | 2655859.5912 | 1249388.6227
9 | 2655837.3895 | 1249450.7452
10 | 2655836.3968 | 1249366.9582
11 | 2655964.8484 | 1249343.1726
12 | 2655986.1804 | 1249354.9264
13 | 2655921.5337 | 1249357.4182
14 | 2655983.3059 | 1249343.0187
15 | 2655911.7087 | 1249358.4263
16 | 2655890.7401 | 1249352.9694
17 | 2655904.6017 | 1249420.7302
18 | 2655872.2433 | 1249480.251
19 | 2655886.2096 | 1249354.2718
20 | 2656027.3701 | 1249348.2441
21 | 2656037.8275 | 1249348.2318
22 | 2656023.9689 | 1249417.5103
23 | 2656000.8895 | 1249354.7079
24 | 2655985.7766 | 1249382.0291
25 | 2655921.0517 | 1249389.7403
26 | 2655733.3101 | 1249627.0294
27 | 2655731.5889 | 1249656.2582
28 | 2655640.2908 | 1249619.7014
29 | 2655850.0249 | 1249443.3109
30 | 2655838.0773 | 1249460.2805
31 | 2655816.0776 | 1249313.372
32 | 2656002.7417 | 1249657.3799
33 | 2656034.7075 | 1249661.2952
34 | 2655992.6161 | 1249674.5511
35 | 2656004.1755 | 1249651.9222
36 | 2655970.7876 | 1249711.2376
37 | 2655998.5236 | 1249601.0805
38 | 2655971.4835 | 1249696.9429
39 | 2655910.9027 | 1249454.2136
40 | 2656037.7327 | 1249334.7261
41 | 2656086.5097 | 1249332.2366
42 | 2656084.6445 | 1249349.9619
43 | 2656013.2559 | 1249447.88
44 | 2655968.4579 | 1249436.671
45 | 2655805.9593 | 1249663.8961
46 | 2655975.3189 | 1249678.4052
47 | 2656006.4843 | 1249534.441
48 | 2656010.1408 | 1249490.0651
49 | 2656053.4337 | 1249662.7848
50 | 2655986.4612 | 1249693.8458
51 | 2656011.8455 | 1249469.6566
52 | 2655967.9287 | 1249456.7353
53 | 2655954.3549 | 1249455.3226
54 | 2655967.2701 | 1249485.7136
55 | 2655967.1146 | 1249492.5575
56 | 2655963.5042 | 1249538.0083
57 | 2655965.0298 | 1249523.0536
58 | 2655829.9329 | 1249668.7614
59 | 2655805.9642 | 1249630.1197
60 | 2655835.9177 | 1249531.7907
61 | 2655838.1012 | 1249501.8742
62 | 2655836.2166 | 1249528.7545
63 | 2655808.3662 | 1249473.232
64 | 2656177.2997 | 1249330.5838
65 | 2656177.814 | 1249358.1095
66 | 2656177.2215 | 1249312.4148
67 | 2656171.2296 | 1249404.8455
68 | 2656131.8712 | 1249310.3061
69 | 2656146.8184 | 1249455.6254
70 | 2656147.2535 | 1249484.3639
71 | 2656133.0928 | 1249454.9264
72 | 2656078.079 | 1249379.2781
73 | 2656092.4171 | 1249381.6598
74 | 2656067.1564 | 1249422.0722
75 | 2656089.116 | 1249399.3852
76 | 2656100.2841 | 1249381.7009
77 | 2656061.2509 | 1249451.1056
78 | 2656105.6676 | 1249373.6936
79 | 2656057.088 | 1249471.5714
80 | 2656147.5955 | 1249513.1615
81 | 2656130.2177 | 1249453.8639
82 | 2656119.5126 | 1249361.6145
83 | 2656119.3386 | 1249361.6326
84 | 2656129.1936 | 1249359.3805
85 | 2656134.6175 | 1249355.9636
86 | 2656128.8628 | 1249448.6182
87 | 2656115.3251 | 1249443.0187
88 | 2656149.3171 | 1249544.9217
89 | 2656107.2451 | 1249534.6477
90 | 2656103.8939 | 1249533.5432
91 | 2656055.0772 | 1249483.9177
92 | 2656051.1127 | 1249514.8953
93 | 2656049.5736 | 1249548.5358
94 | 2656049.6247 | 1249562.602
95 | 2656059.946 | 1249559.3751
96 | 2656071.4127 | 1249526.85
97 | 2656049.6959 | 1249580.7412
98 | 2656050.425 | 1249601.7003
99 | 2656054.6335 | 1249682.5689
100 | 2656051.3237 | 1249619.9474
101 | 2655965.0298 | 1249523.0536

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1