## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4204-9_1_2_node_22 | 0.4 | n |  | TRUE
1 | bus_LV_4204-9_1_2_node_24 | 0.4 | n |  | TRUE
2 | bus_LV_4204-9_1_2_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_4204-9_1_2_node_25 | 0.4 | n |  | TRUE
4 | bus_LV_4204-9_1_2_node_26 | 0.4 | n |  | TRUE
5 | bus_LV_4204-9_1_2_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_4204-9_1_2_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_4204-9_1_2_node_29 | 0.4 | n |  | TRUE
8 | bus_LV_4204-9_1_2_node_30 | 0.4 | n |  | TRUE
9 | bus_LV_4204-9_1_2_node_31 | 0.4 | n |  | TRUE
10 | bus_LV_4204-9_1_2_node_134 | 0.4 | n |  | TRUE
11 | bus_LV_4204-9_1_2_node_133 | 0.4 | n |  | TRUE
12 | bus_LV_4204-9_1_2_node_55 | 0.4 | n |  | TRUE
13 | bus_LV_4204-9_1_2_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_4204-9_1_2_node_135 | 0.4 | n |  | TRUE
15 | bus_LV_4204-9_1_2_node_128 | 0.4 | n |  | TRUE
16 | bus_LV_4204-9_1_2_node_132 | 0.4 | n |  | TRUE
17 | bus_LV_4204-9_1_2_node_57 | 0.4 | n |  | TRUE
18 | bus_LV_4204-9_1_2_node_53 | 0.4 | n |  | TRUE
19 | bus_LV_4204-9_1_2_node_131 | 0.4 | n |  | TRUE
20 | bus_LV_4204-9_1_2_node_58 | 0.4 | n |  | TRUE
21 | bus_LV_4204-9_1_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_4204-9_1_2_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_4204-9_1_2_node_61 | 0.4 | n |  | TRUE
24 | bus_LV_4204-9_1_2_node_69 | 0.4 | n |  | TRUE
25 | bus_LV_4204-9_1_2_node_71 | 0.4 | n |  | TRUE
26 | bus_LV_4204-9_1_2_node_242 | 0.4 | n |  | TRUE
27 | bus_LV_4204-9_1_2_node_244 | 0.4 | n |  | TRUE
28 | bus_LV_4204-9_1_2_node_145 | 0.4 | n |  | TRUE
29 | bus_LV_4204-9_1_2_node_88 | 0.4 | n |  | TRUE
30 | bus_LV_4204-9_1_2_node_89 | 0.4 | n |  | TRUE
31 | bus_LV_4204-9_1_2_node_90 | 0.4 | n |  | TRUE
32 | bus_LV_4204-9_1_2_node_92 | 0.4 | n |  | TRUE
33 | bus_LV_4204-9_1_2_node_93 | 0.4 | n |  | TRUE
34 | bus_LV_4204-9_1_2_node_91 | 0.4 | n |  | TRUE
35 | bus_LV_4204-9_1_2_node_94 | 0.4 | n |  | TRUE
36 | bus_LV_4204-9_1_2_node_95 | 0.4 | n |  | TRUE
37 | bus_LV_4204-9_1_2_node_98 | 0.4 | n |  | TRUE
38 | bus_LV_4204-9_1_2_node_99 | 0.4 | n |  | TRUE
39 | bus_LV_4204-9_1_2_node_107 | 0.4 | n |  | TRUE
40 | bus_LV_4204-9_1_2_node_108 | 0.4 | n |  | TRUE
41 | bus_LV_4204-9_1_2_node_109 | 0.4 | n |  | TRUE
42 | bus_LV_4204-9_1_2_node_96 | 0.4 | n |  | TRUE
43 | bus_LV_4204-9_1_2_node_110 | 0.4 | n |  | TRUE
44 | bus_LV_4204-9_1_2_node_111 | 0.4 | n |  | TRUE
45 | bus_LV_4204-9_1_2_node_97 | 0.4 | n |  | TRUE
46 | bus_LV_4204-9_1_2_node_103 | 0.4 | n |  | TRUE
47 | bus_LV_4204-9_1_2_node_100 | 0.4 | n |  | TRUE
48 | bus_LV_4204-9_1_2_node_104 | 0.4 | n |  | TRUE
49 | bus_LV_4204-9_1_2_node_221 | 0.4 | n |  | TRUE
50 | bus_LV_4204-9_1_2_node_220 | 0.4 | n |  | TRUE
51 | bus_LV_4204-9_1_2_node_112 | 0.4 | n |  | TRUE
52 | bus_LV_4204-9_1_2_node_126 | 0.4 | n |  | TRUE
53 | bus_LV_4204-9_1_2_node_239 | 0.4 | n |  | TRUE
54 | bus_LV_4204-9_1_2_node_106 | 0.4 | n |  | TRUE
55 | bus_LV_4204-9_1_2_node_102 | 0.4 | n |  | TRUE
56 | bus_LV_4204-9_1_2_node_101 | 0.4 | n |  | TRUE
57 | bus_LV_4204-9_1_2_node_105 | 0.4 | n |  | TRUE
58 | bus_LV_4204-9_1_2_node_127 | 0.4 | n |  | TRUE
59 | bus_LV_4204-9_1_2_node_137 | 0.4 | n |  | TRUE
60 | bus_LV_4204-9_1_2_node_122 | 0.4 | n |  | TRUE
61 | bus_LV_4204-9_1_2_node_138 | 0.4 | n |  | TRUE
62 | bus_LV_4204-9_1_2_node_113 | 0.4 | n |  | TRUE
63 | bus_LV_4204-9_1_2_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_4204-9_1_2_node_125 | 0.4 | n |  | TRUE
65 | bus_LV_4204-9_1_2_node_228 | 0.4 | n |  | TRUE
66 | bus_LV_4204-9_1_2_node_115 | 0.4 | n |  | TRUE
67 | bus_LV_4204-9_1_2_node_118 | 0.4 | n |  | TRUE
68 | bus_LV_4204-9_1_2_node_121 | 0.4 | n |  | TRUE
69 | bus_LV_4204-9_1_2_node_116 | 0.4 | n |  | TRUE
70 | bus_LV_4204-9_1_2_node_117 | 0.4 | n |  | TRUE
71 | bus_LV_4204-9_1_2_node_119 | 0.4 | n |  | TRUE
72 | bus_LV_4204-9_1_2_node_120 | 0.4 | n |  | TRUE
73 | bus_LV_4204-9_1_2_node_123 | 0.4 | n |  | TRUE
74 | bus_LV_4204-9_1_2_node_144 | 0.4 | n |  | TRUE
75 | bus_LV_4204-9_1_2_node_236 | 0.4 | n |  | TRUE
76 | bus_LV_4204-9_1_2_node_142 | 0.4 | n |  | TRUE
77 | bus_LV_4204-9_1_2_node_124 | 0.4 | n |  | TRUE
78 | bus_LV_4204-9_1_2_node_130 | 0.4 | n |  | TRUE
79 | bus_LV_4204-9_1_2_node_210 | 0.4 | n |  | TRUE
80 | bus_LV_4204-9_1_2_node_235 | 0.4 | n |  | TRUE
81 | bus_LV_4204-9_1_2_node_232 | 0.4 | n |  | TRUE
82 | bus_LV_4204-9_1_2_node_208 | 0.4 | n |  | TRUE
83 | bus_LV_4204-9_1_2_node_136 | 0.4 | n |  | TRUE
84 | bus_LV_4204-9_1_2_node_139 | 0.4 | n |  | TRUE
85 | bus_LV_4204-9_1_2_node_140 | 0.4 | n |  | TRUE
86 | bus_LV_4204-9_1_2_node_141 | 0.4 | n |  | TRUE
87 | bus_LV_4204-9_1_2_node_143 | 0.4 | n |  | TRUE
88 | bus_LV_4204-9_1_2_node_146 | 0.4 | n |  | TRUE
89 | bus_LV_4204-9_1_2_node_243 | 0.4 | n |  | TRUE
90 | bus_LV_4204-9_1_2_node_247 | 0.4 | n |  | TRUE
91 | bus_LV_4204-9_1_2_node_255 | 0.4 | n |  | TRUE
92 | bus_LV_4204-9_1_2_node_156 | 0.4 | n |  | TRUE
93 | bus_LV_4204-9_1_2_node_212 | 0.4 | n |  | TRUE
94 | bus_LV_4204-9_1_2_node_213 | 0.4 | n |  | TRUE
95 | bus_LV_4204-9_1_2_node_158 | 0.4 | n |  | TRUE
96 | bus_LV_4204-9_1_2_node_159 | 0.4 | n |  | TRUE
97 | bus_LV_4204-9_1_2_node_160 | 0.4 | n |  | TRUE
98 | bus_LV_4204-9_1_2_node_161 | 0.4 | n |  | TRUE
99 | bus_LV_4204-9_1_2_node_162 | 0.4 | n |  | TRUE
100 | bus_LV_4204-9_1_2_node_163 | 0.4 | n |  | TRUE
101 | bus_LV_4204-9_1_2_node_164 | 0.4 | n |  | TRUE
102 | bus_LV_4204-9_1_2_node_172 | 0.4 | n |  | TRUE
103 | bus_LV_4204-9_1_2_node_246 | 0.4 | n |  | TRUE
104 | bus_LV_4204-9_1_2_node_168 | 0.4 | n |  | TRUE
105 | bus_LV_4204-9_1_2_node_241 | 0.4 | n |  | TRUE
106 | bus_LV_4204-9_1_2_node_165 | 0.4 | n |  | TRUE
107 | bus_LV_4204-9_1_2_node_166 | 0.4 | n |  | TRUE
108 | bus_LV_4204-9_1_2_node_167 | 0.4 | n |  | TRUE
109 | bus_LV_4204-9_1_2_node_169 | 0.4 | n |  | TRUE
110 | bus_LV_4204-9_1_2_node_170 | 0.4 | n |  | TRUE
111 | bus_LV_4204-9_1_2_node_171 | 0.4 | n |  | TRUE
112 | bus_LV_4204-9_1_2_node_173 | 0.4 | n |  | TRUE
113 | bus_LV_4204-9_1_2_node_174 | 0.4 | n |  | TRUE
114 | bus_LV_4204-9_1_2_node_175 | 0.4 | n |  | TRUE
115 | bus_LV_4204-9_1_2_node_176 | 0.4 | n |  | TRUE
116 | bus_LV_4204-9_1_2_node_207 | 0.4 | n |  | TRUE
117 | bus_LV_4204-9_1_2_node_252 | 0.4 | n |  | TRUE
118 | bus_LV_4204-9_1_2_node_230 | 0.4 | n |  | TRUE
119 | bus_LV_4204-9_1_2_node_216 | 0.4 | n |  | TRUE
120 | bus_LV_4204-9_1_2_node_209 | 0.4 | n |  | TRUE
121 | bus_LV_4204-9_1_2_node_205 | 0.4 | n |  | TRUE
122 | bus_LV_4204-9_1_2_node_229 | 0.4 | n |  | TRUE
123 | bus_LV_4204-9_1_2_node_219 | 0.4 | n |  | TRUE
124 | bus_LV_4204-9_1_2_node_214 | 0.4 | n |  | TRUE
125 | bus_LV_4204-9_1_2_node_206 | 0.4 | n |  | TRUE
126 | bus_LV_4204-9_1_2_node_211 | 0.4 | n |  | TRUE
127 | bus_LV_4204-9_1_2_node_233 | 0.4 | n |  | TRUE
128 | bus_LV_4204-9_1_2_node_215 | 0.4 | n |  | TRUE
129 | bus_LV_4204-9_1_2_node_217 | 0.4 | n |  | TRUE
130 | bus_LV_4204-9_1_2_node_218 | 0.4 | n |  | TRUE
131 | bus_LV_4204-9_1_2_node_240 | 0.4 | n |  | TRUE
132 | bus_LV_4204-9_1_2_node_222 | 0.4 | n |  | TRUE
133 | bus_LV_4204-9_1_2_node_223 | 0.4 | n |  | TRUE
134 | bus_LV_4204-9_1_2_node_224 | 0.4 | n |  | TRUE
135 | bus_LV_4204-9_1_2_node_225 | 0.4 | n |  | TRUE
136 | bus_LV_4204-9_1_2_node_226 | 0.4 | n |  | TRUE
137 | bus_LV_4204-9_1_2_node_227 | 0.4 | n |  | TRUE
138 | bus_LV_4204-9_1_2_node_234 | 0.4 | n |  | TRUE
139 | bus_LV_4204-9_1_2_node_315 | 0.4 | n |  | TRUE
140 | bus_LV_4204-9_1_2_node_327 | 0.4 | n |  | TRUE
141 | bus_LV_4204-9_1_2_node_248 | 0.4 | n |  | TRUE
142 | bus_LV_4204-9_1_2_node_245 | 0.4 | n |  | TRUE
143 | bus_LV_4204-9_1_2_node_254 | 0.4 | n |  | TRUE
144 | bus_LV_4204-9_1_2_node_253 | 0.4 | n |  | TRUE
145 | bus_LV_4204-9_1_2_node_251 | 0.4 | n |  | TRUE
146 | bus_LV_4204-9_1_2_node_256 | 0.4 | n |  | TRUE
147 | bus_LV_4204-9_1_2_node_310 | 0.4 | n |  | TRUE
148 | bus_LV_4204-9_1_2_node_311 | 0.4 | n |  | TRUE
149 | bus_LV_4204-9_1_2_node_312 | 0.4 | n |  | TRUE
150 | bus_LV_4204-9_1_2_node_313 | 0.4 | n |  | TRUE
151 | bus_LV_4204-9_1_2_node_317 | 0.4 | n |  | TRUE
152 | bus_LV_4204-9_1_2_node_316 | 0.4 | n |  | TRUE
153 | bus_LV_4204-9_1_2_node_325 | 0.4 | n |  | TRUE
154 | bus_LV_4204-9_1_2_node_330 | 0.4 | n |  | TRUE
155 | bus_LV_4204-9_1_2_node_318 | 0.4 | n |  | TRUE
156 | bus_LV_4204-9_1_2_node_331 | 0.4 | n |  | TRUE
157 | bus_LV_4204-9_1_2_node_329 | 0.4 | n |  | TRUE
158 | bus_LV_4204-9_1_2_node_319 | 0.4 | n |  | TRUE
159 | bus_LV_4204-9_1_2_node_320 | 0.4 | n |  | TRUE
160 | bus_LV_4204-9_1_2_node_333 | 0.4 | n |  | TRUE
161 | bus_LV_4204-9_1_2_node_326 | 0.4 | n |  | TRUE
162 | bus_LV_4204-9_1_2_node_332 | 0.4 | n |  | TRUE
163 | bus_LV_4204-9_1_2_node_328 | 0.4 | n |  | TRUE
164 | bus_MV_484_0_node_163 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4204-9_1_2_load_22 | 0 | 0.0011974 | 0.00030011 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4204-9_1_2_load_24 | 1 | 0.0029687 | 0.00074403 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4204-9_1_2_load_23 | 2 | 0.0020277 | 0.00050818 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4204-9_1_2_load_26 | 4 | 0.0021273 | 0.00053314 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4204-9_1_2_load_27 | 5 | 0.0018053 | 0.00045246 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4204-9_1_2_load_28 | 6 | 0.0025511 | 0.00063937 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4204-9_1_2_load_29 | 7 | 0.0022767 | 0.00057059 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4204-9_1_2_load_133 | 11 | 0.0017461 | 0.00043761 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4204-9_1_2_load_55 | 12 | 0.003355 | 0.00084085 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4204-9_1_2_load_52 | 13 | 0.0013579 | 0.00034032 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4204-9_1_2_load_135 | 14 | 0.0017182 | 0.00043062 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4204-9_1_2_load_128 | 15 | 0.002294 | 0.00057493 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4204-9_1_2_load_132 | 16 | 0.0012482 | 0.00031283 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4204-9_1_2_load_57 | 17 | 0.0022435 | 0.00056227 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4204-9_1_2_load_53 | 18 | 0.0028398 | 0.00071171 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4204-9_1_2_load_131 | 19 | 0.0016197 | 0.00040594 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4204-9_1_2_load_58 | 20 | 0.0026439 | 0.00066262 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4204-9_1_2_load_59 | 21 | 0.0016363 | 0.00041009 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4204-9_1_2_load_60 | 22 | 0.00090804 | 0.00022758 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4204-9_1_2_load_61 | 23 | 0.003429 | 0.00085938 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4204-9_1_2_load_69 | 24 | 0.0029529 | 0.00074007 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4204-9_1_2_load_71 | 25 | 0.0015765 | 0.00039511 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4204-9_1_2_load_244 | 27 | 0.00097049 | 0.00024323 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4204-9_1_2_load_88 | 29 | 0.0019399 | 0.00048618 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4204-9_1_2_load_89 | 30 | 0.0044705 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4204-9_1_2_load_93 | 33 | 0.0018813 | 0.0004715 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4204-9_1_2_load_95 | 36 | 0.0044733 | 0.0011211 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4204-9_1_2_load_98 | 37 | 0.0044754 | 0.0011217 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4204-9_1_2_load_99 | 38 | 0.0017091 | 0.00042834 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4204-9_1_2_load_107 | 39 | 0.0024322 | 0.00060956 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4204-9_1_2_load_108 | 40 | 0.0012243 | 0.00030683 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4204-9_1_2_load_109 | 41 | 0.002144 | 0.00053735 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4204-9_1_2_load_111 | 44 | 0.0015793 | 0.00039582 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4204-9_1_2_load_100 | 47 | 0.015018 | 0.0037639 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4204-9_1_2_load_104 | 48 | 0.0044719 | 0.0011208 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4204-9_1_2_load_220 | 50 | 0.0011227 | 0.00028136 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4204-9_1_2_load_126 | 52 | 0.0012494 | 0.00031313 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4204-9_1_2_load_106 | 54 | 0.0093842 | 0.0023519 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4204-9_1_2_load_101 | 56 | 0.0041781 | 0.0010471 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4204-9_1_2_load_127 | 58 | 0.0015159 | 0.00037992 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4204-9_1_2_load_122 | 60 | 0.0015141 | 0.00037947 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4204-9_1_2_load_138 | 61 | 0.0047801 | 0.001198 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4204-9_1_2_load_113 | 62 | 0.0028638 | 0.00071772 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4204-9_1_2_load_114 | 63 | 0.004468 | 0.0011198 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4204-9_1_2_load_125 | 64 | 0.0018706 | 0.00046883 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4204-9_1_2_load_228 | 65 | 0.0023385 | 0.00058609 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4204-9_1_2_load_115 | 66 | 0.0021505 | 0.00053898 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4204-9_1_2_load_121 | 68 | 0.0034661 | 0.00086869 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4204-9_1_2_load_116 | 69 | 0.0044735 | 0.0011212 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4204-9_1_2_load_119 | 71 | 0.0017077 | 0.00042798 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4204-9_1_2_load_120 | 72 | 0.0019165 | 0.00048031 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4204-9_1_2_load_123 | 73 | 0.0012885 | 0.00032292 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4204-9_1_2_load_236 | 75 | 0.0010753 | 0.00026949 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4204-9_1_2_load_124 | 77 | 0.0018721 | 0.00046919 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4204-9_1_2_load_130 | 78 | 0.0018218 | 0.00045658 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4204-9_1_2_load_235 | 80 | 0.00096899 | 0.00024285 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4204-9_1_2_load_232 | 81 | 0.00078849 | 0.00019761 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4204-9_1_2_load_208 | 82 | 0.0010643 | 0.00026675 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4204-9_1_2_load_136 | 83 | 0.0022023 | 0.00055195 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4204-9_1_2_load_139 | 84 | 0.003036 | 0.0007609 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4204-9_1_2_load_140 | 85 | 0.0012991 | 0.00032558 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4204-9_1_2_load_141 | 86 | 0.0013236 | 0.00033172 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4204-9_1_2_load_143 | 87 | 0.0013044 | 0.00032692 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4204-9_1_2_load_146 | 88 | 0.003594 | 0.00090075 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4204-9_1_2_load_243 | 89 | 0.0020939 | 0.00052479 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4204-9_1_2_load_255 | 91 | 0.0015713 | 0.0003938 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4204-9_1_2_load_156 | 92 | 0.0017625 | 0.00044173 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4204-9_1_2_load_212 | 93 | 0.00081704 | 0.00020477 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4204-9_1_2_load_213 | 94 | 0.00089986 | 0.00022553 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4204-9_1_2_load_158 | 95 | 0.0015335 | 0.00038433 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4204-9_1_2_load_159 | 96 | 0.0016152 | 0.0004048 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4204-9_1_2_load_160 | 97 | 0.0024009 | 0.00060172 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4204-9_1_2_load_161 | 98 | 0.0012545 | 0.0003144 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4204-9_1_2_load_162 | 99 | 0.0011821 | 0.00029625 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4204-9_1_2_load_163 | 100 | 0.00092424 | 0.00023164 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4204-9_1_2_load_164 | 101 | 0.0012837 | 0.00032172 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4204-9_1_2_load_172 | 102 | 0.0010803 | 0.00027074 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4204-9_1_2_load_241 | 105 | 0.0021063 | 0.0005279 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4204-9_1_2_load_165 | 106 | 0.0011391 | 0.00028548 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4204-9_1_2_load_166 | 107 | 0.0010442 | 0.00026171 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4204-9_1_2_load_171 | 111 | 0.0019228 | 0.0004819 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4204-9_1_2_load_173 | 112 | 0.0012587 | 0.00031546 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4204-9_1_2_load_174 | 113 | 0.00088308 | 0.00022132 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4204-9_1_2_load_175 | 114 | 0.00093412 | 0.00023411 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4204-9_1_2_load_176 | 115 | 0.00072307 | 0.00018122 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4204-9_1_2_load_252 | 117 | 0.0008041 | 0.00020153 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4204-9_1_2_load_230 | 118 | 0.00093256 | 0.00023372 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4204-9_1_2_load_209 | 120 | 0.0010649 | 0.00026689 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4204-9_1_2_load_205 | 121 | 0.00076315 | 0.00019126 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4204-9_1_2_load_229 | 122 | 0.00093377 | 0.00023403 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4204-9_1_2_load_219 | 123 | 0.00091182 | 0.00022852 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4204-9_1_2_load_206 | 125 | 0.00087566 | 0.00021946 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4204-9_1_2_load_211 | 126 | 0.00096852 | 0.00024274 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4204-9_1_2_load_233 | 127 | 0.0017728 | 0.0004443 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4204-9_1_2_load_215 | 128 | 0.001603 | 0.00040175 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4204-9_1_2_load_217 | 129 | 0.00095782 | 0.00024005 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4204-9_1_2_load_218 | 130 | 0.0013104 | 0.00032841 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4204-9_1_2_load_240 | 131 | 0.001513 | 0.0003792 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4204-9_1_2_load_222 | 132 | 0.001692 | 0.00042405 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4204-9_1_2_load_223 | 133 | 0.0017455 | 0.00043746 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4204-9_1_2_load_224 | 134 | 0.0022926 | 0.00057458 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4204-9_1_2_load_225 | 135 | 0.0016949 | 0.00042478 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4204-9_1_2_load_226 | 136 | 0.0025494 | 0.00063894 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4204-9_1_2_load_227 | 137 | 0.0017088 | 0.00042826 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4204-9_1_2_load_234 | 138 | 0.001592 | 0.00039898 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4204-9_1_2_load_315 | 139 | 0.00083546 | 0.00020938 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4204-9_1_2_load_327 | 140 | 0.0009399 | 0.00023556 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4204-9_1_2_load_248 | 141 | 0.0023123 | 0.00057952 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4204-9_1_2_load_245 | 142 | 0.001355 | 0.0003396 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4204-9_1_2_load_254 | 143 | 0.0018791 | 0.00047096 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4204-9_1_2_load_253 | 144 | 0.0025739 | 0.00064507 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4204-9_1_2_load_251 | 145 | 0.0028716 | 0.00071968 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4204-9_1_2_load_256 | 146 | 0.0050185 | 0.0012578 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4204-9_1_2_load_310 | 147 | 0.00074365 | 0.00018638 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4204-9_1_2_load_311 | 148 | 0.00083542 | 0.00020937 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4204-9_1_2_load_312 | 149 | 0.00095955 | 0.00024049 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4204-9_1_2_load_313 | 150 | 0.00085754 | 0.00021492 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4204-9_1_2_load_317 | 151 | 0.00072799 | 0.00018245 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4204-9_1_2_load_325 | 153 | 0.00022227 | 5.5707e-05 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4204-9_1_2_load_318 | 155 | 0.00081805 | 0.00020502 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4204-9_1_2_load_331 | 156 | 0.00023197 | 5.8138e-05 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4204-9_1_2_load_329 | 157 | 0.00026877 | 6.7359e-05 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4204-9_1_2_load_319 | 158 | 0.00083592 | 0.0002095 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4204-9_1_2_load_320 | 159 | 0.0002608 | 6.5362e-05 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4204-9_1_2_load_333 | 160 | 0.00023875 | 5.9837e-05 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4204-9_1_2_load_326 | 161 | 0.0002496 | 6.2556e-05 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4204-9_1_2_load_332 | 162 | 0.00025263 | 6.3315e-05 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4204-9_1_2_load_328 | 163 | 0.00023198 | 5.814e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 68 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4204-9_1_2_line_0 |  | 0 | 1 | 0.057008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4204-9_1_2_line_1 |  | 1 | 4 | 0.022027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4204-9_1_2_line_2 |  | 1 | 2 | 0.024884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4204-9_1_2_line_3 |  | 2 | 3 | 0.0038988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4204-9_1_2_line_4 |  | 3 | 5 | 0.016361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4204-9_1_2_line_5 |  | 3 | 6 | 0.022285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4204-9_1_2_line_6 |  | 4 | 7 | 0.0019314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4204-9_1_2_line_7 |  | 5 | 8 | 0.034385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4204-9_1_2_line_8 |  | 6 | 9 | 0.0037532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4204-9_1_2_line_9 |  | 8 | 10 | 0.009124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4204-9_1_2_line_10 |  | 8 | 11 | 0.016234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4204-9_1_2_line_11 |  | 9 | 12 | 0.025869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4204-9_1_2_line_12 |  | 9 | 13 | 0.01292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4204-9_1_2_line_13 |  | 10 | 14 | 0.017899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4204-9_1_2_line_14 |  | 10 | 15 | 0.013437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4204-9_1_2_line_15 |  | 11 | 16 | 0.037903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4204-9_1_2_line_16 |  | 12 | 17 | 0.022043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4204-9_1_2_line_17 |  | 13 | 18 | 0.020838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4204-9_1_2_line_18 |  | 14 | 83 | 0.010686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4204-9_1_2_line_19 |  | 15 | 57 | 0.014999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4204-9_1_2_line_20 |  | 16 | 19 | 0.015199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4204-9_1_2_line_21 |  | 17 | 20 | 0.0056953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4204-9_1_2_line_22 |  | 20 | 21 | 0.015574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4204-9_1_2_line_23 |  | 21 | 22 | 0.00040788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4204-9_1_2_line_24 |  | 22 | 23 | 0.017663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4204-9_1_2_line_25 |  | 24 | 25 | 0.00082124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4204-9_1_2_line_26 |  | 25 | 26 | 0.025768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4204-9_1_2_line_27 |  | 26 | 27 | 0.013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4204-9_1_2_line_28 |  | 26 | 28 | 0.003915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4204-9_1_2_line_29 |  | 27 | 142 | 0.016088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4204-9_1_2_line_30 |  | 28 | 89 | 0.022756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4204-9_1_2_line_31 |  | 28 | 76 | 0.010465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4204-9_1_2_line_32 |  | 29 | 30 | 0.008209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4204-9_1_2_line_33 |  | 29 | 31 | 0.0056074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4204-9_1_2_line_34 |  | 31 | 32 | 0.031473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4204-9_1_2_line_35 |  | 31 | 33 | 0.0024062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4204-9_1_2_line_36 |  | 32 | 37 | 0.0090928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4204-9_1_2_line_37 |  | 33 | 38 | 0.0099985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4204-9_1_2_line_38 |  | 34 | 35 | 0.028703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_4204-9_1_2_line_39 |  | 34 | 36 | 0.020536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_4204-9_1_2_line_40 |  | 35 | 39 | 0.01926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_4204-9_1_2_line_41 |  | 35 | 40 | 0.012769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4204-9_1_2_line_42 |  | 36 | 41 | 0.018326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_4204-9_1_2_line_43 |  | 37 | 48 | 0.028534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4204-9_1_2_line_44 |  | 38 | 46 | 0.033477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4204-9_1_2_line_45 |  | 39 | 49 | 0.014575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
46 | LV_4204-9_1_2_line_46 |  | 40 | 50 | 0.016068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4204-9_1_2_line_47 |  | 41 | 51 | 0.0068451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_4204-9_1_2_line_48 |  | 42 | 43 | 0.011814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4204-9_1_2_line_49 |  | 42 | 44 | 0.012437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4204-9_1_2_line_50 |  | 43 | 52 | 0.13638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4204-9_1_2_line_51 |  | 44 | 53 | 0.016203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4204-9_1_2_line_52 |  | 45 | 46 | 0.014323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4204-9_1_2_line_53 |  | 45 | 47 | 0.015136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4204-9_1_2_line_54 |  | 46 | 54 | 0.034171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4204-9_1_2_line_55 |  | 48 | 55 | 0.010672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4204-9_1_2_line_56 |  | 49 | 53 | 0.004094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_4204-9_1_2_line_57 |  | 51 | 62 | 0.018607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4204-9_1_2_line_58 |  | 51 | 63 | 0.010805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_4204-9_1_2_line_59 |  | 52 | 64 | 0.011776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4204-9_1_2_line_60 |  | 53 | 65 | 0.013469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_4204-9_1_2_line_61 |  | 54 | 59 | 0.027134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4204-9_1_2_line_62 |  | 55 | 57 | 0.009253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4204-9_1_2_line_63 |  | 55 | 56 | 0.046042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4204-9_1_2_line_64 |  | 57 | 58 | 0.014048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4204-9_1_2_line_65 |  | 58 | 60 | 0.0092486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4204-9_1_2_line_66 |  | 59 | 61 | 0.020905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4204-9_1_2_line_67 |  | 60 | 71 | 0.021323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4204-9_1_2_line_68 |  | 63 | 66 | 0.017918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_4204-9_1_2_line_69 |  | 64 | 77 | 0.0020452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4204-9_1_2_line_70 |  | 65 | 136 | 0.019864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_4204-9_1_2_line_71 |  | 66 | 67 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
72 | LV_4204-9_1_2_line_72 |  | 67 | 68 | 0.01824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
73 | LV_4204-9_1_2_line_73 |  | 67 | 69 | 0.0017199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4204-9_1_2_line_74 |  | 69 | 70 | 0.020831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4204-9_1_2_line_75 |  | 70 | 71 | 0.022906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4204-9_1_2_line_76 |  | 70 | 72 | 0.0038349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4204-9_1_2_line_77 |  | 72 | 73 | 0.020274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4204-9_1_2_line_78 |  | 74 | 75 | 0.017974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4204-9_1_2_line_79 |  | 74 | 76 | 0.031712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4204-9_1_2_line_80 |  | 75 | 90 | 0.035803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4204-9_1_2_line_81 |  | 76 | 85 | 0.012985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4204-9_1_2_line_82 |  | 78 | 79 | 0.020073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4204-9_1_2_line_83 |  | 79 | 80 | 0.031804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4204-9_1_2_line_84 |  | 79 | 81 | 0.010818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_4204-9_1_2_line_85 |  | 79 | 82 | 0.01759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
86 | LV_4204-9_1_2_line_86 |  | 81 | 127 | 0.020136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_4204-9_1_2_line_87 |  | 82 | 125 | 0.00038285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_4204-9_1_2_line_88 |  | 84 | 85 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4204-9_1_2_line_89 |  | 84 | 86 | 0.01838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4204-9_1_2_line_90 |  | 86 | 87 | 0.010664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4204-9_1_2_line_91 |  | 87 | 88 | 0.018912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4204-9_1_2_line_92 |  | 89 | 91 | 0.02579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4204-9_1_2_line_93 |  | 90 | 141 | 0.014262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4204-9_1_2_line_94 |  | 90 | 103 | 0.009965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4204-9_1_2_line_95 |  | 91 | 143 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4204-9_1_2_line_96 |  | 92 | 93 | 0.0054983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4204-9_1_2_line_97 |  | 93 | 94 | 0.021727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4204-9_1_2_line_98 |  | 94 | 124 | 0.0053685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4204-9_1_2_line_99 |  | 95 | 96 | 4.0549e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4204-9_1_2_line_100 |  | 95 | 97 | 0.02142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4204-9_1_2_line_101 |  | 96 | 98 | 0.021507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4204-9_1_2_line_102 |  | 97 | 99 | 0.00017317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4204-9_1_2_line_103 |  | 98 | 100 | 0.00055169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4204-9_1_2_line_104 |  | 99 | 101 | 0.020876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4204-9_1_2_line_105 |  | 100 | 102 | 0.027448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4204-9_1_2_line_106 |  | 101 | 103 | 0.01734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4204-9_1_2_line_107 |  | 102 | 104 | 0.0065124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4204-9_1_2_line_108 |  | 103 | 105 | 0.011164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4204-9_1_2_line_109 |  | 104 | 111 | 0.026677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4204-9_1_2_line_110 |  | 104 | 107 | 0.014837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4204-9_1_2_line_111 |  | 105 | 131 | 0.0090101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4204-9_1_2_line_112 |  | 106 | 107 | 1.8366e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4204-9_1_2_line_113 |  | 106 | 108 | 0.012504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
114 | LV_4204-9_1_2_line_114 |  | 108 | 109 | 0.011417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_4204-9_1_2_line_115 |  | 108 | 110 | 0.016578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4204-9_1_2_line_116 |  | 109 | 112 | 0.017436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_4204-9_1_2_line_117 |  | 109 | 113 | 0.012921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4204-9_1_2_line_118 |  | 110 | 114 | 0.015063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4204-9_1_2_line_119 |  | 110 | 115 | 0.014376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4204-9_1_2_line_120 |  | 112 | 116 | 0.010065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
121 | LV_4204-9_1_2_line_121 |  | 113 | 117 | 0.017635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4204-9_1_2_line_122 |  | 114 | 118 | 0.0084436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4204-9_1_2_line_123 |  | 115 | 119 | 0.013637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4204-9_1_2_line_124 |  | 116 | 120 | 0.013339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4204-9_1_2_line_125 |  | 116 | 121 | 0.0080234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
126 | LV_4204-9_1_2_line_126 |  | 118 | 122 | 0.0084429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4204-9_1_2_line_127 |  | 119 | 123 | 0.035004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4204-9_1_2_line_128 |  | 119 | 124 | 0.008963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4204-9_1_2_line_129 |  | 120 | 126 | 0.01754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4204-9_1_2_line_130 |  | 121 | 125 | 0.0078513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
131 | LV_4204-9_1_2_line_131 |  | 122 | 139 | 0.023925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4204-9_1_2_line_132 |  | 122 | 140 | 0.055992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4204-9_1_2_line_133 |  | 123 | 129 | 0.002735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4204-9_1_2_line_134 |  | 124 | 128 | 0.019636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4204-9_1_2_line_135 |  | 127 | 138 | 0.0059361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
136 | LV_4204-9_1_2_line_136 |  | 129 | 130 | 0.019072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4204-9_1_2_line_137 |  | 132 | 133 | 0.0021738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
138 | LV_4204-9_1_2_line_138 |  | 132 | 134 | 0.020365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
139 | LV_4204-9_1_2_line_139 |  | 133 | 135 | 0.020039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
140 | LV_4204-9_1_2_line_140 |  | 134 | 136 | 0.0014006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
141 | LV_4204-9_1_2_line_141 |  | 135 | 137 | 0.0024143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
142 | LV_4204-9_1_2_line_142 |  | 137 | 138 | 0.019083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_4204-9_1_2_line_143 |  | 139 | 151 | 0.0023209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4204-9_1_2_line_144 |  | 139 | 150 | 0.018667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4204-9_1_2_line_145 |  | 140 | 163 | 0.0077004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4204-9_1_2_line_146 |  | 142 | 144 | 0.0063591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4204-9_1_2_line_147 |  | 143 | 146 | 0.0030636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4204-9_1_2_line_148 |  | 143 | 145 | 0.015487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4204-9_1_2_line_149 |  | 147 | 148 | 0.014371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4204-9_1_2_line_150 |  | 147 | 149 | 0.011424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4204-9_1_2_line_151 |  | 148 | 150 | 0.0069902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4204-9_1_2_line_152 |  | 151 | 155 | 0.020898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4204-9_1_2_line_153 |  | 152 | 153 | 0.011839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4204-9_1_2_line_154 |  | 152 | 154 | 0.033619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4204-9_1_2_line_155 |  | 154 | 156 | 0.010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4204-9_1_2_line_156 |  | 154 | 157 | 0.0028969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4204-9_1_2_line_157 |  | 155 | 158 | 0.0029036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4204-9_1_2_line_158 |  | 156 | 162 | 0.009709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4204-9_1_2_line_159 |  | 157 | 163 | 0.015642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4204-9_1_2_line_160 |  | 158 | 159 | 0.022817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4204-9_1_2_line_161 |  | 159 | 160 | 0.0029351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4204-9_1_2_line_162 |  | 161 | 162 | 0.013426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4204-9_1_2_trafo_121 | 0.63 MVA 20/0.4 kV | 164 | 68 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2655739.2372 | 1250641.8887 | 2655689.7417 | 1250613.6033
1 | 2655739.2372 | 1250641.8887 | 2655748.8291 | 1250622.0595
2 | 2655728.4016 | 1250664.2893 | 2655739.2372 | 1250641.8887
3 | 2655726.7038 | 1250667.7991 | 2655728.4016 | 1250664.2893
4 | 2655726.7038 | 1250667.7991 | 2655742.0113 | 1250673.5748
5 | 2655726.7038 | 1250667.7991 | 2655716.6901 | 1250687.7078
6 | 2655748.8291 | 1250622.0595 | 2655749.6701 | 1250620.3208
7 | 2655774.1823 | 1250685.7134 | 2655742.0113 | 1250673.5748
8 | 2655715.0036 | 1250691.0608 | 2655716.6901 | 1250687.7078
9 | 2655774.1823 | 1250685.7134 | 2655782.4797 | 1250689.5608
10 | 2655774.1823 | 1250685.7134 | 2655779.421 | 1250670.3483
11 | 2655715.0036 | 1250691.0608 | 2655704.6427 | 1250714.7643
12 | 2655715.0036 | 1250691.0608 | 2655704.0793 | 1250697.9592
13 | 2655782.4797 | 1250689.5608 | 2655775.005 | 1250705.8238
14 | 2655782.4797 | 1250689.5608 | 2655794.9713 | 1250694.5122
15 | 2655779.421 | 1250670.3483 | 2655791.6526 | 1250634.4731
16 | 2655704.6427 | 1250714.7643 | 2655695.8143 | 1250734.9617
17 | 2655704.0793 | 1250697.9592 | 2655697.2724 | 1250702.2575 | 2655687.5122 | 1250710.5196
18 | 2655770.5424 | 1250715.5331 | 2655775.005 | 1250705.8238
19 | 2655808.9144 | 1250700.039 | 2655794.9713 | 1250694.5122
20 | 2655796.5574 | 1250620.0872 | 2655791.6526 | 1250634.4731
21 | 2655693.5333 | 1250740.1802 | 2655695.8143 | 1250734.9617
22 | 2655693.5333 | 1250740.1802 | 2655687.2957 | 1250754.4504
23 | 2655687.1324 | 1250754.8241 | 2655687.2957 | 1250754.4504
24 | 2655687.1324 | 1250754.8241 | 2655683.2278 | 1250763.757 | 2655679.6488 | 1250770.8151
25 | 2655687.1411 | 1250795.921 | 2655687.8795 | 1250796.2805
26 | 2655711.0474 | 1250807.5597 | 2655687.8795 | 1250796.2805
27 | 2655711.0474 | 1250807.5597 | 2655708.3741 | 1250820.8867
28 | 2655714.579 | 1250809.2719 | 2655711.0474 | 1250807.5597
29 | 2655708.3741 | 1250820.8867 | 2655705.21 | 1250836.6605
30 | 2655714.579 | 1250809.2719 | 2655710.5318 | 1250831.665
31 | 2655714.579 | 1250809.2719 | 2655724.1863 | 1250813.4873
32 | 2655893.3169 | 1250734.128 | 2655893.2252 | 1250740.8058 | 2655893.2096 | 1250742.3363
33 | 2655893.3939 | 1250728.5211 | 2655893.3169 | 1250734.128
34 | 2655863.3278 | 1250718.9311 | 2655893.3939 | 1250728.5211
35 | 2655893.3939 | 1250728.5211 | 2655893.28 | 1250726.1176
36 | 2655863.3278 | 1250718.9311 | 2655854.7234 | 1250715.9911
37 | 2655892.8067 | 1250716.1303 | 2655893.28 | 1250726.1176
38 | 2655886.6466 | 1250817.2411 | 2655892.731 | 1250789.1902
39 | 2655892.731 | 1250789.1902 | 2655872.7806 | 1250784.3212
40 | 2655886.6466 | 1250817.2411 | 2655882.5333 | 1250836.0568
41 | 2655886.6466 | 1250817.2411 | 2655874.0768 | 1250814.994
42 | 2655854.9772 | 1250779.9761 | 2655872.7806 | 1250784.3212
43 | 2655827.7225 | 1250706.7652 | 2655854.7234 | 1250715.9911
44 | 2655891.2219 | 1250682.6912 | 2655892.8067 | 1250716.1303
45 | 2655879.4205 | 1250850.2959 | 2655882.5333 | 1250836.0568
46 | 2655874.0768 | 1250814.994 | 2655858.2596 | 1250812.1664
47 | 2655848.3273 | 1250778.3532 | 2655854.9772 | 1250779.9761
48 | 2655906.6368 | 1250860.2371 | 2655913.2169 | 1250870.0615
49 | 2655906.6368 | 1250860.2371 | 2655895.4848 | 1250857.3633 | 2655894.5786 | 1250857.1998
50 | 2655913.2169 | 1250870.0615 | 2655909.6492 | 1250860.1766 | 2655914.983 | 1250810.8928 | 2655919.0933 | 1250794.4757 | 2655946.5158 | 1250746.6346 | 2655948.3235 | 1250742.8059
51 | 2655878.6353 | 1250854.3135 | 2655883.3901 | 1250855.1811 | 2655894.5786 | 1250857.1998
52 | 2655877.2485 | 1250685.9951 | 2655886.48 | 1250683.636 | 2655891.2219 | 1250682.6912
53 | 2655877.2485 | 1250685.9951 | 2655876.2721 | 1250683.8733 | 2655873.6626 | 1250681.2247 | 2655865.4561 | 1250677.3335 | 2655865.4561 | 1250677.3335
54 | 2655891.2219 | 1250682.6912 | 2655883.4404 | 1250649.4175
55 | 2655817.5869 | 1250703.334 | 2655827.7225 | 1250706.7652
56 | 2655879.4205 | 1250850.2959 | 2655878.6353 | 1250854.3135
57 | 2655848.3273 | 1250778.3532 | 2655845.6326 | 1250796.7627
58 | 2655848.3273 | 1250778.3532 | 2655837.8308 | 1250775.789
59 | 2655948.3235 | 1250742.8059 | 2655953.3511 | 1250732.1575
60 | 2655878.6353 | 1250854.3135 | 2655876.2371 | 1250867.5676
61 | 2655877.2613 | 1250622.9961 | 2655883.4404 | 1250649.4175
62 | 2655817.5869 | 1250703.334 | 2655808.9144 | 1250700.039
63 | 2655817.5869 | 1250703.334 | 2655819.4836 | 1250678.279 | 2655822.531 | 1250671.3029 | 2655823.6599 | 1250658.0488
64 | 2655808.9144 | 1250700.039 | 2655803.5345 | 1250713.016
65 | 2655803.5345 | 1250713.016 | 2655799.9926 | 1250721.5595
66 | 2655877.2613 | 1250622.9961 | 2655866.0502 | 1250622.3344 | 2655861.7991 | 1250624.8628 | 2655858.9623 | 1250628.7054
67 | 2655791.8267 | 1250741.2568 | 2655799.9926 | 1250721.5595
68 | 2655837.8308 | 1250775.789 | 2655820.425 | 1250771.537
69 | 2655954.2243 | 1250730.3081 | 2655953.3511 | 1250732.1575
70 | 2655872.7005 | 1250887.1142 | 2655876.2371 | 1250867.5676
71 | 2655804.9628 | 1250767.7598 | 2655820.425 | 1250771.537
72 | 2655804.9628 | 1250767.7598 | 2655800.8626 | 1250785.5335
73 | 2655804.9628 | 1250767.7598 | 2655803.2918 | 1250767.3523
74 | 2655783.0544 | 1250762.4166 | 2655803.2918 | 1250767.3523
75 | 2655783.0544 | 1250762.4166 | 2655791.8267 | 1250741.2568
76 | 2655783.0544 | 1250762.4166 | 2655781.4318 | 1250765.8913
77 | 2655772.8535 | 1250784.2611 | 2655781.4318 | 1250765.8913
78 | 2655753.4952 | 1250825.7157 | 2655771.083 | 1250829.4229
79 | 2655724.1863 | 1250813.4873 | 2655737.4723 | 1250819.8388 | 2655753.4952 | 1250825.7157
80 | 2655806.1166 | 1250836.8073 | 2655771.083 | 1250829.4229
81 | 2655724.1863 | 1250813.4873 | 2655729.5097 | 1250801.6432
82 | 2655854.4747 | 1250987.845 | 2655874.2832 | 1250991.0953
83 | 2655854.4747 | 1250987.845 | 2655848.2242 | 1251019.0286
84 | 2655854.4747 | 1250987.845 | 2655856.4008 | 1250977.1994
85 | 2655854.4747 | 1250987.845 | 2655837.116 | 1250985.0003
86 | 2655859.9858 | 1250957.3857 | 2655856.4008 | 1250977.1994
87 | 2655836.7381 | 1250984.9383 | 2655837.116 | 1250985.0003
88 | 2655735.5746 | 1250788.1495 | 2655729.5097 | 1250801.6432
89 | 2655743.1093 | 1250771.3853 | 2655735.5746 | 1250788.1495
90 | 2655747.4811 | 1250761.6586 | 2655743.1093 | 1250771.3853
91 | 2655755.234 | 1250744.4092 | 2655747.4811 | 1250761.6586
92 | 2655705.9448 | 1250857.0442 | 2655710.5318 | 1250831.665
93 | 2655808.0839 | 1250822.6827 | 2655806.1166 | 1250836.8073
94 | 2655815.895 | 1250838.8674 | 2655806.1166 | 1250836.8073
95 | 2655701.7467 | 1250880.2715 | 2655705.9448 | 1250857.0442
96 | 2655697.7701 | 1250960.8855 | 2655703.1667 | 1250961.9379
97 | 2655724.4921 | 1250966.0963 | 2655703.1667 | 1250961.9379
98 | 2655729.7614 | 1250967.1238 | 2655724.4921 | 1250966.0963
99 | 2655806.2055 | 1250897.9283 | 2655806.212 | 1250897.8883
100 | 2655809.6799 | 1250876.7505 | 2655806.212 | 1250897.8883
101 | 2655806.2055 | 1250897.9283 | 2655802.7236 | 1250919.1511
102 | 2655809.6799 | 1250876.7505 | 2655809.7079 | 1250876.5796
103 | 2655802.6343 | 1250919.6956 | 2655802.7236 | 1250919.1511
104 | 2655809.7079 | 1250876.5796 | 2655813.0877 | 1250855.9788
105 | 2655802.6343 | 1250919.6956 | 2655800.7597 | 1250931.1222 | 2655791.3377 | 1250943.8915
106 | 2655815.895 | 1250838.8674 | 2655813.0877 | 1250855.9788
107 | 2655787.4712 | 1250949.1318 | 2655791.3377 | 1250943.8915
108 | 2655815.895 | 1250838.8674 | 2655826.8827 | 1250840.8442
109 | 2655787.4712 | 1250949.1318 | 2655813.6846 | 1250954.0857
110 | 2655787.4712 | 1250949.1318 | 2655784.8489 | 1250963.7353
111 | 2655835.7505 | 1250842.4395 | 2655826.8827 | 1250840.8442
112 | 2655784.8489 | 1250963.7353 | 2655784.8457 | 1250963.7534
113 | 2655782.6358 | 1250976.0605 | 2655784.8457 | 1250963.7534
114 | 2655782.6358 | 1250976.0605 | 2655793.9331 | 1250977.9237
115 | 2655766.2286 | 1250973.371 | 2655782.6358 | 1250976.0605
116 | 2655793.9331 | 1250977.9237 | 2655811.1398 | 1250980.7434
117 | 2655793.9331 | 1250977.9237 | 2655791.6973 | 1250990.65
118 | 2655766.2286 | 1250973.371 | 2655763.5305 | 1250988.1902
119 | 2655766.2286 | 1250973.371 | 2655752.0417 | 1250971.0464
120 | 2655821.0724 | 1250982.3711 | 2655811.1398 | 1250980.7434
121 | 2655791.6973 | 1250990.65 | 2655788.646 | 1251008.0186
122 | 2655763.5305 | 1250988.1902 | 2655762.018 | 1250996.4973
123 | 2655738.5842 | 1250968.8412 | 2655752.0417 | 1250971.0464
124 | 2655821.0724 | 1250982.3711 | 2655818.4971 | 1250995.4596
125 | 2655821.0724 | 1250982.3711 | 2655828.9902 | 1250983.6686
126 | 2655762.018 | 1250996.4973 | 2655760.5057 | 1251004.8036
127 | 2655738.5842 | 1250968.8412 | 2655745.2181 | 1250934.4721
128 | 2655738.5842 | 1250968.8412 | 2655729.7614 | 1250967.1238
129 | 2655815.1108 | 1251012.6693 | 2655818.4971 | 1250995.4596
130 | 2655836.7381 | 1250984.9383 | 2655828.9902 | 1250983.6686
131 | 2655760.5057 | 1251004.8036 | 2655756.7054 | 1251028.4248
132 | 2655760.5057 | 1251004.8036 | 2655751.4496 | 1251060.0585
133 | 2655745.7365 | 1250931.7866 | 2655745.2181 | 1250934.4721
134 | 2655729.7614 | 1250967.1238 | 2655725.8515 | 1250986.367
135 | 2655859.9858 | 1250957.3857 | 2655861.0427 | 1250951.5444
136 | 2655745.7365 | 1250931.7866 | 2655749.3509 | 1250913.0607
137 | 2655868.4381 | 1250910.6714 | 2655868.8252 | 1250908.5323
138 | 2655872.4511 | 1250888.4924 | 2655868.8252 | 1250908.5323
139 | 2655864.8703 | 1250930.39 | 2655868.4381 | 1250910.6714
140 | 2655872.7005 | 1250887.1142 | 2655872.4511 | 1250888.4924
141 | 2655864.4405 | 1250932.7658 | 2655864.8703 | 1250930.39
142 | 2655864.4405 | 1250932.7658 | 2655861.0427 | 1250951.5444
143 | 2655754.4324 | 1251027.9559 | 2655756.7054 | 1251028.4248
144 | 2655774.9878 | 1251032.1957 | 2655756.7054 | 1251028.4248
145 | 2655751.4496 | 1251060.0585 | 2655743.908 | 1251058.5029
146 | 2655703.9593 | 1250842.8954 | 2655705.21 | 1250836.6605
147 | 2655701.2019 | 1250883.2863 | 2655701.7467 | 1250880.2715
148 | 2655701.7467 | 1250880.2715 | 2655687.1792 | 1250875.0155
149 | 2655795.9085 | 1251036.5108 | 2655781.8339 | 1251033.6078
150 | 2655795.9085 | 1251036.5108 | 2655807.0968 | 1251038.8185
151 | 2655774.9878 | 1251032.1957 | 2655781.8339 | 1251033.6078
152 | 2655754.4324 | 1251027.9559 | 2655733.9652 | 1251023.7344
153 | 2655725.427 | 1251087.6888 | 2655713.8114 | 1251085.3994
154 | 2655725.7518 | 1251054.7579 | 2655724.2976 | 1251060.1035 | 2655727.4462 | 1251074.4319 | 2655725.427 | 1251087.6888
155 | 2655725.7518 | 1251054.7579 | 2655715.6144 | 1251052.4416
156 | 2655725.7518 | 1251054.7579 | 2655728.5889 | 1251055.3431
157 | 2655733.9652 | 1251023.7344 | 2655731.1214 | 1251023.1478
158 | 2655706.1493 | 1251050.2789 | 2655715.6144 | 1251052.4416
159 | 2655728.5889 | 1251055.3431 | 2655743.908 | 1251058.5029
160 | 2655708.7746 | 1251018.5385 | 2655731.1214 | 1251023.1478
161 | 2655708.7746 | 1251018.5385 | 2655705.9 | 1251017.9456
162 | 2655706.1493 | 1251050.2789 | 2655704.4363 | 1251049.8876 | 2655697.226 | 1251048.4744 | 2655692.9849 | 1251047.6457

## bus_geodata
| x | y | coords
0 | 2655689.7417 | 1250613.6033
1 | 2655739.2372 | 1250641.8887
2 | 2655728.4016 | 1250664.2893
3 | 2655726.7038 | 1250667.7991
4 | 2655748.8291 | 1250622.0595
5 | 2655742.0113 | 1250673.5748
6 | 2655716.6901 | 1250687.7078
7 | 2655749.6701 | 1250620.3208
8 | 2655774.1822 | 1250685.7134
9 | 2655715.0036 | 1250691.0608
10 | 2655782.4797 | 1250689.5608
11 | 2655779.421 | 1250670.3483
12 | 2655704.6427 | 1250714.7643
13 | 2655704.0793 | 1250697.9592
14 | 2655775.005 | 1250705.8238
15 | 2655794.9713 | 1250694.5122
16 | 2655791.6526 | 1250634.4731
17 | 2655695.8143 | 1250734.9617
18 | 2655687.5122 | 1250710.5196
19 | 2655796.5574 | 1250620.0872
20 | 2655693.5333 | 1250740.1802
21 | 2655687.2957 | 1250754.4504
22 | 2655687.1324 | 1250754.8241
23 | 2655679.6488 | 1250770.8151
24 | 2655687.1411 | 1250795.921
25 | 2655687.8795 | 1250796.2805
26 | 2655711.0474 | 1250807.5597
27 | 2655708.3741 | 1250820.8867
28 | 2655714.579 | 1250809.2719
29 | 2655893.3169 | 1250734.128
30 | 2655893.2096 | 1250742.3363
31 | 2655893.3939 | 1250728.5211
32 | 2655863.3278 | 1250718.9311
33 | 2655893.28 | 1250726.1176
34 | 2655892.731 | 1250789.1902
35 | 2655886.6466 | 1250817.2411
36 | 2655872.7806 | 1250784.3212
37 | 2655854.7234 | 1250715.9911
38 | 2655892.8067 | 1250716.1303
39 | 2655882.5333 | 1250836.0568
40 | 2655874.0768 | 1250814.994
41 | 2655854.9772 | 1250779.9761
42 | 2655906.6368 | 1250860.2371
43 | 2655913.2169 | 1250870.0615
44 | 2655894.5786 | 1250857.1998
45 | 2655877.2485 | 1250685.9951
46 | 2655891.2219 | 1250682.6912
47 | 2655865.4561 | 1250677.3335
48 | 2655827.7225 | 1250706.7652
49 | 2655879.4205 | 1250850.2959
50 | 2655858.2596 | 1250812.1664
51 | 2655848.3273 | 1250778.3532
52 | 2655948.3235 | 1250742.8059
53 | 2655878.6353 | 1250854.3135
54 | 2655883.4404 | 1250649.4175
55 | 2655817.5869 | 1250703.334
56 | 2655823.6599 | 1250658.0488
57 | 2655808.9144 | 1250700.039
58 | 2655803.5345 | 1250713.016
59 | 2655877.2613 | 1250622.9961
60 | 2655799.9926 | 1250721.5595
61 | 2655858.9623 | 1250628.7054
62 | 2655845.6326 | 1250796.7628
63 | 2655837.8308 | 1250775.789
64 | 2655953.3511 | 1250732.1575
65 | 2655876.2371 | 1250867.5676
66 | 2655820.425 | 1250771.537
67 | 2655804.9628 | 1250767.7598
68 | 2655800.8626 | 1250785.5335
69 | 2655803.2918 | 1250767.3523
70 | 2655783.0544 | 1250762.4166
71 | 2655791.8267 | 1250741.2568
72 | 2655781.4318 | 1250765.8913
73 | 2655772.8535 | 1250784.2611
74 | 2655753.4952 | 1250825.7157
75 | 2655771.083 | 1250829.4229
76 | 2655724.1863 | 1250813.4873
77 | 2655954.2243 | 1250730.3081
78 | 2655874.2832 | 1250991.0953
79 | 2655854.4747 | 1250987.845
80 | 2655848.2242 | 1251019.0286
81 | 2655856.4008 | 1250977.1994
82 | 2655837.116 | 1250985.0003
83 | 2655770.5424 | 1250715.5331
84 | 2655735.5746 | 1250788.1495
85 | 2655729.5097 | 1250801.6432
86 | 2655743.1093 | 1250771.3853
87 | 2655747.4811 | 1250761.6586
88 | 2655755.234 | 1250744.4092
89 | 2655710.5318 | 1250831.665
90 | 2655806.1166 | 1250836.8073
91 | 2655705.9448 | 1250857.0442
92 | 2655697.7701 | 1250960.8855
93 | 2655703.1667 | 1250961.9379
94 | 2655724.4921 | 1250966.0963
95 | 2655806.212 | 1250897.8883
96 | 2655806.2055 | 1250897.9283
97 | 2655809.6799 | 1250876.7505
98 | 2655802.7236 | 1250919.1511
99 | 2655809.7079 | 1250876.5796
100 | 2655802.6343 | 1250919.6956
101 | 2655813.0877 | 1250855.9788
102 | 2655791.3377 | 1250943.8915
103 | 2655815.895 | 1250838.8674
104 | 2655787.4712 | 1250949.1318
105 | 2655826.8827 | 1250840.8442
106 | 2655784.8457 | 1250963.7534
107 | 2655784.8489 | 1250963.7353
108 | 2655782.6358 | 1250976.0605
109 | 2655793.9331 | 1250977.9237
110 | 2655766.2286 | 1250973.371
111 | 2655813.6846 | 1250954.0857
112 | 2655811.1398 | 1250980.7434
113 | 2655791.6973 | 1250990.65
114 | 2655763.5305 | 1250988.1902
115 | 2655752.0417 | 1250971.0464
116 | 2655821.0724 | 1250982.3711
117 | 2655788.646 | 1251008.0186
118 | 2655762.018 | 1250996.4973
119 | 2655738.5842 | 1250968.8412
120 | 2655818.4971 | 1250995.4596
121 | 2655828.9902 | 1250983.6686
122 | 2655760.5057 | 1251004.8036
123 | 2655745.2181 | 1250934.4721
124 | 2655729.7614 | 1250967.1238
125 | 2655836.7381 | 1250984.9383
126 | 2655815.1108 | 1251012.6693
127 | 2655859.9858 | 1250957.3857
128 | 2655725.8515 | 1250986.367
129 | 2655745.7365 | 1250931.7866
130 | 2655749.3509 | 1250913.0607
131 | 2655835.7505 | 1250842.4395
132 | 2655868.8252 | 1250908.5323
133 | 2655868.4381 | 1250910.6714
134 | 2655872.4511 | 1250888.4924
135 | 2655864.8703 | 1250930.39
136 | 2655872.7005 | 1250887.1142
137 | 2655864.4405 | 1250932.7658
138 | 2655861.0427 | 1250951.5444
139 | 2655756.7054 | 1251028.4248
140 | 2655751.4496 | 1251060.0585
141 | 2655808.0839 | 1250822.6827
142 | 2655705.21 | 1250836.6605
143 | 2655701.7467 | 1250880.2715
144 | 2655703.9593 | 1250842.8954
145 | 2655687.1792 | 1250875.0155
146 | 2655701.2019 | 1250883.2863
147 | 2655795.9085 | 1251036.5108
148 | 2655781.8339 | 1251033.6078
149 | 2655807.0968 | 1251038.8185
150 | 2655774.9878 | 1251032.1957
151 | 2655754.4324 | 1251027.9559
152 | 2655725.427 | 1251087.6888
153 | 2655713.8114 | 1251085.3994
154 | 2655725.7518 | 1251054.7579
155 | 2655733.9652 | 1251023.7344
156 | 2655715.6144 | 1251052.4416
157 | 2655728.5889 | 1251055.3431
158 | 2655731.1214 | 1251023.1478
159 | 2655708.7746 | 1251018.5385
160 | 2655705.9 | 1251017.9456
161 | 2655692.9849 | 1251047.6457
162 | 2655706.1493 | 1251050.2789
163 | 2655743.908 | 1251058.5029
164 | 2655804.9628 | 1250767.7598

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1