## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4252-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4252-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4252-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4252-1_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_4252-1_0_3_node_50 | 0.4 | n |  | TRUE
5 | bus_LV_4252-1_0_3_node_49 | 0.4 | n |  | TRUE
6 | bus_LV_4252-1_0_3_node_62 | 0.4 | n |  | TRUE
7 | bus_LV_4252-1_0_3_node_40 | 0.4 | n |  | TRUE
8 | bus_LV_4252-1_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_4252-1_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_4252-1_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_4252-1_0_3_node_68 | 0.4 | n |  | TRUE
12 | bus_LV_4252-1_0_3_node_67 | 0.4 | n |  | TRUE
13 | bus_LV_4252-1_0_3_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_4252-1_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_4252-1_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4252-1_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_4252-1_0_3_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_4252-1_0_3_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_4252-1_0_3_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_4252-1_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_4252-1_0_3_node_56 | 0.4 | n |  | TRUE
22 | bus_LV_4252-1_0_3_node_55 | 0.4 | n |  | TRUE
23 | bus_LV_4252-1_0_3_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_4252-1_0_3_node_53 | 0.4 | n |  | TRUE
25 | bus_LV_4252-1_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_4252-1_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_4252-1_0_3_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_4252-1_0_3_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_4252-1_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_4252-1_0_3_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_4252-1_0_3_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_4252-1_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_4252-1_0_3_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_4252-1_0_3_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_4252-1_0_3_node_69 | 0.4 | n |  | TRUE
36 | bus_LV_4252-1_0_3_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_4252-1_0_3_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_4252-1_0_3_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_4252-1_0_3_node_65 | 0.4 | n |  | TRUE
40 | bus_LV_4252-1_0_3_node_23 | 0.4 | n |  | TRUE
41 | bus_LV_4252-1_0_3_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_4252-1_0_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_4252-1_0_3_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_4252-1_0_3_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_4252-1_0_3_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_4252-1_0_3_node_25 | 0.4 | n |  | TRUE
47 | bus_LV_4252-1_0_3_node_27 | 0.4 | n |  | TRUE
48 | bus_LV_4252-1_0_3_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_4252-1_0_3_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_4252-1_0_3_node_37 | 0.4 | n |  | TRUE
51 | bus_LV_4252-1_0_3_node_38 | 0.4 | n |  | TRUE
52 | bus_LV_4252-1_0_3_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_4252-1_0_3_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_4252-1_0_3_node_35 | 0.4 | n |  | TRUE
55 | bus_LV_4252-1_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_4252-1_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_4252-1_0_3_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_4252-1_0_3_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_4252-1_0_3_node_51 | 0.4 | n |  | TRUE
60 | bus_LV_4252-1_0_3_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_4252-1_0_3_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_4252-1_0_3_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_4252-1_0_3_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_4252-1_0_3_node_63 | 0.4 | n |  | TRUE
65 | bus_LV_4252-1_0_3_node_64 | 0.4 | n |  | TRUE
66 | bus_LV_4252-1_0_3_node_66 | 0.4 | n |  | TRUE
67 | bus_MV_347_1_node_106 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4252-1_0_3_load_0 | 0 | 0.0073429 | 0.0018403 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4252-1_0_3_load_1 | 1 | 0.0011954 | 0.0002996 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4252-1_0_3_load_2 | 2 | 0.0023626 | 0.00059212 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4252-1_0_3_load_50 | 4 | 0.0012169 | 0.00030498 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4252-1_0_3_load_49 | 5 | 0.0019438 | 0.00048717 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4252-1_0_3_load_62 | 6 | 0.0025962 | 0.00065066 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4252-1_0_3_load_5 | 8 | 0.030752 | 0.0077072 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4252-1_0_3_load_6 | 9 | 0.0021882 | 0.00054843 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4252-1_0_3_load_8 | 13 | 0.03691 | 0.0092504 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4252-1_0_3_load_9 | 14 | 0.033931 | 0.008504 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4252-1_0_3_load_12 | 17 | 0.0062845 | 0.001575 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4252-1_0_3_load_13 | 18 | 0.0021057 | 0.00052775 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4252-1_0_3_load_21 | 20 | 0.0071003 | 0.0017795 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4252-1_0_3_load_56 | 21 | 0.01407 | 0.0035264 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4252-1_0_3_load_55 | 22 | 0.012534 | 0.0031414 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4252-1_0_3_load_14 | 25 | 0.0015448 | 0.00038717 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4252-1_0_3_load_15 | 26 | 0.0029175 | 0.00073119 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4252-1_0_3_load_17 | 28 | 0.0029905 | 0.00074948 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4252-1_0_3_load_19 | 29 | 0.0012129 | 0.00030398 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4252-1_0_3_load_31 | 31 | 0.0024779 | 0.00062101 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4252-1_0_3_load_28 | 33 | 0.0033573 | 0.00084142 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4252-1_0_3_load_33 | 34 | 0.0039661 | 0.000994 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4252-1_0_3_load_69 | 35 | 0.0057694 | 0.001446 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4252-1_0_3_load_32 | 36 | 0.0034318 | 0.00086009 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4252-1_0_3_load_26 | 37 | 0.0033017 | 0.00082748 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4252-1_0_3_load_34 | 38 | 0.0023667 | 0.00059315 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4252-1_0_3_load_65 | 39 | 0.0021891 | 0.00054865 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4252-1_0_3_load_24 | 41 | 0.019804 | 0.0049632 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4252-1_0_3_load_44 | 42 | 0.011706 | 0.0029338 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4252-1_0_3_load_41 | 43 | 0.009862 | 0.0024716 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4252-1_0_3_load_42 | 45 | 0.0010729 | 0.0002689 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4252-1_0_3_load_25 | 46 | 0.010534 | 0.0026401 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4252-1_0_3_load_29 | 48 | 0.004733 | 0.0011862 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4252-1_0_3_load_30 | 49 | 0.0094518 | 0.0023688 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4252-1_0_3_load_38 | 51 | 0.0078768 | 0.0019741 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4252-1_0_3_load_46 | 52 | 0.0014451 | 0.00036219 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4252-1_0_3_load_48 | 53 | 0.0012151 | 0.00030454 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4252-1_0_3_load_35 | 54 | 0.0026306 | 0.00065929 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4252-1_0_3_load_39 | 55 | 0.0023394 | 0.0005863 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4252-1_0_3_load_57 | 57 | 0.0020623 | 0.00051686 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4252-1_0_3_load_51 | 59 | 0.0048679 | 0.00122 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4252-1_0_3_load_54 | 61 | 0.0050904 | 0.0012758 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4252-1_0_3_load_59 | 62 | 0.00076369 | 0.0001914 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4252-1_0_3_load_61 | 63 | 0.0015159 | 0.00037992 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4252-1_0_3_load_63 | 64 | 0.0016439 | 0.000412 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4252-1_0_3_load_64 | 65 | 0.002375 | 0.00059523 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4252-1_0_3_load_66 | 66 | 0.00058436 | 0.00014645 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4252-1_0_3_line_0 |  | 0 | 1 | 0.021758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4252-1_0_3_line_1 |  | 0 | 2 | 0.0014143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4252-1_0_3_line_2 |  | 2 | 3 | 0.028668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4252-1_0_3_line_3 |  | 3 | 4 | 0.011705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4252-1_0_3_line_4 |  | 3 | 5 | 0.024759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4252-1_0_3_line_5 |  | 4 | 6 | 0.0063013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4252-1_0_3_line_6 |  | 5 | 7 | 0.015598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
7 | LV_4252-1_0_3_line_7 |  | 6 | 58 | 0.021977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4252-1_0_3_line_8 |  | 7 | 53 | 0.028726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4252-1_0_3_line_9 |  | 7 | 44 | 0.045971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_4252-1_0_3_line_10 |  | 7 | 55 | 0.023082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4252-1_0_3_line_11 |  | 8 | 9 | 0.027575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4252-1_0_3_line_12 |  | 9 | 10 | 0.03541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4252-1_0_3_line_13 |  | 10 | 11 | 0.010329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4252-1_0_3_line_14 |  | 11 | 12 | 0.008884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4252-1_0_3_line_15 |  | 12 | 39 | 0.0052499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4252-1_0_3_line_16 |  | 12 | 30 | 0.023382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4252-1_0_3_line_17 |  | 13 | 14 | 0.0070507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4252-1_0_3_line_18 |  | 13 | 15 | 0.030853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4252-1_0_3_line_19 |  | 14 | 16 | 0.030143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4252-1_0_3_line_20 |  | 15 | 17 | 0.014706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4252-1_0_3_line_21 |  | 15 | 18 | 0.030709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4252-1_0_3_line_22 |  | 16 | 19 | 0.006974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4252-1_0_3_line_23 |  | 17 | 20 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4252-1_0_3_line_24 |  | 18 | 21 | 0.030099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4252-1_0_3_line_25 |  | 19 | 22 | 0.029133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4252-1_0_3_line_26 |  | 20 | 23 | 0.0064152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4252-1_0_3_line_27 |  | 21 | 24 | 0.037907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4252-1_0_3_line_28 |  | 23 | 40 | 0.030681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4252-1_0_3_line_29 |  | 23 | 41 | 0.028637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_4252-1_0_3_line_30 |  | 24 | 59 | 0.031755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4252-1_0_3_line_31 |  | 25 | 26 | 0.00015268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4252-1_0_3_line_32 |  | 25 | 27 | 0.029247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4252-1_0_3_line_33 |  | 26 | 28 | 0.015348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4252-1_0_3_line_34 |  | 27 | 29 | 0.031594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4252-1_0_3_line_35 |  | 27 | 30 | 0.032827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4252-1_0_3_line_36 |  | 28 | 31 | 0.011435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4252-1_0_3_line_37 |  | 30 | 35 | 0.019712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4252-1_0_3_line_38 |  | 31 | 36 | 0.0047623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4252-1_0_3_line_39 |  | 32 | 33 | 0.01743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4252-1_0_3_line_40 |  | 32 | 34 | 0.049364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4252-1_0_3_line_41 |  | 33 | 37 | 0.021892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4252-1_0_3_line_42 |  | 34 | 38 | 0.017817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4252-1_0_3_line_43 |  | 36 | 52 | 0.021041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4252-1_0_3_line_44 |  | 37 | 46 | 0.05331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4252-1_0_3_line_45 |  | 38 | 54 | 0.018842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4252-1_0_3_line_46 |  | 39 | 66 | 0.010624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4252-1_0_3_line_47 |  | 40 | 42 | 0.013706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4252-1_0_3_line_48 |  | 40 | 43 | 0.0155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4252-1_0_3_line_49 |  | 41 | 44 | 0.010939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
50 | LV_4252-1_0_3_line_50 |  | 43 | 45 | 0.021348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4252-1_0_3_line_51 |  | 45 | 56 | 0.039671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4252-1_0_3_line_52 |  | 46 | 47 | 0.0091738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4252-1_0_3_line_53 |  | 47 | 48 | 0.012934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4252-1_0_3_line_54 |  | 47 | 49 | 0.024942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4252-1_0_3_line_55 |  | 48 | 50 | 0.025374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4252-1_0_3_line_56 |  | 50 | 51 | 0.030107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4252-1_0_3_line_57 |  | 51 | 55 | 0.006627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4252-1_0_3_line_58 |  | 52 | 53 | 0.0041142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4252-1_0_3_line_59 |  | 56 | 57 | 0.044544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4252-1_0_3_line_60 |  | 58 | 64 | 0.0024109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4252-1_0_3_line_61 |  | 58 | 62 | 0.015911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4252-1_0_3_line_62 |  | 59 | 60 | 0.034354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4252-1_0_3_line_63 |  | 60 | 61 | 0.019602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4252-1_0_3_line_64 |  | 62 | 63 | 0.0093576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4252-1_0_3_line_65 |  | 64 | 65 | 0.010593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4252-1_0_3_trafo_49 | 0.63 MVA 20/0.4 kV | 67 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2621395.9469 | 1265479.816 | 2621374.7616 | 1265474.8556
1 | 2621395.9469 | 1265479.816 | 2621397.3239 | 1265480.1384
2 | 2621425.2366 | 1265486.674 | 2621397.3239 | 1265480.1384
3 | 2621425.2366 | 1265486.674 | 2621426.9536 | 1265475.0959
4 | 2621425.2366 | 1265486.674 | 2621449.7755 | 1265489.9689
5 | 2621426.9536 | 1265475.0959 | 2621427.878 | 1265468.8628
6 | 2621465.2347 | 1265492.0447 | 2621449.7755 | 1265489.9689
7 | 2621431.1019 | 1265447.1231 | 2621427.878 | 1265468.8628
8 | 2621465.2347 | 1265492.0447 | 2621465.9278 | 1265463.3273
9 | 2621465.2347 | 1265492.0447 | 2621452.516 | 1265536.2295
10 | 2621465.2347 | 1265492.0447 | 2621487.1643 | 1265499.2466
11 | 2621502.881 | 1265332.2251 | 2621527.3324 | 1265344.9722
12 | 2621502.881 | 1265332.2251 | 2621488.5838 | 1265325.6909 | 2621473.0688 | 1265318.6186 | 2621470.5882 | 1265317.4866
13 | 2621470.4776 | 1265325.1693 | 2621467.4485 | 1265323.7018 | 2621467.843 | 1265322.8804 | 2621470.5882 | 1265317.4866
14 | 2621467.8346 | 1265333.5323 | 2621467.8341 | 1265331.5754 | 2621470.4776 | 1265325.1693
15 | 2621467.8346 | 1265333.5323 | 2621469.9571 | 1265333.7401 | 2621472.7685 | 1265335.0868
16 | 2621467.8346 | 1265333.5323 | 2621457.5712 | 1265354.5542
17 | 2621375.1773 | 1265557.0098 | 2621368.353 | 1265555.2374
18 | 2621405.0397 | 1265564.7667 | 2621400.7447 | 1265563.6504 | 2621375.1773 | 1265557.0098
19 | 2621341.917 | 1265541.5117 | 2621346.5486 | 1265545.3533 | 2621354.4058 | 1265550.4185 | 2621363.8868 | 1265554.0774 | 2621368.353 | 1265555.2374
20 | 2621405.0397 | 1265564.7667 | 2621419.2724 | 1265568.4661
21 | 2621405.0397 | 1265564.7667 | 2621403.9681 | 1265567.5536 | 2621395.2597 | 1265593.8739
22 | 2621337.0864 | 1265536.4686 | 2621341.917 | 1265541.5117
23 | 2621435.3576 | 1265572.647 | 2621419.2724 | 1265568.4661
24 | 2621368.2694 | 1265593.5319 | 2621368.9638 | 1265590.9548 | 2621374.5604 | 1265592.3426 | 2621376.9461 | 1265590.5389 | 2621386.0605 | 1265591.4501 | 2621395.2597 | 1265593.8739
25 | 2621337.0864 | 1265536.4686 | 2621330.3378 | 1265564.8086
26 | 2621441.5665 | 1265574.2609 | 2621435.3576 | 1265572.647
27 | 2621368.2694 | 1265593.5319 | 2621357.5299 | 1265629.8852
28 | 2621441.5665 | 1265574.2609 | 2621471.201 | 1265582.5295
29 | 2621441.5665 | 1265574.2609 | 2621449.4894 | 1265546.742
30 | 2621357.5299 | 1265629.8852 | 2621325.7752 | 1265629.777
31 | 2621467.2959 | 1265406.644 | 2621467.2996 | 1265406.4914
32 | 2621468.2482 | 1265377.2865 | 2621467.6205 | 1265382.2099 | 2621467.4407 | 1265400.6444 | 2621467.2996 | 1265406.4914
33 | 2621467.2959 | 1265406.644 | 2621466.9256 | 1265421.9877
34 | 2621468.2482 | 1265377.2865 | 2621439.6015 | 1265363.9613
35 | 2621468.2482 | 1265377.2865 | 2621462.3369 | 1265371.2832 | 2621453.7847 | 1265366.8158 | 2621451.958 | 1265366.0086 | 2621457.5712 | 1265354.5542
36 | 2621466.6497 | 1265433.419 | 2621466.9256 | 1265421.9877
37 | 2621457.5712 | 1265354.5542 | 2621475.1336 | 1265363.5052
38 | 2621466.6497 | 1265433.419 | 2621466.5348 | 1265438.1799
39 | 2621519.3555 | 1265400.5326 | 2621515.8793 | 1265417.6122
40 | 2621519.3555 | 1265400.5326 | 2621563.6643 | 1265422.2936
41 | 2621515.8793 | 1265417.6122 | 2621511.5131 | 1265439.0643
42 | 2621579.6566 | 1265430.1478 | 2621563.6643 | 1265422.2936
43 | 2621466.0271 | 1265459.2144 | 2621466.5348 | 1265438.1799
44 | 2621511.5131 | 1265439.0643 | 2621511.5131 | 1265439.0643 | 2621514.0946 | 1265443.499 | 2621545.6165 | 1265456.745 | 2621541.4068 | 1265470.083
45 | 2621579.6566 | 1265430.1478 | 2621596.5691 | 1265438.4539
46 | 2621472.7685 | 1265335.0868 | 2621479.9914 | 1265338.5465 | 2621482.2681 | 1265339.8334
47 | 2621471.201 | 1265582.5295 | 2621484.725 | 1265584.7584
48 | 2621471.201 | 1265582.5295 | 2621468.1672 | 1265592.8146 | 2621467.3665 | 1265597.5241
49 | 2621452.516 | 1265536.2295 | 2621449.4894 | 1265546.742
50 | 2621467.3665 | 1265597.5241 | 2621463.788 | 1265618.5705
51 | 2621461.591 | 1265658.1476 | 2621462.3847 | 1265634.4227 | 2621463.0186 | 1265625.719 | 2621463.1283 | 1265622.4504 | 2621463.788 | 1265618.5705
52 | 2621537.775 | 1265478.4317 | 2621539.8047 | 1265475.159 | 2621541.4068 | 1265470.083
53 | 2621537.775 | 1265478.4317 | 2621530.3697 | 1265481.6292 | 2621529.033 | 1265486.3095
54 | 2621556.5937 | 1265487.8622 | 2621555.8778 | 1265490.1167 | 2621542.7707 | 1265485.6437 | 2621537.775 | 1265478.4317
55 | 2621522.0648 | 1265510.7082 | 2621529.033 | 1265486.3095
56 | 2621522.0648 | 1265510.7082 | 2621493.4604 | 1265501.3143
57 | 2621493.4604 | 1265501.3143 | 2621487.1643 | 1265499.2466
58 | 2621466.0271 | 1265459.2144 | 2621465.9278 | 1265463.3273
59 | 2621461.591 | 1265658.1476 | 2621431.9178 | 1265652.3584 | 2621418.5335 | 1265647.2914
60 | 2621431.1019 | 1265447.1231 | 2621431.454 | 1265444.7381
61 | 2621431.1019 | 1265447.1231 | 2621415.3773 | 1265444.698
62 | 2621291.5749 | 1265628.0911 | 2621299.8285 | 1265629.6886 | 2621325.7752 | 1265629.777
63 | 2621291.5749 | 1265628.0911 | 2621284.3904 | 1265626.5087 | 2621278.5267 | 1265624.0303 | 2621274.1439 | 1265620.1119
64 | 2621406.0953 | 1265443.5191 | 2621413.1622 | 1265444.3563 | 2621415.3773 | 1265444.698
65 | 2621433.0011 | 1265434.2586 | 2621431.454 | 1265444.7381

## bus_geodata
| x | y | coords
0 | 2621395.9469 | 1265479.816
1 | 2621374.7616 | 1265474.8556
2 | 2621397.3239 | 1265480.1384
3 | 2621425.2366 | 1265486.674
4 | 2621426.9536 | 1265475.0959
5 | 2621449.7755 | 1265489.9689
6 | 2621427.878 | 1265468.8628
7 | 2621465.2347 | 1265492.0447
8 | 2621527.3324 | 1265344.9722
9 | 2621502.881 | 1265332.2251
10 | 2621470.5882 | 1265317.4866
11 | 2621470.4776 | 1265325.1693
12 | 2621467.8346 | 1265333.5323
13 | 2621375.1773 | 1265557.0098
14 | 2621368.353 | 1265555.2374
15 | 2621405.0397 | 1265564.7667
16 | 2621341.917 | 1265541.5117
17 | 2621419.2724 | 1265568.4661
18 | 2621395.2597 | 1265593.8739
19 | 2621337.0864 | 1265536.4686
20 | 2621435.3576 | 1265572.647
21 | 2621368.2694 | 1265593.5319
22 | 2621330.3378 | 1265564.8086
23 | 2621441.5665 | 1265574.2609
24 | 2621357.5299 | 1265629.8852
25 | 2621467.2996 | 1265406.4914
26 | 2621467.2959 | 1265406.644
27 | 2621468.2482 | 1265377.2865
28 | 2621466.9256 | 1265421.9877
29 | 2621439.6015 | 1265363.9613
30 | 2621457.5712 | 1265354.5542
31 | 2621466.6497 | 1265433.419
32 | 2621519.3555 | 1265400.5326
33 | 2621515.8793 | 1265417.6122
34 | 2621563.6643 | 1265422.2936
35 | 2621475.1336 | 1265363.5052
36 | 2621466.5348 | 1265438.1799
37 | 2621511.5131 | 1265439.0643
38 | 2621579.6566 | 1265430.1478
39 | 2621472.7685 | 1265335.0868
40 | 2621471.201 | 1265582.5295
41 | 2621449.4894 | 1265546.742
42 | 2621484.725 | 1265584.7584
43 | 2621467.3665 | 1265597.5241
44 | 2621452.516 | 1265536.2295
45 | 2621463.788 | 1265618.5705
46 | 2621541.4068 | 1265470.083
47 | 2621537.775 | 1265478.4317
48 | 2621529.033 | 1265486.3095
49 | 2621556.5937 | 1265487.8622
50 | 2621522.0648 | 1265510.7082
51 | 2621493.4604 | 1265501.3143
52 | 2621466.0271 | 1265459.2144
53 | 2621465.9278 | 1265463.3273
54 | 2621596.5691 | 1265438.4539
55 | 2621487.1643 | 1265499.2466
56 | 2621461.591 | 1265658.1476
57 | 2621418.5335 | 1265647.2914
58 | 2621431.1019 | 1265447.1231
59 | 2621325.7752 | 1265629.777
60 | 2621291.5749 | 1265628.0911
61 | 2621274.1438 | 1265620.1119
62 | 2621415.3773 | 1265444.698
63 | 2621406.0953 | 1265443.5191
64 | 2621431.454 | 1265444.7381
65 | 2621433.0011 | 1265434.2586
66 | 2621482.2681 | 1265339.8334
67 | 2621465.2347 | 1265492.0447

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1