## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4260-5_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4260-5_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4260-5_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4260-5_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4260-5_0_4_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_4260-5_0_4_node_13 | 0.4 | n |  | TRUE
6 | bus_LV_4260-5_0_4_node_85 | 0.4 | n |  | TRUE
7 | bus_LV_4260-5_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_4260-5_0_4_node_91 | 0.4 | n |  | TRUE
9 | bus_LV_4260-5_0_4_node_94 | 0.4 | n |  | TRUE
10 | bus_LV_4260-5_0_4_node_36 | 0.4 | n |  | TRUE
11 | bus_LV_4260-5_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_4260-5_0_4_node_64 | 0.4 | n |  | TRUE
13 | bus_LV_4260-5_0_4_node_31 | 0.4 | n |  | TRUE
14 | bus_LV_4260-5_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_4260-5_0_4_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_4260-5_0_4_node_86 | 0.4 | n |  | TRUE
17 | bus_LV_4260-5_0_4_node_93 | 0.4 | n |  | TRUE
18 | bus_LV_4260-5_0_4_node_98 | 0.4 | n |  | TRUE
19 | bus_LV_4260-5_0_4_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_4260-5_0_4_node_90 | 0.4 | n |  | TRUE
21 | bus_LV_4260-5_0_4_node_95 | 0.4 | n |  | TRUE
22 | bus_LV_4260-5_0_4_node_54 | 0.4 | n |  | TRUE
23 | bus_LV_4260-5_0_4_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_4260-5_0_4_node_33 | 0.4 | n |  | TRUE
25 | bus_LV_4260-5_0_4_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_4260-5_0_4_node_58 | 0.4 | n |  | TRUE
27 | bus_LV_4260-5_0_4_node_89 | 0.4 | n |  | TRUE
28 | bus_LV_4260-5_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_4260-5_0_4_node_62 | 0.4 | n |  | TRUE
30 | bus_LV_4260-5_0_4_node_63 | 0.4 | n |  | TRUE
31 | bus_LV_4260-5_0_4_node_8 | 0.4 | n |  | TRUE
32 | bus_LV_4260-5_0_4_node_9 | 0.4 | n |  | TRUE
33 | bus_LV_4260-5_0_4_node_88 | 0.4 | n |  | TRUE
34 | bus_LV_4260-5_0_4_node_14 | 0.4 | n |  | TRUE
35 | bus_LV_4260-5_0_4_node_15 | 0.4 | n |  | TRUE
36 | bus_LV_4260-5_0_4_node_16 | 0.4 | n |  | TRUE
37 | bus_LV_4260-5_0_4_node_17 | 0.4 | n |  | TRUE
38 | bus_LV_4260-5_0_4_node_18 | 0.4 | n |  | TRUE
39 | bus_LV_4260-5_0_4_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_4260-5_0_4_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_4260-5_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_4260-5_0_4_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_4260-5_0_4_node_25 | 0.4 | n |  | TRUE
44 | bus_LV_4260-5_0_4_node_19 | 0.4 | n |  | TRUE
45 | bus_LV_4260-5_0_4_node_20 | 0.4 | n |  | TRUE
46 | bus_LV_4260-5_0_4_node_22 | 0.4 | n |  | TRUE
47 | bus_LV_4260-5_0_4_node_23 | 0.4 | n |  | TRUE
48 | bus_LV_4260-5_0_4_node_73 | 0.4 | n |  | TRUE
49 | bus_LV_4260-5_0_4_node_103 | 0.4 | n |  | TRUE
50 | bus_LV_4260-5_0_4_node_74 | 0.4 | n |  | TRUE
51 | bus_LV_4260-5_0_4_node_101 | 0.4 | n |  | TRUE
52 | bus_LV_4260-5_0_4_node_27 | 0.4 | n |  | TRUE
53 | bus_LV_4260-5_0_4_node_28 | 0.4 | n |  | TRUE
54 | bus_LV_4260-5_0_4_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_4260-5_0_4_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_4260-5_0_4_node_32 | 0.4 | n |  | TRUE
57 | bus_LV_4260-5_0_4_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_4260-5_0_4_node_82 | 0.4 | n |  | TRUE
59 | bus_LV_4260-5_0_4_node_118 | 0.4 | n |  | TRUE
60 | bus_LV_4260-5_0_4_node_81 | 0.4 | n |  | TRUE
61 | bus_LV_4260-5_0_4_node_117 | 0.4 | n |  | TRUE
62 | bus_LV_4260-5_0_4_node_121 | 0.4 | n |  | TRUE
63 | bus_LV_4260-5_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_4260-5_0_4_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_4260-5_0_4_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_4260-5_0_4_node_39 | 0.4 | n |  | TRUE
67 | bus_LV_4260-5_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_4260-5_0_4_node_41 | 0.4 | n |  | TRUE
69 | bus_LV_4260-5_0_4_node_42 | 0.4 | n |  | TRUE
70 | bus_LV_4260-5_0_4_node_43 | 0.4 | n |  | TRUE
71 | bus_LV_4260-5_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_4260-5_0_4_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_4260-5_0_4_node_102 | 0.4 | n |  | TRUE
74 | bus_LV_4260-5_0_4_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_4260-5_0_4_node_45 | 0.4 | n |  | TRUE
76 | bus_LV_4260-5_0_4_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_4260-5_0_4_node_106 | 0.4 | n |  | TRUE
78 | bus_LV_4260-5_0_4_node_105 | 0.4 | n |  | TRUE
79 | bus_LV_4260-5_0_4_node_47 | 0.4 | n |  | TRUE
80 | bus_LV_4260-5_0_4_node_51 | 0.4 | n |  | TRUE
81 | bus_LV_4260-5_0_4_node_49 | 0.4 | n |  | TRUE
82 | bus_LV_4260-5_0_4_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_4260-5_0_4_node_104 | 0.4 | n |  | TRUE
84 | bus_LV_4260-5_0_4_node_83 | 0.4 | n |  | TRUE
85 | bus_LV_4260-5_0_4_node_96 | 0.4 | n |  | TRUE
86 | bus_LV_4260-5_0_4_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_4260-5_0_4_node_57 | 0.4 | n |  | TRUE
88 | bus_LV_4260-5_0_4_node_97 | 0.4 | n |  | TRUE
89 | bus_LV_4260-5_0_4_node_55 | 0.4 | n |  | TRUE
90 | bus_LV_4260-5_0_4_node_56 | 0.4 | n |  | TRUE
91 | bus_LV_4260-5_0_4_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_4260-5_0_4_node_60 | 0.4 | n |  | TRUE
93 | bus_LV_4260-5_0_4_node_61 | 0.4 | n |  | TRUE
94 | bus_LV_4260-5_0_4_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_4260-5_0_4_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_4260-5_0_4_node_76 | 0.4 | n |  | TRUE
97 | bus_LV_4260-5_0_4_node_80 | 0.4 | n |  | TRUE
98 | bus_LV_4260-5_0_4_node_79 | 0.4 | n |  | TRUE
99 | bus_LV_4260-5_0_4_node_119 | 0.4 | n |  | TRUE
100 | bus_LV_4260-5_0_4_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_4260-5_0_4_node_70 | 0.4 | n |  | TRUE
102 | bus_LV_4260-5_0_4_node_72 | 0.4 | n |  | TRUE
103 | bus_LV_4260-5_0_4_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_4260-5_0_4_node_116 | 0.4 | n |  | TRUE
105 | bus_LV_4260-5_0_4_node_99 | 0.4 | n |  | TRUE
106 | bus_LV_4260-5_0_4_node_100 | 0.4 | n |  | TRUE
107 | bus_LV_4260-5_0_4_node_109 | 0.4 | n |  | TRUE
108 | bus_LV_4260-5_0_4_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_4260-5_0_4_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_4260-5_0_4_node_113 | 0.4 | n |  | TRUE
111 | bus_LV_4260-5_0_4_node_114 | 0.4 | n |  | TRUE
112 | bus_LV_4260-5_0_4_node_120 | 0.4 | n |  | TRUE
113 | bus_LV_4260-5_0_4_node_115 | 0.4 | n |  | TRUE
114 | bus_MV_305_0_node_36 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4260-5_0_4_load_0 | 0 | 0.0032876 | 0.00082394 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4260-5_0_4_load_85 | 6 | 0.00068361 | 0.00017133 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4260-5_0_4_load_94 | 9 | 0.017486 | 0.0043823 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4260-5_0_4_load_64 | 12 | 0.05669 | 0.014208 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4260-5_0_4_load_12 | 15 | 0.012054 | 0.0030211 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4260-5_0_4_load_86 | 16 | 0.00053184 | 0.00013329 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4260-5_0_4_load_98 | 18 | 0.012638 | 0.0031675 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4260-5_0_4_load_90 | 20 | 0.0070438 | 0.0017653 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4260-5_0_4_load_95 | 21 | 0.019381 | 0.0048574 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4260-5_0_4_load_53 | 23 | 0.0028533 | 0.00071512 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4260-5_0_4_load_33 | 24 | 0.031448 | 0.0078816 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4260-5_0_4_load_59 | 25 | 0.033425 | 0.0083771 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4260-5_0_4_load_58 | 26 | 0.027595 | 0.006916 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4260-5_0_4_load_89 | 27 | 0.023638 | 0.0059243 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4260-5_0_4_load_29 | 28 | 0.0048934 | 0.0012264 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4260-5_0_4_load_62 | 29 | 0.065888 | 0.016513 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4260-5_0_4_load_8 | 31 | 0.001229 | 0.00030801 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4260-5_0_4_load_88 | 33 | 0.00090714 | 0.00022735 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4260-5_0_4_load_14 | 34 | 0.0012575 | 0.00031517 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4260-5_0_4_load_15 | 35 | 0.0011947 | 0.00029942 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4260-5_0_4_load_16 | 36 | 0.0011942 | 0.0002993 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4260-5_0_4_load_17 | 37 | 0.0010566 | 0.00026481 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4260-5_0_4_load_24 | 39 | 0.0010554 | 0.0002645 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4260-5_0_4_load_26 | 40 | 0.0012466 | 0.00031242 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4260-5_0_4_load_30 | 41 | 0.0088248 | 0.0022117 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4260-5_0_4_load_25 | 43 | 0.0022175 | 0.00055577 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4260-5_0_4_load_19 | 44 | 0.0015289 | 0.00038319 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4260-5_0_4_load_20 | 45 | 0.00085418 | 0.00021408 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4260-5_0_4_load_22 | 46 | 0.00082119 | 0.00020581 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4260-5_0_4_load_23 | 47 | 0.0010516 | 0.00026357 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4260-5_0_4_load_73 | 48 | 0.0039089 | 0.00097966 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4260-5_0_4_load_103 | 49 | 0.0011566 | 0.00028988 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4260-5_0_4_load_74 | 50 | 0.0039473 | 0.00098928 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4260-5_0_4_load_101 | 51 | 0.0019154 | 0.00048005 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4260-5_0_4_load_27 | 52 | 0.00066134 | 0.00016575 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4260-5_0_4_load_28 | 53 | 0.0017074 | 0.00042791 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4260-5_0_4_load_34 | 54 | 0.002088 | 0.00052329 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4260-5_0_4_load_82 | 58 | 0.0010614 | 0.00026602 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4260-5_0_4_load_118 | 59 | 0.0063632 | 0.0015948 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4260-5_0_4_load_81 | 60 | 0.0071209 | 0.0017847 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4260-5_0_4_load_117 | 61 | 0.0010287 | 0.00025782 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4260-5_0_4_load_121 | 62 | 0.025171 | 0.0063084 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4260-5_0_4_load_37 | 64 | 0.0014222 | 0.00035645 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4260-5_0_4_load_38 | 65 | 0.0012315 | 0.00030865 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4260-5_0_4_load_39 | 66 | 0.0023774 | 0.00059583 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4260-5_0_4_load_40 | 67 | 0.0011976 | 0.00030014 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4260-5_0_4_load_41 | 68 | 0.0017555 | 0.00043997 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4260-5_0_4_load_42 | 69 | 0.0011982 | 0.0003003 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4260-5_0_4_load_102 | 73 | 0.0011976 | 0.00030014 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4260-5_0_4_load_44 | 74 | 0.0059823 | 0.0014993 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4260-5_0_4_load_106 | 77 | 0.0038523 | 0.00096547 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4260-5_0_4_load_105 | 78 | 0.0053613 | 0.0013437 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4260-5_0_4_load_49 | 81 | 0.0030368 | 0.00076109 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4260-5_0_4_load_71 | 82 | 0.0038538 | 0.00096586 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4260-5_0_4_load_104 | 83 | 0.0055533 | 0.0013918 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4260-5_0_4_load_96 | 85 | 0.0050891 | 0.0012754 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4260-5_0_4_load_68 | 86 | 0.0025328 | 0.00063478 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4260-5_0_4_load_97 | 88 | 0.0072126 | 0.0018077 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4260-5_0_4_load_55 | 89 | 0.0028486 | 0.00071393 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4260-5_0_4_load_56 | 90 | 0.0081454 | 0.0020414 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4260-5_0_4_load_60 | 92 | 0.0053772 | 0.0013477 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4260-5_0_4_load_61 | 93 | 0.02065 | 0.0051755 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4260-5_0_4_load_76 | 96 | 0.001975 | 0.00049497 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4260-5_0_4_load_80 | 97 | 0.00080746 | 0.00020237 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4260-5_0_4_load_79 | 98 | 0.0019233 | 0.00048203 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4260-5_0_4_load_119 | 99 | 0.0010755 | 0.00026955 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4260-5_0_4_load_78 | 100 | 0.0011371 | 0.00028499 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4260-5_0_4_load_70 | 101 | 0.0029273 | 0.00073366 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4260-5_0_4_load_72 | 102 | 0.004178 | 0.0010471 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4260-5_0_4_load_107 | 103 | 0.0058373 | 0.001463 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4260-5_0_4_load_116 | 104 | 0.0010287 | 0.00025782 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4260-5_0_4_load_99 | 105 | 0.0037295 | 0.00093469 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4260-5_0_4_load_100 | 106 | 0.0070061 | 0.0017559 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4260-5_0_4_load_109 | 107 | 0.00084714 | 0.00021231 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4260-5_0_4_load_110 | 108 | 0.00084904 | 0.00021279 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4260-5_0_4_load_111 | 109 | 0.00084714 | 0.00021231 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4260-5_0_4_load_113 | 110 | 0.00091134 | 0.0002284 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4260-5_0_4_load_114 | 111 | 0.0010468 | 0.00026235 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4260-5_0_4_load_120 | 112 | 0.0010168 | 0.00025483 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4260-5_0_4_load_115 | 113 | 0.0010287 | 0.00025782 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 24 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4260-5_0_4_line_0 |  | 0 | 1 | 0.02014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4260-5_0_4_line_1 |  | 0 | 2 | 0.053342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4260-5_0_4_line_2 |  | 1 | 3 | 0.041108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4260-5_0_4_line_3 |  | 2 | 4 | 0.010644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4260-5_0_4_line_4 |  | 3 | 5 | 0.072752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4260-5_0_4_line_5 |  | 3 | 6 | 0.036284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4260-5_0_4_line_6 |  | 4 | 10 | 0.034051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4260-5_0_4_line_7 |  | 5 | 14 | 0.009952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4260-5_0_4_line_8 |  | 5 | 15 | 0.081599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4260-5_0_4_line_9 |  | 6 | 16 | 0.017704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4260-5_0_4_line_10 |  | 7 | 8 | 0.058616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4260-5_0_4_line_11 |  | 7 | 9 | 0.0273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4260-5_0_4_line_12 |  | 8 | 19 | 0.034421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4260-5_0_4_line_13 |  | 8 | 20 | 0.027755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4260-5_0_4_line_14 |  | 8 | 17 | 0.045196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4260-5_0_4_line_15 |  | 9 | 21 | 0.019312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4260-5_0_4_line_16 |  | 10 | 22 | 0.038374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4260-5_0_4_line_17 |  | 10 | 23 | 0.024837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4260-5_0_4_line_18 |  | 11 | 12 | 0.058598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_4260-5_0_4_line_19 |  | 11 | 13 | 0.012299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_4260-5_0_4_line_20 |  | 12 | 27 | 0.019736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4260-5_0_4_line_21 |  | 13 | 28 | 0.017503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_4260-5_0_4_line_22 |  | 13 | 24 | 0.048998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_4260-5_0_4_line_23 |  | 14 | 33 | 0.069844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4260-5_0_4_line_24 |  | 14 | 32 | 0.083439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4260-5_0_4_line_25 |  | 17 | 18 | 0.011035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4260-5_0_4_line_26 |  | 18 | 105 | 0.013317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4260-5_0_4_line_27 |  | 19 | 85 | 0.019771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4260-5_0_4_line_28 |  | 22 | 62 | 0.046368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4260-5_0_4_line_29 |  | 23 | 63 | 0.019937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4260-5_0_4_line_30 |  | 25 | 26 | 0.0032461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4260-5_0_4_line_31 |  | 26 | 92 | 0.037408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4260-5_0_4_line_32 |  | 27 | 93 | 0.058758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4260-5_0_4_line_33 |  | 28 | 41 | 0.013195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_4260-5_0_4_line_34 |  | 29 | 30 | 0.021924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4260-5_0_4_line_35 |  | 30 | 94 | 0.23037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4260-5_0_4_line_36 |  | 30 | 57 | 0.006459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4260-5_0_4_line_37 |  | 31 | 32 | 0.09032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4260-5_0_4_line_38 |  | 34 | 35 | 0.0066877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_4260-5_0_4_line_39 |  | 34 | 36 | 0.00105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_4260-5_0_4_line_40 |  | 35 | 37 | 0.012521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_4260-5_0_4_line_41 |  | 36 | 38 | 0.014811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_4260-5_0_4_line_42 |  | 37 | 39 | 0.0051055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_4260-5_0_4_line_43 |  | 38 | 40 | 0.032848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4260-5_0_4_line_44 |  | 38 | 41 | 0.0070308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_4260-5_0_4_line_45 |  | 39 | 42 | 0.016079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_4260-5_0_4_line_46 |  | 40 | 43 | 0.0018699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4260-5_0_4_line_47 |  | 42 | 47 | 0.012636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_4260-5_0_4_line_48 |  | 42 | 44 | 0.011147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4260-5_0_4_line_49 |  | 43 | 52 | 0.0049213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4260-5_0_4_line_50 |  | 44 | 45 | 0.0049782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4260-5_0_4_line_51 |  | 45 | 46 | 0.01158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4260-5_0_4_line_52 |  | 46 | 48 | 0.00048597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4260-5_0_4_line_53 |  | 47 | 49 | 0.0058864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_4260-5_0_4_line_54 |  | 48 | 50 | 0.005578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4260-5_0_4_line_55 |  | 49 | 51 | 0.0031703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_4260-5_0_4_line_56 |  | 51 | 73 | 0.024619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_4260-5_0_4_line_57 |  | 52 | 53 | 0.014339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4260-5_0_4_line_58 |  | 53 | 54 | 0.011673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4260-5_0_4_line_59 |  | 54 | 55 | 0.0058728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4260-5_0_4_line_60 |  | 55 | 60 | 0.014493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4260-5_0_4_line_61 |  | 55 | 58 | 0.01269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4260-5_0_4_line_62 |  | 56 | 57 | 0.008882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4260-5_0_4_line_63 |  | 56 | 58 | 0.035065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4260-5_0_4_line_64 |  | 57 | 59 | 0.013831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4260-5_0_4_line_65 |  | 59 | 99 | 0.047293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4260-5_0_4_line_66 |  | 60 | 61 | 0.0095378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4260-5_0_4_line_67 |  | 61 | 104 | 0.00038651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4260-5_0_4_line_68 |  | 63 | 81 | 0.046273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4260-5_0_4_line_69 |  | 64 | 65 | 0.0022187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4260-5_0_4_line_70 |  | 64 | 66 | 0.003431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4260-5_0_4_line_71 |  | 65 | 67 | 0.014959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4260-5_0_4_line_72 |  | 67 | 68 | 0.0027232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4260-5_0_4_line_73 |  | 68 | 69 | 0.0035003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4260-5_0_4_line_74 |  | 69 | 70 | 0.018942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4260-5_0_4_line_75 |  | 70 | 71 | 0.005408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4260-5_0_4_line_76 |  | 71 | 72 | 0.006404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_4260-5_0_4_line_77 |  | 71 | 73 | 0.0088864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_4260-5_0_4_line_78 |  | 72 | 82 | 0.016851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_4260-5_0_4_line_79 |  | 72 | 86 | 0.010761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4260-5_0_4_line_80 |  | 74 | 75 | 0.002513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4260-5_0_4_line_81 |  | 75 | 76 | 0.005503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4260-5_0_4_line_82 |  | 76 | 77 | 0.023226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_4260-5_0_4_line_83 |  | 76 | 78 | 0.036077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_4260-5_0_4_line_84 |  | 77 | 82 | 0.018969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_4260-5_0_4_line_85 |  | 78 | 83 | 0.027627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_4260-5_0_4_line_86 |  | 79 | 80 | 0.03006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
87 | LV_4260-5_0_4_line_87 |  | 79 | 81 | 0.031664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4260-5_0_4_line_88 |  | 80 | 84 | 0.019683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_4260-5_0_4_line_89 |  | 80 | 83 | 0.010026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_4260-5_0_4_line_90 |  | 84 | 87 | 0.03192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_4260-5_0_4_line_91 |  | 85 | 88 | 0.016314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4260-5_0_4_line_92 |  | 86 | 101 | 0.021149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4260-5_0_4_line_93 |  | 87 | 91 | 0.027436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_4260-5_0_4_line_94 |  | 87 | 90 | 0.021804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4260-5_0_4_line_95 |  | 88 | 91 | 0.030989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
96 | LV_4260-5_0_4_line_96 |  | 89 | 90 | 0.028771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4260-5_0_4_line_97 |  | 92 | 93 | 0.019932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4260-5_0_4_line_98 |  | 94 | 95 | 0.071829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4260-5_0_4_line_99 |  | 94 | 96 | 0.027921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4260-5_0_4_line_100 |  | 95 | 97 | 0.031003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4260-5_0_4_line_101 |  | 95 | 98 | 0.039035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4260-5_0_4_line_102 |  | 98 | 100 | 0.013955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4260-5_0_4_line_103 |  | 99 | 112 | 0.03417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4260-5_0_4_line_104 |  | 101 | 102 | 0.031157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4260-5_0_4_line_105 |  | 102 | 103 | 0.018923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4260-5_0_4_line_106 |  | 104 | 113 | 0.00038046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4260-5_0_4_line_107 |  | 105 | 106 | 0.0090803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4260-5_0_4_line_108 |  | 107 | 108 | 7.0529e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4260-5_0_4_line_109 |  | 108 | 109 | 7.0508e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4260-5_0_4_line_110 |  | 109 | 110 | 4.4002e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4260-5_0_4_line_111 |  | 110 | 111 | 0.017367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4260-5_0_4_line_112 |  | 111 | 113 | 0.012174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4260-5_0_4_trafo_33 | 0.63 MVA 20/0.4 kV | 114 | 24 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2639231.4353 | 1266072.4075 | 2639231.983 | 1266052.2745
1 | 2639212.2172 | 1266002.7747 | 2639225.854 | 1266034.2098 | 2639231.983 | 1266052.2745
2 | 2639271.2689 | 1266082.6901 | 2639266.9891 | 1266080.9605 | 2639254.0886 | 1266077.0165 | 2639231.4353 | 1266072.4075
3 | 2639202.4102 | 1266006.8682 | 2639209.0118 | 1266003.6318 | 2639212.2172 | 1266002.7747
4 | 2639297.6416 | 1266149.5464 | 2639292.0675 | 1266130.7404 | 2639281.4185 | 1266097.2791 | 2639276.4323 | 1266087.4167 | 2639271.2689 | 1266082.6901
5 | 2639271.2689 | 1266082.6901 | 2639276.4258 | 1266075.9306 | 2639302.8922 | 1266067.4829
6 | 2639202.4102 | 1266006.8682 | 2639195.5017 | 1266009.8468 | 2639178.0461 | 1266021.8064 | 2639172.9367 | 1266023.685
7 | 2639297.6416 | 1266149.5464 | 2639300.4918 | 1266159.0833
8 | 2639297.6416 | 1266149.5464 | 2639343.41 | 1266136.7636 | 2639346.6751 | 1266133.7054 | 2639347.6855 | 1266127.819 | 2639341.3284 | 1266105.057
9 | 2639302.8922 | 1266067.4829 | 2639319.7574 | 1266062.0998
10 | 2639067.6012 | 1266129.8424 | 2639071.0545 | 1266137.037 | 2639080.2706 | 1266156.2227 | 2639092.9771 | 1266182.6812
11 | 2639092.9771 | 1266182.6812 | 2639114.9284 | 1266166.4506
12 | 2639052.6889 | 1266098.7995 | 2639067.6012 | 1266129.8424
13 | 2639067.6012 | 1266129.8424 | 2639041.5561 | 1266139.4328
14 | 2639067.6012 | 1266129.8424 | 2639071.0545 | 1266137.037 | 2639080.1992 | 1266126.0229 | 2639095.5325 | 1266119.564 | 2639093.4862 | 1266113.6462
15 | 2639114.9284 | 1266166.4506 | 2639130.4569 | 1266154.9691
16 | 2639146.7904 | 1265997.3932 | 2639153.6461 | 1265998.9841 | 2639159.8653 | 1266005.7301 | 2639168.1348 | 1266016.6482 | 2639172.9367 | 1266023.685
17 | 2639172.9367 | 1266023.685 | 2639149.6258 | 1266032.2585
18 | 2639134.5943 | 1265875.5921 | 2639192.296 | 1265865.3813
19 | 2639134.5943 | 1265875.5921 | 2639122.4654 | 1265877.8357
20 | 2639211.7296 | 1265861.9424 | 2639192.296 | 1265865.3813
21 | 2639122.4654 | 1265877.8357 | 2639105.2565 | 1265881.0284
22 | 2639122.4654 | 1265877.8357 | 2639123.2261 | 1265882.3551 | 2639129.5108 | 1265882.6413 | 2639135.0161 | 1265891.484 | 2639147.1993 | 1265916.3695
23 | 2639300.4918 | 1266159.0833 | 2639305.4689 | 1266157.8377 | 2639352.0279 | 1266146.161 | 2639354.5816 | 1266145.9334 | 2639359.8212 | 1266145.9682 | 2639363.1718 | 1266147.0469 | 2639365.9771 | 1266150.8571 | 2639366.1682 | 1266151.4863
24 | 2639300.4918 | 1266159.0833 | 2639301.9867 | 1266164.1079 | 2639305.5506 | 1266176.1291 | 2639313.0987 | 1266189.0329 | 2639326.6882 | 1266207.0584 | 2639333.1063 | 1266214.4063 | 2639336.4686 | 1266218.2536 | 2639345.5816 | 1266227.8989
25 | 2639093.4862 | 1266113.6462 | 2639089.8802 | 1266103.2165
26 | 2639089.8802 | 1266103.2165 | 2639086.0766 | 1266092.2153 | 2639086.7424 | 1266090.6766
27 | 2639052.6889 | 1266098.7995 | 2639034.0598 | 1266105.4216
28 | 2639133.6082 | 1265952.9298 | 2639138.3699 | 1265969.4509 | 2639146.7904 | 1265997.3932
29 | 2639130.9145 | 1266039.1403 | 2639149.6258 | 1266032.2585
30 | 2639299.6604 | 1265884.1505 | 2639300.5667 | 1265887.2675
31 | 2639299.6604 | 1265884.1505 | 2639289.2165 | 1265848.2304 | 2639289.2165 | 1265848.2304
32 | 2639269.589 | 1265851.7037 | 2639211.7296 | 1265861.9424
33 | 2639092.2831 | 1265883.4352 | 2639105.2565 | 1265881.0284
34 | 2639100.1013 | 1265792.9383 | 2639105.3137 | 1265807.3831 | 2639107.7104 | 1265813.4974
35 | 2639100.1013 | 1265792.9383 | 2639105.0041 | 1265791.5809 | 2639097.7909 | 1265767.7273 | 2639097.5717 | 1265763.3004 | 2639099.5785 | 1265756.9981 | 2639102.7211 | 1265753.1272 | 2639107.0354 | 1265749.6977 | 2639129.2841 | 1265741.6724 | 2639146.5011 | 1265736.2935 | 2639197.727 | 1265724.1017 | 2639212.4583 | 1265722.298 | 2639222.8076 | 1265721.655 | 2639234.0325 | 1265721.7962 | 2639235.2145 | 1265721.8151 | 2639249.0429 | 1265723.3301 | 2639249.7489 | 1265719.054 | 2639278.0848 | 1265723.0004
36 | 2639100.1013 | 1265792.9383 | 2639093.878 | 1265794.7318
37 | 2639345.5816 | 1266227.8989 | 2639353.2766 | 1266242.4716 | 2639380.5112 | 1266311.1062
38 | 2639069.8531 | 1265888.0019 | 2639063.3103 | 1265889.3867
39 | 2639069.8531 | 1265888.0019 | 2639070.8803 | 1265887.7845
40 | 2639063.3103 | 1265889.3867 | 2639051.0607 | 1265891.9792
41 | 2639085.3702 | 1265884.7177 | 2639070.8803 | 1265887.7845
42 | 2639046.2896 | 1265893.7595 | 2639050.1159 | 1265892.1792 | 2639051.0607 | 1265891.9792
43 | 2639085.3702 | 1265884.7177 | 2639078.0366 | 1265852.699
44 | 2639085.3702 | 1265884.7177 | 2639092.2831 | 1265883.4352
45 | 2639032.8082 | 1265902.2611 | 2639040.7092 | 1265896.0644 | 2639046.2896 | 1265893.7595
46 | 2639078.0366 | 1265852.699 | 2639077.6192 | 1265850.8763
47 | 2639032.8082 | 1265902.2611 | 2639030.6562 | 1265911.1866 | 2639030.4236 | 1265914.6339
48 | 2639032.8082 | 1265902.2611 | 2639024.1806 | 1265897.612 | 2639022.8346 | 1265897.625
49 | 2639076.5204 | 1265846.0792 | 2639077.6192 | 1265850.8763
50 | 2639022.8346 | 1265897.625 | 2639017.8566 | 1265897.6729
51 | 2639006.4323 | 1265899.3046 | 2639014.5883 | 1265897.7044 | 2639017.8566 | 1265897.6729
52 | 2639005.9554 | 1265899.3981 | 2639006.4323 | 1265899.3046
53 | 2639030.5544 | 1265920.4873 | 2639030.1972 | 1265917.9885 | 2639030.4236 | 1265914.6339
54 | 2639005.9554 | 1265899.3981 | 2639000.4818 | 1265900.4721
55 | 2639031.0029 | 1265923.6257 | 2639030.5544 | 1265920.4873
56 | 2639031.0029 | 1265923.6257 | 2639031.2407 | 1265925.2895 | 2639037.2864 | 1265947.4168
57 | 2639076.5204 | 1265846.0792 | 2639075.8132 | 1265842.9915 | 2639074.6384 | 1265837.3463 | 2639072.4467 | 1265832.8953 | 2639072.2225 | 1265832.512
58 | 2639064.2471 | 1265824.3091 | 2639065.0315 | 1265824.7962 | 2639069.8485 | 1265828.4528 | 2639072.2225 | 1265832.512
59 | 2639059.2579 | 1265821.211 | 2639064.2471 | 1265824.3091
60 | 2639059.2579 | 1265821.211 | 2639051.4447 | 1265819.7807 | 2639045.0148 | 1265821.0311
61 | 2639059.2579 | 1265821.211 | 2639063.3111 | 1265815.1112 | 2639062.2768 | 1265809.8451
62 | 2639093.878 | 1265794.7318 | 2639096.6984 | 1265803.1565
63 | 2639096.6984 | 1265803.1565 | 2639062.2768 | 1265809.8451
64 | 2639093.878 | 1265794.7318 | 2639090.0949 | 1265781.4287
65 | 2639090.0949 | 1265781.4287 | 2639088.6097 | 1265776.206 | 2639084.507 | 1265764.7152 | 2639081.7384 | 1265762.1283 | 2639079.0247 | 1265760.3314 | 2639076.1818 | 1265759.8678 | 2639056.8502 | 1265763.8528
66 | 2639035.6524 | 1265822.8519 | 2639045.0148 | 1265821.0311
67 | 2639035.6524 | 1265822.8519 | 2639035.273 | 1265822.9257
68 | 2639130.9145 | 1266039.1403 | 2639097.7302 | 1266051.3408 | 2639087.4851 | 1266055.1101
69 | 2639081.6549 | 1265949.1276 | 2639079.5283 | 1265949.7602
70 | 2639084.9434 | 1265948.1492 | 2639081.6549 | 1265949.1276
71 | 2639079.5283 | 1265949.7602 | 2639065.1908 | 1265954.0258
72 | 2639062.5806 | 1265954.8024 | 2639065.1908 | 1265954.0258
73 | 2639062.5806 | 1265954.8024 | 2639059.2256 | 1265955.8006
74 | 2639041.0697 | 1265961.2022 | 2639059.2256 | 1265955.8006
75 | 2639039.6285 | 1265955.989 | 2639041.0697 | 1265961.2022
76 | 2639039.6285 | 1265955.989 | 2639033.4655 | 1265957.7941
77 | 2639039.6285 | 1265955.989 | 2639037.2864 | 1265947.4168
78 | 2639033.4655 | 1265957.7941 | 2639038.3524 | 1265973.921
79 | 2639033.4655 | 1265957.7941 | 2639023.1379 | 1265960.8155
80 | 2639055.8773 | 1266012.7257 | 2639055.1571 | 1266010.318
81 | 2639055.8773 | 1266012.7257 | 2639050.5893 | 1266014.303
82 | 2639050.5893 | 1266014.303 | 2639043.8536 | 1265992.0751
83 | 2639050.5893 | 1266014.303 | 2639057.4343 | 1266036.8866 | 2639051.4727 | 1266047.849
84 | 2639043.8536 | 1265992.0751 | 2639038.3524 | 1265973.921
85 | 2639034.0442 | 1266067.8531 | 2639038.3205 | 1266066.2926 | 2639044.6161 | 1266055.7933 | 2639048.487 | 1266053.3393 | 2639051.4727 | 1266047.849
86 | 2639057.7687 | 1266066.043 | 2639029.6232 | 1266076.8205
87 | 2639057.7687 | 1266066.043 | 2639087.4851 | 1266055.1101
88 | 2639029.6232 | 1266076.8205 | 2639011.1917 | 1266083.8707
89 | 2639029.6232 | 1266076.8205 | 2639033.9509 | 1266067.8871 | 2639034.0442 | 1266067.8531
90 | 2638981.2289 | 1266095.1146 | 2639011.1917 | 1266083.8707
91 | 2639034.0598 | 1266105.4216 | 2639018.6879 | 1266110.8859
92 | 2639002.8395 | 1265966.7541 | 2639023.1379 | 1265960.8155
93 | 2638981.2289 | 1266095.1146 | 2638984.8096 | 1266108.1253 | 2638989.4886 | 1266121.2655
94 | 2638981.2289 | 1266095.1146 | 2638975.411 | 1266074.1016
95 | 2638989.4886 | 1266121.2655 | 2639018.6879 | 1266110.8859
96 | 2638967.7341 | 1266046.3741 | 2638975.411 | 1266074.1016
97 | 2639269.589 | 1265851.7037 | 2639289.2165 | 1265848.2304
98 | 2639247.3341 | 1265672.2378 | 2639247.0753 | 1265679.4635 | 2639249.3032 | 1265688.6515 | 2639250.4333 | 1265689.6708 | 2639251.4057 | 1265703.1091 | 2639250.3968 | 1265708.7843 | 2639250.2506 | 1265713.798 | 2639260.932 | 1265716.4263 | 2639278.0848 | 1265723.0004
99 | 2639278.0848 | 1265723.0004 | 2639304.937 | 1265730.6499
100 | 2639216.9114 | 1265678.6518 | 2639247.3341 | 1265672.2378
101 | 2639247.3341 | 1265672.2378 | 2639254.0671 | 1265670.8148 | 2639264.6271 | 1265672.4638 | 2639284.8172 | 1265679.7519
102 | 2639284.8172 | 1265679.7519 | 2639297.9433 | 1265684.49
103 | 2639023.3528 | 1265770.5472 | 2639028.0652 | 1265769.9019 | 2639050.7291 | 1265765.1147 | 2639056.8502 | 1265763.8528
104 | 2639002.8395 | 1265966.7541 | 2639011.3083 | 1265996.7379
105 | 2639016.4518 | 1266014.9483 | 2639011.3083 | 1265996.7379
106 | 2639035.273 | 1265822.9257 | 2639034.8995 | 1265822.9983
107 | 2639086.7424 | 1266090.6766 | 2639087.7892 | 1266088.2571 | 2639093.8379 | 1266086.0345
108 | 2639005.89 | 1265828.6399 | 2639005.883 | 1265828.6413
109 | 2639005.8969 | 1265828.6386 | 2639005.89 | 1265828.6399
110 | 2639005.9012 | 1265828.6378 | 2639005.8969 | 1265828.6386
111 | 2639005.9012 | 1265828.6378 | 2639022.949 | 1265825.3224
112 | 2639034.8995 | 1265822.9983 | 2639022.949 | 1265825.3224

## bus_geodata
| x | y | coords
0 | 2639231.983 | 1266052.2745
1 | 2639231.4353 | 1266072.4075
2 | 2639212.2172 | 1266002.7747
3 | 2639271.2689 | 1266082.6901
4 | 2639202.4102 | 1266006.8682
5 | 2639297.6416 | 1266149.5464
6 | 2639302.8922 | 1266067.4829
7 | 2639092.9771 | 1266182.6812
8 | 2639067.6012 | 1266129.8424
9 | 2639114.9284 | 1266166.4506
10 | 2639172.9367 | 1266023.685
11 | 2639134.5943 | 1265875.5921
12 | 2639192.296 | 1265865.3813
13 | 2639122.4654 | 1265877.8357
14 | 2639300.4918 | 1266159.0833
15 | 2639341.3284 | 1266105.057
16 | 2639319.7574 | 1266062.0998
17 | 2639093.4862 | 1266113.6462
18 | 2639089.8802 | 1266103.2165
19 | 2639052.6889 | 1266098.7995
20 | 2639041.5561 | 1266139.4328
21 | 2639130.4569 | 1266154.9691
22 | 2639146.7904 | 1265997.3932
23 | 2639149.6258 | 1266032.2585
24 | 2639147.1993 | 1265916.3695
25 | 2639300.5667 | 1265887.2675
26 | 2639299.6604 | 1265884.1505
27 | 2639211.7296 | 1265861.9424
28 | 2639105.2565 | 1265881.0284
29 | 2639107.7104 | 1265813.4974
30 | 2639100.1013 | 1265792.9383
31 | 2639380.5112 | 1266311.1062
32 | 2639345.5816 | 1266227.8989
33 | 2639366.1682 | 1266151.4863
34 | 2639069.8531 | 1265888.0019
35 | 2639063.3103 | 1265889.3867
36 | 2639070.8803 | 1265887.7845
37 | 2639051.0607 | 1265891.9792
38 | 2639085.3702 | 1265884.7177
39 | 2639046.2896 | 1265893.7595
40 | 2639078.0366 | 1265852.699
41 | 2639092.2831 | 1265883.4352
42 | 2639032.8082 | 1265902.2611
43 | 2639077.6192 | 1265850.8763
44 | 2639022.8346 | 1265897.625
45 | 2639017.8566 | 1265897.6729
46 | 2639006.4323 | 1265899.3046
47 | 2639030.4236 | 1265914.6339
48 | 2639005.9554 | 1265899.3981
49 | 2639030.5544 | 1265920.4873
50 | 2639000.4818 | 1265900.4721
51 | 2639031.0029 | 1265923.6257
52 | 2639076.5204 | 1265846.0792
53 | 2639072.2225 | 1265832.512
54 | 2639064.2471 | 1265824.3091
55 | 2639059.2579 | 1265821.211
56 | 2639096.6984 | 1265803.1565
57 | 2639093.878 | 1265794.7318
58 | 2639062.2768 | 1265809.8451
59 | 2639090.0949 | 1265781.4287
60 | 2639045.0148 | 1265821.0311
61 | 2639035.6524 | 1265822.8519
62 | 2639133.6082 | 1265952.9298
63 | 2639130.9145 | 1266039.1403
64 | 2639081.6549 | 1265949.1276
65 | 2639079.5283 | 1265949.7602
66 | 2639084.9434 | 1265948.1492
67 | 2639065.1908 | 1265954.0258
68 | 2639062.5806 | 1265954.8024
69 | 2639059.2256 | 1265955.8006
70 | 2639041.0697 | 1265961.2022
71 | 2639039.6285 | 1265955.989
72 | 2639033.4655 | 1265957.7941
73 | 2639037.2864 | 1265947.4168
74 | 2639055.1571 | 1266010.318
75 | 2639055.8773 | 1266012.7257
76 | 2639050.5893 | 1266014.303
77 | 2639043.8536 | 1265992.0751
78 | 2639051.4727 | 1266047.849
79 | 2639057.7687 | 1266066.043
80 | 2639029.6232 | 1266076.8205
81 | 2639087.4851 | 1266055.1101
82 | 2639038.3524 | 1265973.921
83 | 2639034.0442 | 1266067.8531
84 | 2639011.1917 | 1266083.8707
85 | 2639034.0598 | 1266105.4217
86 | 2639023.1379 | 1265960.8155
87 | 2638981.2289 | 1266095.1146
88 | 2639018.6879 | 1266110.8859
89 | 2638967.7341 | 1266046.3741
90 | 2638975.411 | 1266074.1016
91 | 2638989.4886 | 1266121.2655
92 | 2639289.2165 | 1265848.2304
93 | 2639269.589 | 1265851.7037
94 | 2639278.0848 | 1265723.0004
95 | 2639247.3341 | 1265672.2378
96 | 2639304.937 | 1265730.6499
97 | 2639216.9114 | 1265678.6518
98 | 2639284.8172 | 1265679.7519
99 | 2639056.8502 | 1265763.8528
100 | 2639297.9433 | 1265684.49
101 | 2639002.8395 | 1265966.7541
102 | 2639011.3083 | 1265996.7379
103 | 2639016.4518 | 1266014.9483
104 | 2639035.273 | 1265822.9257
105 | 2639086.7424 | 1266090.6766
106 | 2639093.8379 | 1266086.0345
107 | 2639005.883 | 1265828.6413
108 | 2639005.89 | 1265828.6399
109 | 2639005.8969 | 1265828.6386
110 | 2639005.9012 | 1265828.6378
111 | 2639022.949 | 1265825.3224
112 | 2639023.3528 | 1265770.5472
113 | 2639034.8995 | 1265822.9983
114 | 2639122.4654 | 1265877.8357

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1