## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4261-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4261-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4261-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4261-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4261-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4261-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4261-3_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4261-3_0_4_node_11 | 0.4 | n |  | TRUE
8 | bus_LV_4261-3_0_4_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_4261-3_0_4_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_4261-3_0_4_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_4261-3_0_4_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_4261-3_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_4261-3_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_4261-3_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_4261-3_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_4261-3_0_4_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_4261-3_0_4_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_4261-3_0_4_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_4261-3_0_4_node_36 | 0.4 | n |  | TRUE
20 | bus_LV_4261-3_0_4_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_4261-3_0_4_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_4261-3_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_4261-3_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_4261-3_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_4261-3_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_4261-3_0_4_node_33 | 0.4 | n |  | TRUE
27 | bus_LV_4261-3_0_4_node_67 | 0.4 | n |  | TRUE
28 | bus_LV_4261-3_0_4_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_4261-3_0_4_node_66 | 0.4 | n |  | TRUE
30 | bus_LV_4261-3_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_4261-3_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_4261-3_0_4_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_4261-3_0_4_node_52 | 0.4 | n |  | TRUE
34 | bus_LV_4261-3_0_4_node_63 | 0.4 | n |  | TRUE
35 | bus_LV_4261-3_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_4261-3_0_4_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_4261-3_0_4_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_4261-3_0_4_node_32 | 0.4 | n |  | TRUE
39 | bus_LV_4261-3_0_4_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_4261-3_0_4_node_89 | 0.4 | n |  | TRUE
41 | bus_LV_4261-3_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_4261-3_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_4261-3_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_4261-3_0_4_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_4261-3_0_4_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_4261-3_0_4_node_60 | 0.4 | n |  | TRUE
47 | bus_LV_4261-3_0_4_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_4261-3_0_4_node_61 | 0.4 | n |  | TRUE
49 | bus_LV_4261-3_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_4261-3_0_4_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_4261-3_0_4_node_42 | 0.4 | n |  | TRUE
52 | bus_LV_4261-3_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_4261-3_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_4261-3_0_4_node_64 | 0.4 | n |  | TRUE
55 | bus_LV_4261-3_0_4_node_62 | 0.4 | n |  | TRUE
56 | bus_LV_4261-3_0_4_node_105 | 0.4 | n |  | TRUE
57 | bus_LV_4261-3_0_4_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_4261-3_0_4_node_45 | 0.4 | n |  | TRUE
59 | bus_LV_4261-3_0_4_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_4261-3_0_4_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_4261-3_0_4_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_4261-3_0_4_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_4261-3_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_4261-3_0_4_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_4261-3_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_4261-3_0_4_node_114 | 0.4 | n |  | TRUE
67 | bus_LV_4261-3_0_4_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_4261-3_0_4_node_100 | 0.4 | n |  | TRUE
69 | bus_LV_4261-3_0_4_node_112 | 0.4 | n |  | TRUE
70 | bus_LV_4261-3_0_4_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_4261-3_0_4_node_104 | 0.4 | n |  | TRUE
72 | bus_LV_4261-3_0_4_node_80 | 0.4 | n |  | TRUE
73 | bus_LV_4261-3_0_4_node_81 | 0.4 | n |  | TRUE
74 | bus_LV_4261-3_0_4_node_181 | 0.4 | n |  | TRUE
75 | bus_LV_4261-3_0_4_node_77 | 0.4 | n |  | TRUE
76 | bus_LV_4261-3_0_4_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_4261-3_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_4261-3_0_4_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_4261-3_0_4_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_4261-3_0_4_node_86 | 0.4 | n |  | TRUE
81 | bus_LV_4261-3_0_4_node_78 | 0.4 | n |  | TRUE
82 | bus_LV_4261-3_0_4_node_88 | 0.4 | n |  | TRUE
83 | bus_LV_4261-3_0_4_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_4261-3_0_4_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_4261-3_0_4_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_4261-3_0_4_node_75 | 0.4 | n |  | TRUE
87 | bus_LV_4261-3_0_4_node_74 | 0.4 | n |  | TRUE
88 | bus_LV_4261-3_0_4_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_4261-3_0_4_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_4261-3_0_4_node_82 | 0.4 | n |  | TRUE
91 | bus_LV_4261-3_0_4_node_90 | 0.4 | n |  | TRUE
92 | bus_LV_4261-3_0_4_node_92 | 0.4 | n |  | TRUE
93 | bus_LV_4261-3_0_4_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_4261-3_0_4_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_4261-3_0_4_node_93 | 0.4 | n |  | TRUE
96 | bus_LV_4261-3_0_4_node_116 | 0.4 | n |  | TRUE
97 | bus_LV_4261-3_0_4_node_91 | 0.4 | n |  | TRUE
98 | bus_LV_4261-3_0_4_node_117 | 0.4 | n |  | TRUE
99 | bus_LV_4261-3_0_4_node_94 | 0.4 | n |  | TRUE
100 | bus_LV_4261-3_0_4_node_95 | 0.4 | n |  | TRUE
101 | bus_LV_4261-3_0_4_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_4261-3_0_4_node_97 | 0.4 | n |  | TRUE
103 | bus_LV_4261-3_0_4_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_4261-3_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_4261-3_0_4_node_103 | 0.4 | n |  | TRUE
106 | bus_LV_4261-3_0_4_node_106 | 0.4 | n |  | TRUE
107 | bus_LV_4261-3_0_4_node_177 | 0.4 | n |  | TRUE
108 | bus_LV_4261-3_0_4_node_109 | 0.4 | n |  | TRUE
109 | bus_LV_4261-3_0_4_node_143 | 0.4 | n |  | TRUE
110 | bus_LV_4261-3_0_4_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_4261-3_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_4261-3_0_4_node_115 | 0.4 | n |  | TRUE
113 | bus_LV_4261-3_0_4_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_4261-3_0_4_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_4261-3_0_4_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_4261-3_0_4_node_110 | 0.4 | n |  | TRUE
117 | bus_LV_4261-3_0_4_node_125 | 0.4 | n |  | TRUE
118 | bus_LV_4261-3_0_4_node_126 | 0.4 | n |  | TRUE
119 | bus_LV_4261-3_0_4_node_144 | 0.4 | n |  | TRUE
120 | bus_LV_4261-3_0_4_node_145 | 0.4 | n |  | TRUE
121 | bus_LV_4261-3_0_4_node_124 | 0.4 | n |  | TRUE
122 | bus_LV_4261-3_0_4_node_175 | 0.4 | n |  | TRUE
123 | bus_LV_4261-3_0_4_node_139 | 0.4 | n |  | TRUE
124 | bus_LV_4261-3_0_4_node_138 | 0.4 | n |  | TRUE
125 | bus_LV_4261-3_0_4_node_118 | 0.4 | n |  | TRUE
126 | bus_LV_4261-3_0_4_node_119 | 0.4 | n |  | TRUE
127 | bus_LV_4261-3_0_4_node_121 | 0.4 | n |  | TRUE
128 | bus_LV_4261-3_0_4_node_131 | 0.4 | n |  | TRUE
129 | bus_LV_4261-3_0_4_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_4261-3_0_4_node_122 | 0.4 | n |  | TRUE
131 | bus_LV_4261-3_0_4_node_123 | 0.4 | n |  | TRUE
132 | bus_LV_4261-3_0_4_node_127 | 0.4 | n |  | TRUE
133 | bus_LV_4261-3_0_4_node_128 | 0.4 | n |  | TRUE
134 | bus_LV_4261-3_0_4_node_167 | 0.4 | n |  | TRUE
135 | bus_LV_4261-3_0_4_node_130 | 0.4 | n |  | TRUE
136 | bus_LV_4261-3_0_4_node_129 | 0.4 | n |  | TRUE
137 | bus_LV_4261-3_0_4_node_178 | 0.4 | n |  | TRUE
138 | bus_LV_4261-3_0_4_node_158 | 0.4 | n |  | TRUE
139 | bus_LV_4261-3_0_4_node_132 | 0.4 | n |  | TRUE
140 | bus_LV_4261-3_0_4_node_133 | 0.4 | n |  | TRUE
141 | bus_LV_4261-3_0_4_node_134 | 0.4 | n |  | TRUE
142 | bus_LV_4261-3_0_4_node_135 | 0.4 | n |  | TRUE
143 | bus_LV_4261-3_0_4_node_136 | 0.4 | n |  | TRUE
144 | bus_LV_4261-3_0_4_node_137 | 0.4 | n |  | TRUE
145 | bus_LV_4261-3_0_4_node_161 | 0.4 | n |  | TRUE
146 | bus_LV_4261-3_0_4_node_159 | 0.4 | n |  | TRUE
147 | bus_LV_4261-3_0_4_node_160 | 0.4 | n |  | TRUE
148 | bus_LV_4261-3_0_4_node_140 | 0.4 | n |  | TRUE
149 | bus_LV_4261-3_0_4_node_141 | 0.4 | n |  | TRUE
150 | bus_LV_4261-3_0_4_node_142 | 0.4 | n |  | TRUE
151 | bus_LV_4261-3_0_4_node_168 | 0.4 | n |  | TRUE
152 | bus_LV_4261-3_0_4_node_176 | 0.4 | n |  | TRUE
153 | bus_LV_4261-3_0_4_node_169 | 0.4 | n |  | TRUE
154 | bus_LV_4261-3_0_4_node_171 | 0.4 | n |  | TRUE
155 | bus_LV_4261-3_0_4_node_165 | 0.4 | n |  | TRUE
156 | bus_LV_4261-3_0_4_node_166 | 0.4 | n |  | TRUE
157 | bus_LV_4261-3_0_4_node_146 | 0.4 | n |  | TRUE
158 | bus_LV_4261-3_0_4_node_147 | 0.4 | n |  | TRUE
159 | bus_LV_4261-3_0_4_node_148 | 0.4 | n |  | TRUE
160 | bus_LV_4261-3_0_4_node_149 | 0.4 | n |  | TRUE
161 | bus_LV_4261-3_0_4_node_162 | 0.4 | n |  | TRUE
162 | bus_LV_4261-3_0_4_node_170 | 0.4 | n |  | TRUE
163 | bus_LV_4261-3_0_4_node_163 | 0.4 | n |  | TRUE
164 | bus_LV_4261-3_0_4_node_152 | 0.4 | n |  | TRUE
165 | bus_LV_4261-3_0_4_node_153 | 0.4 | n |  | TRUE
166 | bus_LV_4261-3_0_4_node_154 | 0.4 | n |  | TRUE
167 | bus_LV_4261-3_0_4_node_155 | 0.4 | n |  | TRUE
168 | bus_LV_4261-3_0_4_node_156 | 0.4 | n |  | TRUE
169 | bus_LV_4261-3_0_4_node_157 | 0.4 | n |  | TRUE
170 | bus_LV_4261-3_0_4_node_164 | 0.4 | n |  | TRUE
171 | bus_LV_4261-3_0_4_node_172 | 0.4 | n |  | TRUE
172 | bus_LV_4261-3_0_4_node_173 | 0.4 | n |  | TRUE
173 | bus_LV_4261-3_0_4_node_174 | 0.4 | n |  | TRUE
174 | bus_LV_4261-3_0_4_node_179 | 0.4 | n |  | TRUE
175 | bus_MV_298_0_node_127 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4261-3_0_4_load_0 | 0 | 0.0035449 | 0.00088844 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4261-3_0_4_load_1 | 1 | 0.001746 | 0.00043758 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4261-3_0_4_load_2 | 2 | 0.0014285 | 0.00035801 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4261-3_0_4_load_4 | 4 | 0.00095123 | 0.0002384 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4261-3_0_4_load_5 | 5 | 0.0024452 | 0.00061283 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4261-3_0_4_load_6 | 6 | 0.00099865 | 0.00025028 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4261-3_0_4_load_11 | 7 | 0.0027553 | 0.00069053 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4261-3_0_4_load_17 | 8 | 0.0068048 | 0.0017054 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4261-3_0_4_load_27 | 9 | 0.00091276 | 0.00022876 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4261-3_0_4_load_12 | 10 | 0.0021354 | 0.00053519 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4261-3_0_4_load_25 | 11 | 0.00089751 | 0.00022494 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4261-3_0_4_load_7 | 12 | 0.0029239 | 0.00073279 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4261-3_0_4_load_8 | 13 | 0.0050352 | 0.0012619 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4261-3_0_4_load_9 | 14 | 0.008126 | 0.0020366 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4261-3_0_4_load_10 | 15 | 0.0043352 | 0.0010865 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4261-3_0_4_load_14 | 16 | 0.0036882 | 0.00092435 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4261-3_0_4_load_15 | 17 | 0.0059109 | 0.0014814 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4261-3_0_4_load_16 | 18 | 0.0032806 | 0.00082219 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4261-3_0_4_load_36 | 19 | 0.0042986 | 0.0010773 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4261-3_0_4_load_31 | 20 | 0.0024097 | 0.00060394 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4261-3_0_4_load_18 | 21 | 0.0026037 | 0.00065255 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4261-3_0_4_load_20 | 23 | 0.0025033 | 0.00062737 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4261-3_0_4_load_21 | 24 | 0.0021852 | 0.00054766 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4261-3_0_4_load_22 | 25 | 0.0011861 | 0.00029728 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4261-3_0_4_load_33 | 26 | 0.0016373 | 0.00041035 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4261-3_0_4_load_67 | 27 | 0.0016801 | 0.00042107 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4261-3_0_4_load_34 | 28 | 0.0020565 | 0.00051541 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4261-3_0_4_load_66 | 29 | 0.0023148 | 0.00058015 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4261-3_0_4_load_23 | 30 | 0.0018041 | 0.00045214 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4261-3_0_4_load_24 | 31 | 0.0011198 | 0.00028066 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4261-3_0_4_load_26 | 32 | 0.0019165 | 0.00048031 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4261-3_0_4_load_52 | 33 | 0.002664 | 0.00066767 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4261-3_0_4_load_28 | 35 | 0.0035004 | 0.00087728 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4261-3_0_4_load_29 | 36 | 0.0039357 | 0.00098639 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4261-3_0_4_load_30 | 37 | 0.0018099 | 0.00045359 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4261-3_0_4_load_68 | 39 | 0.0011078 | 0.00027763 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4261-3_0_4_load_89 | 40 | 0.0015729 | 0.00039422 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4261-3_0_4_load_35 | 41 | 0.0016361 | 0.00041005 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4261-3_0_4_load_38 | 43 | 0.0016368 | 0.00041022 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4261-3_0_4_load_39 | 44 | 0.0013463 | 0.00033742 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4261-3_0_4_load_53 | 45 | 0.0042856 | 0.0010741 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4261-3_0_4_load_60 | 46 | 0.00071237 | 0.00017854 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4261-3_0_4_load_54 | 47 | 0.005212 | 0.0013062 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4261-3_0_4_load_61 | 48 | 0.0025982 | 0.00065118 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4261-3_0_4_load_40 | 49 | 0.00913 | 0.0022882 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4261-3_0_4_load_41 | 50 | 0.0046 | 0.0011529 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4261-3_0_4_load_42 | 51 | 0.0025804 | 0.0006467 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4261-3_0_4_load_62 | 55 | 0.0019259 | 0.00048267 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4261-3_0_4_load_105 | 56 | 0.0015228 | 0.00038166 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4261-3_0_4_load_45 | 58 | 0.0051517 | 0.0012911 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4261-3_0_4_load_48 | 61 | 0.0011102 | 0.00027824 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4261-3_0_4_load_49 | 62 | 0.001972 | 0.00049423 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4261-3_0_4_load_59 | 64 | 0.0016799 | 0.00042102 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4261-3_0_4_load_55 | 65 | 0.0026851 | 0.00067296 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4261-3_0_4_load_114 | 66 | 0.0033519 | 0.00084007 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4261-3_0_4_load_100 | 68 | 0.0013708 | 0.00034355 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4261-3_0_4_load_112 | 69 | 0.0064446 | 0.0016152 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4261-3_0_4_load_56 | 70 | 0.0019753 | 0.00049506 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4261-3_0_4_load_104 | 71 | 0.005095 | 0.0012769 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4261-3_0_4_load_80 | 72 | 0.002746 | 0.00068821 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4261-3_0_4_load_81 | 73 | 0.0021194 | 0.00053118 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4261-3_0_4_load_181 | 74 | 0.0018214 | 0.0004565 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4261-3_0_4_load_77 | 75 | 0.0046779 | 0.0011724 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4261-3_0_4_load_69 | 76 | 0.0026744 | 0.00067026 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4261-3_0_4_load_70 | 77 | 0.0064205 | 0.0016091 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4261-3_0_4_load_79 | 79 | 0.0012111 | 0.00030354 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4261-3_0_4_load_78 | 81 | 0.0010013 | 0.00025095 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4261-3_0_4_load_88 | 82 | 0.0041039 | 0.0010285 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4261-3_0_4_load_84 | 83 | 0.001094 | 0.00027418 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4261-3_0_4_load_72 | 84 | 0.0022773 | 0.00057075 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4261-3_0_4_load_73 | 85 | 0.00063449 | 0.00015902 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4261-3_0_4_load_75 | 86 | 0.0010028 | 0.00025132 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4261-3_0_4_load_76 | 88 | 0.0022797 | 0.00057135 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4261-3_0_4_load_83 | 89 | 0.0018406 | 0.0004613 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4261-3_0_4_load_90 | 91 | 0.0027162 | 0.00068074 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4261-3_0_4_load_92 | 92 | 0.0027834 | 0.0006976 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4261-3_0_4_load_85 | 93 | 0.0047557 | 0.0011919 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4261-3_0_4_load_87 | 94 | 0.0015188 | 0.00038065 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4261-3_0_4_load_116 | 96 | 0.0051598 | 0.0012932 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4261-3_0_4_load_91 | 97 | 0.0028181 | 0.00070628 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4261-3_0_4_load_117 | 98 | 0.0055482 | 0.0013905 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4261-3_0_4_load_94 | 99 | 0.0076811 | 0.0019251 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4261-3_0_4_load_95 | 100 | 0.0018108 | 0.00045383 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4261-3_0_4_load_97 | 102 | 0.0056154 | 0.0014074 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4261-3_0_4_load_103 | 105 | 0.001682 | 0.00042155 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4261-3_0_4_load_106 | 106 | 0.0012156 | 0.00030467 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4261-3_0_4_load_177 | 107 | 0.0093192 | 0.0023356 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4261-3_0_4_load_109 | 108 | 0.010114 | 0.0025348 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4261-3_0_4_load_107 | 110 | 0.00089396 | 0.00022405 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4261-3_0_4_load_102 | 113 | 0.0042868 | 0.0010744 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4261-3_0_4_load_111 | 114 | 0.0059475 | 0.0014906 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4261-3_0_4_load_108 | 115 | 0.0089307 | 0.0022382 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4261-3_0_4_load_125 | 117 | 0.0012618 | 0.00031623 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4261-3_0_4_load_126 | 118 | 0.013042 | 0.0032686 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4261-3_0_4_load_145 | 120 | 0.007329 | 0.0018368 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4261-3_0_4_load_175 | 122 | 0.00089462 | 0.00022421 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4261-3_0_4_load_139 | 123 | 0.0028282 | 0.00070882 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4261-3_0_4_load_138 | 124 | 0.0049011 | 0.0012283 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4261-3_0_4_load_118 | 125 | 0.0039637 | 0.00099341 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4261-3_0_4_load_121 | 127 | 0.010117 | 0.0025356 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4261-3_0_4_load_131 | 128 | 0.0022081 | 0.00055339 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4261-3_0_4_load_120 | 129 | 0.004716 | 0.0011819 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4261-3_0_4_load_123 | 131 | 0.0021712 | 0.00054416 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4261-3_0_4_load_127 | 132 | 0.0014047 | 0.00035206 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4261-3_0_4_load_130 | 135 | 0.0016368 | 0.00041022 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4261-3_0_4_load_129 | 136 | 0.0015226 | 0.0003816 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4261-3_0_4_load_178 | 137 | 0.0011363 | 0.00028479 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4261-3_0_4_load_158 | 138 | 0.0011368 | 0.00028492 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4261-3_0_4_load_132 | 139 | 0.0047534 | 0.0011913 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4261-3_0_4_load_133 | 140 | 0.003424 | 0.00085813 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4261-3_0_4_load_136 | 143 | 0.0051886 | 0.0013004 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4261-3_0_4_load_161 | 145 | 0.012183 | 0.0030533 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4261-3_0_4_load_159 | 146 | 0.00707 | 0.0017719 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4261-3_0_4_load_160 | 147 | 0.0012905 | 0.00032343 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4261-3_0_4_load_141 | 149 | 0.0044988 | 0.0011275 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4261-3_0_4_load_142 | 150 | 0.0066478 | 0.0016661 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4261-3_0_4_load_168 | 151 | 0.003882 | 0.00097291 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4261-3_0_4_load_176 | 152 | 0.006137 | 0.0015381 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4261-3_0_4_load_169 | 153 | 0.0086597 | 0.0021703 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4261-3_0_4_load_171 | 154 | 0.0016669 | 0.00041776 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4261-3_0_4_load_165 | 155 | 0.007127 | 0.0017862 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4261-3_0_4_load_166 | 156 | 0.001539 | 0.0003857 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4261-3_0_4_load_146 | 157 | 0.0076571 | 0.001919 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4261-3_0_4_load_148 | 159 | 0.00061905 | 0.00015515 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4261-3_0_4_load_149 | 160 | 0.0014208 | 0.00035609 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4261-3_0_4_load_162 | 161 | 0.0018322 | 0.00045919 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4261-3_0_4_load_170 | 162 | 0.0030497 | 0.00076434 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4261-3_0_4_load_163 | 163 | 0.0033142 | 0.00083061 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4261-3_0_4_load_152 | 164 | 0.0053355 | 0.0013372 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4261-3_0_4_load_153 | 165 | 0.0019336 | 0.00048461 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4261-3_0_4_load_154 | 166 | 0.0015396 | 0.00038586 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4261-3_0_4_load_155 | 167 | 0.0014823 | 0.00037149 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4261-3_0_4_load_156 | 168 | 0.0041628 | 0.0010433 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4261-3_0_4_load_157 | 169 | 0.0037789 | 0.00094707 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4261-3_0_4_load_164 | 170 | 0.0038928 | 0.00097564 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4261-3_0_4_load_172 | 171 | 0.00052904 | 0.00013259 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4261-3_0_4_load_173 | 172 | 0.001136 | 0.0002847 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4261-3_0_4_load_174 | 173 | 0.0013273 | 0.00033266 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4261-3_0_4_load_179 | 174 | 0.0012779 | 0.00032028 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4261-3_0_4_line_0 |  | 0 | 1 | 0.0041287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4261-3_0_4_line_1 |  | 0 | 2 | 0.0082026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4261-3_0_4_line_2 |  | 1 | 3 | 0.027947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4261-3_0_4_line_3 |  | 2 | 4 | 0.010541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4261-3_0_4_line_4 |  | 3 | 5 | 0.016733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4261-3_0_4_line_5 |  | 3 | 6 | 0.02031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4261-3_0_4_line_6 |  | 4 | 7 | 0.002722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4261-3_0_4_line_7 |  | 5 | 8 | 0.019821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4261-3_0_4_line_8 |  | 6 | 9 | 0.0025252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4261-3_0_4_line_9 |  | 7 | 10 | 0.027204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4261-3_0_4_line_10 |  | 9 | 11 | 0.0083834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4261-3_0_4_line_11 |  | 11 | 30 | 0.017441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4261-3_0_4_line_12 |  | 12 | 13 | 0.01901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4261-3_0_4_line_13 |  | 12 | 14 | 0.011332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4261-3_0_4_line_14 |  | 13 | 15 | 0.0038828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4261-3_0_4_line_15 |  | 15 | 16 | 0.026957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4261-3_0_4_line_16 |  | 16 | 17 | 0.011758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_4261-3_0_4_line_17 |  | 17 | 18 | 0.0088717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_4261-3_0_4_line_18 |  | 18 | 19 | 0.0019303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_4261-3_0_4_line_19 |  | 19 | 20 | 0.00044482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_4261-3_0_4_line_20 |  | 20 | 36 | 0.0060084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_4261-3_0_4_line_21 |  | 21 | 22 | 0.014465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_4261-3_0_4_line_22 |  | 21 | 23 | 0.01193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4261-3_0_4_line_23 |  | 22 | 24 | 0.010713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_4261-3_0_4_line_24 |  | 22 | 25 | 0.0088752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_4261-3_0_4_line_25 |  | 24 | 26 | 0.023402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_4261-3_0_4_line_26 |  | 25 | 27 | 0.016379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_4261-3_0_4_line_27 |  | 26 | 28 | 0.00045839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_4261-3_0_4_line_28 |  | 27 | 29 | 0.0096857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_4261-3_0_4_line_29 |  | 28 | 41 | 0.014147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_4261-3_0_4_line_30 |  | 29 | 38 | 0.014272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_4261-3_0_4_line_31 |  | 30 | 31 | 0.034895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4261-3_0_4_line_32 |  | 31 | 32 | 0.0052811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4261-3_0_4_line_33 |  | 32 | 33 | 0.0262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4261-3_0_4_line_34 |  | 33 | 34 | 0.015374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4261-3_0_4_line_35 |  | 34 | 55 | 0.01435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4261-3_0_4_line_36 |  | 35 | 36 | 0.013232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_4261-3_0_4_line_37 |  | 35 | 37 | 0.019042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_4261-3_0_4_line_38 |  | 37 | 38 | 0.0069414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_4261-3_0_4_line_39 |  | 38 | 39 | 0.014188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_4261-3_0_4_line_40 |  | 39 | 40 | 0.021124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_4261-3_0_4_line_41 |  | 40 | 75 | 0.004893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_4261-3_0_4_line_42 |  | 41 | 42 | 0.025941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_4261-3_0_4_line_43 |  | 42 | 43 | 0.013277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_4261-3_0_4_line_44 |  | 42 | 44 | 0.0084845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_4261-3_0_4_line_45 |  | 43 | 45 | 0.0041187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_4261-3_0_4_line_46 |  | 44 | 46 | 0.0089963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_4261-3_0_4_line_47 |  | 45 | 47 | 0.0097113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_4261-3_0_4_line_48 |  | 46 | 48 | 0.0041243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_4261-3_0_4_line_49 |  | 49 | 50 | 0.026407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_4261-3_0_4_line_50 |  | 49 | 51 | 0.01718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_4261-3_0_4_line_51 |  | 50 | 52 | 0.029526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_4261-3_0_4_line_52 |  | 51 | 53 | 0.0065311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_4261-3_0_4_line_53 |  | 53 | 54 | 0.008215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_4261-3_0_4_line_54 |  | 53 | 55 | 0.018672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4261-3_0_4_line_55 |  | 54 | 56 | 0.018912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_4261-3_0_4_line_56 |  | 54 | 57 | 0.021587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_4261-3_0_4_line_57 |  | 56 | 71 | 0.014978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_4261-3_0_4_line_58 |  | 57 | 66 | 0.0041936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_4261-3_0_4_line_59 |  | 57 | 60 | 0.039861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_4261-3_0_4_line_60 |  | 58 | 59 | 0.016957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_4261-3_0_4_line_61 |  | 58 | 60 | 0.030394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_4261-3_0_4_line_62 |  | 59 | 61 | 0.007354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4261-3_0_4_line_63 |  | 59 | 62 | 0.010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_4261-3_0_4_line_64 |  | 60 | 63 | 0.02183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_4261-3_0_4_line_65 |  | 62 | 64 | 0.027964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_4261-3_0_4_line_66 |  | 63 | 65 | 0.021385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_4261-3_0_4_line_67 |  | 64 | 67 | 0.0046166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4261-3_0_4_line_68 |  | 65 | 68 | 0.011511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4261-3_0_4_line_69 |  | 66 | 69 | 0.022094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_4261-3_0_4_line_70 |  | 67 | 70 | 0.0084866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4261-3_0_4_line_71 |  | 69 | 114 | 0.015986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_4261-3_0_4_line_72 |  | 71 | 105 | 0.024282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_4261-3_0_4_line_73 |  | 72 | 73 | 0.039067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_4261-3_0_4_line_74 |  | 72 | 74 | 0.028215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_4261-3_0_4_line_75 |  | 73 | 90 | 0.021562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_4261-3_0_4_line_76 |  | 75 | 87 | 0.013026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_4261-3_0_4_line_77 |  | 76 | 77 | 0.0089598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_4261-3_0_4_line_78 |  | 77 | 78 | 0.021081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_4261-3_0_4_line_79 |  | 78 | 79 | 0.011881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_4261-3_0_4_line_80 |  | 78 | 80 | 0.017611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_4261-3_0_4_line_81 |  | 79 | 81 | 0.011928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_4261-3_0_4_line_82 |  | 80 | 82 | 0.0125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_4261-3_0_4_line_83 |  | 80 | 83 | 0.022029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_4261-3_0_4_line_84 |  | 81 | 88 | 0.0037371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_4261-3_0_4_line_85 |  | 82 | 96 | 0.019459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_4261-3_0_4_line_86 |  | 83 | 93 | 0.010138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_4261-3_0_4_line_87 |  | 84 | 85 | 0.0055817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_4261-3_0_4_line_88 |  | 85 | 86 | 0.01616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_4261-3_0_4_line_89 |  | 86 | 89 | 0.013016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_4261-3_0_4_line_90 |  | 87 | 88 | 0.016237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_4261-3_0_4_line_91 |  | 89 | 90 | 0.0070333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_4261-3_0_4_line_92 |  | 90 | 91 | 0.016665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_4261-3_0_4_line_93 |  | 91 | 92 | 0.0059355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_4261-3_0_4_line_94 |  | 92 | 97 | 0.021355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_4261-3_0_4_line_95 |  | 93 | 94 | 0.029456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_4261-3_0_4_line_96 |  | 94 | 95 | 0.025345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_4261-3_0_4_line_97 |  | 95 | 97 | 0.013055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_4261-3_0_4_line_98 |  | 96 | 98 | 0.011845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_4261-3_0_4_line_99 |  | 98 | 125 | 0.0087331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_4261-3_0_4_line_100 |  | 99 | 100 | 0.0067323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_4261-3_0_4_line_101 |  | 99 | 101 | 0.014442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_4261-3_0_4_line_102 |  | 100 | 102 | 0.0094883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_4261-3_0_4_line_103 |  | 101 | 103 | 0.009068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_4261-3_0_4_line_104 |  | 101 | 104 | 0.022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_4261-3_0_4_line_105 |  | 102 | 105 | 0.017178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_4261-3_0_4_line_106 |  | 103 | 106 | 0.022838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_4261-3_0_4_line_107 |  | 104 | 107 | 0.0089483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_4261-3_0_4_line_108 |  | 106 | 110 | 0.0092795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_4261-3_0_4_line_109 |  | 108 | 109 | 0.010424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_4261-3_0_4_line_110 |  | 109 | 119 | 0.009408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_4261-3_0_4_line_111 |  | 109 | 120 | 0.017272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
112 | LV_4261-3_0_4_line_112 |  | 110 | 115 | 0.038774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
113 | LV_4261-3_0_4_line_113 |  | 111 | 112 | 0.014273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
114 | LV_4261-3_0_4_line_114 |  | 111 | 113 | 0.022286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
115 | LV_4261-3_0_4_line_115 |  | 111 | 114 | 0.016301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
116 | LV_4261-3_0_4_line_116 |  | 112 | 123 | 0.0121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_4261-3_0_4_line_117 |  | 115 | 116 | 0.0026357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_4261-3_0_4_line_118 |  | 116 | 117 | 0.04388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_4261-3_0_4_line_119 |  | 116 | 118 | 0.018261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_4261-3_0_4_line_120 |  | 117 | 121 | 0.015384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_4261-3_0_4_line_121 |  | 118 | 122 | 0.0020541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_4261-3_0_4_line_122 |  | 119 | 144 | 0.012644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_4261-3_0_4_line_123 |  | 120 | 153 | 0.0093599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_4261-3_0_4_line_124 |  | 121 | 128 | 0.011274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_4261-3_0_4_line_125 |  | 121 | 126 | 0.02035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_4261-3_0_4_line_126 |  | 122 | 134 | 0.024945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_4261-3_0_4_line_127 |  | 123 | 124 | 0.017095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_4261-3_0_4_line_128 |  | 124 | 148 | 0.013271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_4261-3_0_4_line_129 |  | 125 | 126 | 0.017924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_4261-3_0_4_line_130 |  | 126 | 127 | 0.01451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_4261-3_0_4_line_131 |  | 127 | 129 | 0.022892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_4261-3_0_4_line_132 |  | 129 | 130 | 0.014656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_4261-3_0_4_line_133 |  | 130 | 131 | 0.012546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_4261-3_0_4_line_134 |  | 131 | 132 | 0.025878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_4261-3_0_4_line_135 |  | 132 | 133 | 0.0048714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
136 | LV_4261-3_0_4_line_136 |  | 133 | 135 | 0.016509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_4261-3_0_4_line_137 |  | 133 | 136 | 0.024047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
138 | LV_4261-3_0_4_line_138 |  | 134 | 171 | 0.011443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_4261-3_0_4_line_139 |  | 134 | 156 | 0.0064978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_4261-3_0_4_line_140 |  | 135 | 137 | 0.0068345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_4261-3_0_4_line_141 |  | 137 | 138 | 0.0066975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_4261-3_0_4_line_142 |  | 138 | 169 | 0.008257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
143 | LV_4261-3_0_4_line_143 |  | 139 | 140 | 0.010897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_4261-3_0_4_line_144 |  | 139 | 141 | 0.00466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
145 | LV_4261-3_0_4_line_145 |  | 140 | 142 | 0.021261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_4261-3_0_4_line_146 |  | 141 | 143 | 0.016225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
147 | LV_4261-3_0_4_line_147 |  | 141 | 144 | 0.025651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
148 | LV_4261-3_0_4_line_148 |  | 142 | 145 | 0.024391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
149 | LV_4261-3_0_4_line_149 |  | 142 | 146 | 0.0034093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_4261-3_0_4_line_150 |  | 146 | 147 | 0.0083038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
151 | LV_4261-3_0_4_line_151 |  | 148 | 149 | 0.012997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
152 | LV_4261-3_0_4_line_152 |  | 148 | 150 | 0.01244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
153 | LV_4261-3_0_4_line_153 |  | 149 | 151 | 0.022653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_4261-3_0_4_line_154 |  | 150 | 152 | 0.00083572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_4261-3_0_4_line_155 |  | 151 | 153 | 0.016285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
156 | LV_4261-3_0_4_line_156 |  | 152 | 154 | 0.02094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
157 | LV_4261-3_0_4_line_157 |  | 154 | 170 | 0.0024986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
158 | LV_4261-3_0_4_line_158 |  | 155 | 156 | 0.026802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
159 | LV_4261-3_0_4_line_159 |  | 157 | 158 | 0.035357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
160 | LV_4261-3_0_4_line_160 |  | 158 | 159 | 0.042421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
161 | LV_4261-3_0_4_line_161 |  | 158 | 160 | 0.038258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
162 | LV_4261-3_0_4_line_162 |  | 159 | 161 | 0.013918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
163 | LV_4261-3_0_4_line_163 |  | 160 | 162 | 0.020666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
164 | LV_4261-3_0_4_line_164 |  | 161 | 163 | 0.020319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
165 | LV_4261-3_0_4_line_165 |  | 163 | 170 | 0.0066551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
166 | LV_4261-3_0_4_line_166 |  | 164 | 165 | 0.026663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
167 | LV_4261-3_0_4_line_167 |  | 164 | 166 | 0.00068449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_4261-3_0_4_line_168 |  | 165 | 167 | 0.005364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
169 | LV_4261-3_0_4_line_169 |  | 166 | 168 | 0.028283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
170 | LV_4261-3_0_4_line_170 |  | 167 | 169 | 0.010604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
171 | LV_4261-3_0_4_line_171 |  | 171 | 172 | 0.0056789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
172 | LV_4261-3_0_4_line_172 |  | 172 | 173 | 0.017697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
173 | LV_4261-3_0_4_line_173 |  | 173 | 174 | 0.0024435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4261-3_0_4_trafo_43 | 0.63 MVA 20/0.4 kV | 175 | 52 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2635233.6576 | 1267268.7085 | 2635232.0079 | 1267272.4933
1 | 2635233.6576 | 1267268.7085 | 2635236.9353 | 1267261.1892
2 | 2635223.2079 | 1267298.9797 | 2635229.2824 | 1267278.7459 | 2635232.0079 | 1267272.4933
3 | 2635241.1471 | 1267251.5266 | 2635236.9353 | 1267261.1892
4 | 2635223.2079 | 1267298.9797 | 2635208.265 | 1267291.4489
5 | 2635223.2079 | 1267298.9797 | 2635217.2677 | 1267318.4016
6 | 2635242.3296 | 1267249.0773 | 2635241.7063 | 1267250.2439 | 2635241.1471 | 1267251.5266
7 | 2635208.265 | 1267291.4489 | 2635196.3268 | 1267285.4323 | 2635193.1381 | 1267291.0418
8 | 2635217.2677 | 1267318.4016 | 2635216.6292 | 1267320.4893 | 2635216.5194 | 1267320.8133
9 | 2635242.3296 | 1267249.0773 | 2635255.1491 | 1267225.0838 | 2635255.1491 | 1267225.0838
10 | 2635216.5194 | 1267320.8133 | 2635213.8292 | 1267328.7533
11 | 2635208.2326 | 1267345.2717 | 2635213.8292 | 1267328.7533
12 | 2635070.3129 | 1267196.6947 | 2635059.9157 | 1267212.609
13 | 2635070.3129 | 1267196.6947 | 2635076.5109 | 1267187.2079
14 | 2635059.9157 | 1267212.609 | 2635057.792 | 1267215.8596
15 | 2635057.792 | 1267215.8596 | 2635043.048 | 1267238.4273
16 | 2635036.617 | 1267248.2709 | 2635043.048 | 1267238.4273
17 | 2635036.617 | 1267248.2709 | 2635036.43 | 1267248.5571 | 2635031.6332 | 1267255.6104
18 | 2635031.6332 | 1267255.6104 | 2635030.5476 | 1267257.2065
19 | 2635030.5476 | 1267257.2065 | 2635030.2975 | 1267257.5744
20 | 2635030.2975 | 1267257.5744 | 2635026.9186 | 1267262.5426
21 | 2634961.7755 | 1267271.6209 | 2634968.2869 | 1267258.7046
22 | 2634973.6571 | 1267248.052 | 2634968.2869 | 1267258.7046
23 | 2634961.7755 | 1267271.6209 | 2634952.1979 | 1267266.821
24 | 2634961.7755 | 1267271.6209 | 2634967.2121 | 1267276.3564 | 2634968.705 | 1267277.0944
25 | 2634931.2764 | 1267256.3361 | 2634952.1979 | 1267266.821
26 | 2634968.705 | 1267277.0944 | 2634983.3882 | 1267284.353
27 | 2634931.2764 | 1267256.3361 | 2634930.8666 | 1267256.1307
28 | 2634992.0709 | 1267288.6453 | 2634983.3882 | 1267284.353
29 | 2634918.219 | 1267249.7924 | 2634930.8666 | 1267256.1307
30 | 2635004.8652 | 1267294.9701 | 2634992.0709 | 1267288.6453
31 | 2635208.2326 | 1267345.2717 | 2635207.1134 | 1267348.575 | 2635193.9491 | 1267377.0901
32 | 2635193.9491 | 1267377.0901 | 2635191.7356 | 1267381.8849
33 | 2635180.7539 | 1267405.6722 | 2635191.7356 | 1267381.8849
34 | 2635174.3098 | 1267419.6308 | 2635180.7539 | 1267405.6722
35 | 2635174.3098 | 1267419.6308 | 2635167.989 | 1267432.5137
36 | 2635019.4774 | 1267273.4842 | 2635026.9186 | 1267262.5426
37 | 2635008.7687 | 1267289.2303 | 2635019.4774 | 1267273.4842
38 | 2635004.8652 | 1267294.9701 | 2635008.7687 | 1267289.2303
39 | 2635004.8652 | 1267294.9701 | 2634999.7452 | 1267308.202
40 | 2634992.1223 | 1267327.9028 | 2634999.7452 | 1267308.202
41 | 2634992.1223 | 1267327.9028 | 2634990.3566 | 1267332.4661
42 | 2634895.0272 | 1267238.1697 | 2634918.219 | 1267249.7924
43 | 2634895.0272 | 1267238.1697 | 2634901.2937 | 1267226.4651
44 | 2634895.0272 | 1267238.1697 | 2634890.4503 | 1267245.3138
45 | 2634901.2937 | 1267226.4651 | 2634903.2377 | 1267222.834
46 | 2634890.4503 | 1267245.3138 | 2634885.5973 | 1267252.8889
47 | 2634907.8214 | 1267214.2725 | 2634903.2377 | 1267222.834
48 | 2634885.5973 | 1267252.8889 | 2634883.3724 | 1267256.3616
49 | 2635139.2927 | 1267437.3206 | 2635126.9621 | 1267430.3794 | 2635115.6027 | 1267425.7748
50 | 2635139.2927 | 1267437.3206 | 2635151.0577 | 1267443.9433 | 2635154.1953 | 1267445.8652
51 | 2635088.2392 | 1267414.6829 | 2635115.6027 | 1267425.7748
52 | 2635159.7647 | 1267449.2767 | 2635154.1953 | 1267445.8652
53 | 2635159.7647 | 1267449.2767 | 2635162.2169 | 1267457.1191
54 | 2635159.7647 | 1267449.2767 | 2635167.989 | 1267432.5137
55 | 2635162.2169 | 1267457.1191 | 2635147.7042 | 1267469.2454
56 | 2635162.2169 | 1267457.1191 | 2635164.6863 | 1267464.628 | 2635169.2765 | 1267471.1377 | 2635173.1881 | 1267475.3306
57 | 2635147.7042 | 1267469.2454 | 2635136.2106 | 1267478.8489
58 | 2635173.1881 | 1267475.3306 | 2635170.5646 | 1267478.6023
59 | 2635173.1881 | 1267475.3306 | 2635199.6795 | 1267445.4779
60 | 2635221.1927 | 1267403.5314 | 2635214.7775 | 1267419.2281
61 | 2635199.6795 | 1267445.4779 | 2635204.2257 | 1267439.156 | 2635211.8359 | 1267426.4255 | 2635214.7775 | 1267419.2281
62 | 2635221.1927 | 1267403.5314 | 2635228.1547 | 1267405.9005
63 | 2635221.1927 | 1267403.5314 | 2635224.1442 | 1267393.5596
64 | 2635199.6795 | 1267445.4779 | 2635219.2055 | 1267455.3567
65 | 2635224.1442 | 1267393.5596 | 2635232.0807 | 1267366.7458
66 | 2635219.2055 | 1267455.3567 | 2635212.4629 | 1267475.6509
67 | 2635233.391 | 1267362.319 | 2635232.0807 | 1267366.7458
68 | 2635209.0823 | 1267486.6513 | 2635210.7366 | 1267480.8468 | 2635212.4629 | 1267475.6509
69 | 2635170.5646 | 1267478.6023 | 2635166.9321 | 1267483.1324 | 2635162.9097 | 1267488.7125 | 2635158.9966 | 1267497.2688
70 | 2635233.391 | 1267362.319 | 2635235.5248 | 1267355.3823 | 2635235.8906 | 1267354.2089
71 | 2635152.1655 | 1267511.7162 | 2635153.69 | 1267508.8721 | 2635158.9966 | 1267497.2688
72 | 2635117.5773 | 1267494.4182 | 2635136.2106 | 1267478.8489
73 | 2634870.5013 | 1267297.3341 | 2634869.5196 | 1267301.7092 | 2634886.0899 | 1267308.7897 | 2634888.7434 | 1267303.0234 | 2634898.0345 | 1267307.2713
74 | 2634870.5013 | 1267297.3341 | 2634866.5806 | 1267325.2754
75 | 2634917.6443 | 1267316.2367 | 2634898.0345 | 1267307.2713
76 | 2634985.656 | 1267344.6142 | 2634990.3566 | 1267332.4661
77 | 2634993.3181 | 1267392.2134 | 2635002.1066 | 1267393.9575
78 | 2634973.0262 | 1267386.5362 | 2634990.4434 | 1267391.6429 | 2634993.3181 | 1267392.2134
79 | 2634973.0262 | 1267386.5362 | 2634976.4535 | 1267375.1601
80 | 2634967.1924 | 1267403.1581 | 2634973.0262 | 1267386.5362
81 | 2634976.4535 | 1267375.1601 | 2634979.8942 | 1267363.7394
82 | 2634967.1924 | 1267403.1581 | 2634962.9608 | 1267414.9197
83 | 2634967.1924 | 1267403.1581 | 2634947.141 | 1267394.0361
84 | 2634980.9722 | 1267360.1612 | 2634979.8942 | 1267363.7394
85 | 2634962.9608 | 1267414.9197 | 2634956.3733 | 1267433.2295
86 | 2634947.141 | 1267394.0361 | 2634937.9127 | 1267389.8379
87 | 2634956.1134 | 1267330.6995 | 2634951.0638 | 1267328.3211
88 | 2634936.4446 | 1267321.4354 | 2634951.0638 | 1267328.3211
89 | 2634936.4446 | 1267321.4354 | 2634924.6691 | 1267315.889
90 | 2634985.656 | 1267344.6142 | 2634980.9722 | 1267360.1612
91 | 2634917.6443 | 1267316.2367 | 2634924.6691 | 1267315.889
92 | 2634917.6443 | 1267316.2367 | 2634913.196 | 1267318.7678 | 2634908.684 | 1267329.3965
93 | 2634908.684 | 1267329.3965 | 2634906.3646 | 1267334.86
94 | 2634898.0199 | 1267354.5171 | 2634906.3646 | 1267334.86
95 | 2634911.1011 | 1267377.6405 | 2634937.9127 | 1267389.8379
96 | 2634890.3839 | 1267364.3103 | 2634894.4146 | 1267370.0493 | 2634911.1011 | 1267377.6405
97 | 2634890.3839 | 1267364.3103 | 2634895.0216 | 1267361.5801 | 2634898.0199 | 1267354.5171
98 | 2634956.3733 | 1267433.2295 | 2634952.3633 | 1267444.375
99 | 2634952.3633 | 1267444.375 | 2634949.4069 | 1267452.5924
100 | 2635094.3612 | 1267518.3534 | 2635095.08 | 1267517.6082 | 2635098.9157 | 1267513.3961
101 | 2635088.8798 | 1267531.2479 | 2635090.4374 | 1267523.7073 | 2635091.422 | 1267521.4004 | 2635094.3612 | 1267518.3534
102 | 2635098.9157 | 1267513.3961 | 2635105.3042 | 1267506.3808
103 | 2635088.8798 | 1267531.2479 | 2635079.8345 | 1267532.195
104 | 2635111.7938 | 1267529.527 | 2635095.259 | 1267530.5519 | 2635088.8798 | 1267531.2479
105 | 2635117.5773 | 1267494.4182 | 2635111.8081 | 1267499.2388 | 2635105.3042 | 1267506.3808
106 | 2635079.8345 | 1267532.195 | 2635067.4622 | 1267530.6539 | 2635057.5631 | 1267527.5631
107 | 2635111.7938 | 1267529.527 | 2635119.6235 | 1267533.8593
108 | 2635057.5631 | 1267527.5631 | 2635053.6311 | 1267526.3355 | 2635048.852 | 1267524.3888
109 | 2635064.7178 | 1267565.7183 | 2635069.9956 | 1267556.7291
110 | 2635059.9954 | 1267573.8628 | 2635064.7178 | 1267565.7183
111 | 2635064.7178 | 1267565.7183 | 2635081.4742 | 1267569.9081
112 | 2635048.852 | 1267524.3888 | 2635012.9425 | 1267509.7618
113 | 2635146.2071 | 1267538.2042 | 2635145.4191 | 1267532.7512 | 2635142.2689 | 1267524.5711
114 | 2635142.2689 | 1267524.5711 | 2635154.5954 | 1267526.2233 | 2635163.7579 | 1267529.8355
115 | 2635142.2689 | 1267524.5711 | 2635150.1432 | 1267515.4891 | 2635152.1655 | 1267511.7162
116 | 2635146.2071 | 1267538.2042 | 2635147.4286 | 1267542.9037 | 2635146.3379 | 1267550.0659
117 | 2635010.5016 | 1267508.7676 | 2635012.9425 | 1267509.7618
118 | 2635010.5016 | 1267508.7676 | 2634996.1395 | 1267501.3106 | 2634972.3816 | 1267487.073
119 | 2635010.5016 | 1267508.7676 | 2634998.8903 | 1267522.862
120 | 2634959.1861 | 1267479.1652 | 2634972.3816 | 1267487.073
121 | 2634997.5842 | 1267524.4474 | 2634998.8903 | 1267522.862
122 | 2635059.9954 | 1267573.8628 | 2635055.0041 | 1267585.486
123 | 2635081.4742 | 1267569.9081 | 2635090.5545 | 1267572.1786
124 | 2634963.7255 | 1267468.8402 | 2634959.1861 | 1267479.1652
125 | 2634941.688 | 1267468.6877 | 2634959.1861 | 1267479.1652
126 | 2634981.7233 | 1267543.7001 | 2634997.5842 | 1267524.4474
127 | 2635146.3379 | 1267550.0659 | 2635143.7639 | 1267566.9662
128 | 2635141.7659 | 1267580.0856 | 2635143.7639 | 1267566.9662
129 | 2634941.688 | 1267468.6877 | 2634946.7217 | 1267460.0557 | 2634949.4069 | 1267452.5924
130 | 2634941.688 | 1267468.6877 | 2634928.8169 | 1267461.9887
131 | 2634928.8169 | 1267461.9887 | 2634926.9506 | 1267461.0174 | 2634907.6743 | 1267453.2345
132 | 2634894.0841 | 1267447.7473 | 2634907.6743 | 1267453.2345
133 | 2634894.0841 | 1267447.7473 | 2634891.5227 | 1267458.3287 | 2634891.4771 | 1267459.9867
134 | 2634890.7655 | 1267485.8549 | 2634891.4771 | 1267459.9867
135 | 2634890.6316 | 1267490.7244 | 2634890.7655 | 1267485.8549
136 | 2634890.6316 | 1267490.7244 | 2634890.1374 | 1267507.2256
137 | 2634890.6316 | 1267490.7244 | 2634868.0737 | 1267482.3929
138 | 2634981.7233 | 1267543.7001 | 2634972.7023 | 1267550.7407 | 2634972.7023 | 1267550.7407
139 | 2634981.7233 | 1267543.7001 | 2634984.2895 | 1267546.3283 | 2634986.9205 | 1267547.356
140 | 2634889.9328 | 1267514.057 | 2634890.1374 | 1267507.2256
141 | 2634889.7326 | 1267520.7515 | 2634889.7879 | 1267518.8952 | 2634889.9328 | 1267514.057
142 | 2634889.7326 | 1267520.7515 | 2634889.4867 | 1267529.0048
143 | 2635050.0761 | 1267626.3839 | 2635051.0026 | 1267615.5259
144 | 2635051.3988 | 1267610.8828 | 2635051.0026 | 1267615.5259
145 | 2635048.2685 | 1267647.5683 | 2635050.0761 | 1267626.3839
146 | 2635051.3988 | 1267610.8828 | 2635047.305 | 1267610.7585 | 2635044.3223 | 1267609.8513 | 2635041.9312 | 1267608.1915 | 2635040.6147 | 1267606.8049 | 2635039.7315 | 1267604.6982 | 2635039.8941 | 1267602.8006
147 | 2635055.0041 | 1267585.486 | 2635051.3988 | 1267610.8828
148 | 2635026.9508 | 1267637.8129 | 2635038.9014 | 1267646.9791 | 2635048.2685 | 1267647.5683
149 | 2635048.2685 | 1267647.5683 | 2635047.9791 | 1267650.9654
150 | 2635047.2742 | 1267659.2392 | 2635047.9791 | 1267650.9654
151 | 2635141.7659 | 1267580.0856 | 2635128.8159 | 1267578.9778
152 | 2635141.7659 | 1267580.0856 | 2635140.844 | 1267592.4912
153 | 2635106.419 | 1267575.8391 | 2635116.9029 | 1267577.9587 | 2635128.8159 | 1267578.9778
154 | 2635140.844 | 1267592.4912 | 2635140.7821 | 1267593.3247
155 | 2635106.419 | 1267575.8391 | 2635100.0182 | 1267574.545 | 2635090.5545 | 1267572.1786
156 | 2635140.9967 | 1267614.2557 | 2635140.6369 | 1267595.2787 | 2635140.7821 | 1267593.3247
157 | 2635140.9967 | 1267614.2557 | 2635141.0441 | 1267616.7539
158 | 2635011.8858 | 1267557.1076 | 2634986.9205 | 1267547.356
159 | 2635160.1116 | 1267697.2563 | 2635156.219 | 1267697.4889 | 2635124.8182 | 1267699.3733
160 | 2635160.1116 | 1267697.2563 | 2635149.9566 | 1267670.9549 | 2635146.429 | 1267657.172
161 | 2635160.1116 | 1267697.2563 | 2635163.5321 | 1267686.5468 | 2635165.766 | 1267659.624
162 | 2635143.4498 | 1267643.6026 | 2635143.8146 | 1267646.9568 | 2635146.429 | 1267657.172
163 | 2635168.6421 | 1267639.1731 | 2635166.2644 | 1267653.6172 | 2635165.766 | 1267659.624
164 | 2635143.4498 | 1267643.6026 | 2635141.2531 | 1267623.4025
165 | 2635141.2531 | 1267623.4025 | 2635141.1526 | 1267622.479 | 2635141.0441 | 1267616.7539
166 | 2634889.0112 | 1267544.9654 | 2634888.2171 | 1267571.6164
167 | 2634888.1967 | 1267572.3006 | 2634888.2171 | 1267571.6164
168 | 2634889.0112 | 1267544.9654 | 2634889.1709 | 1267539.6038
169 | 2634888.1967 | 1267572.3006 | 2634887.6763 | 1267589.7668 | 2634887.5608 | 1267600.5757
170 | 2634889.4867 | 1267529.0048 | 2634889.1709 | 1267539.6038
171 | 2634972.7023 | 1267550.7407 | 2634968.421 | 1267554.4716
172 | 2634968.421 | 1267554.4716 | 2634955.2635 | 1267565.9375 | 2634955.1146 | 1267566.1315
173 | 2634955.1146 | 1267566.1315 | 2634953.6275 | 1267568.0704

## bus_geodata
| x | y | coords
0 | 2635233.6576 | 1267268.7085
1 | 2635232.0079 | 1267272.4933
2 | 2635236.9353 | 1267261.1892
3 | 2635223.2079 | 1267298.9797
4 | 2635241.1471 | 1267251.5266
5 | 2635208.265 | 1267291.4489
6 | 2635217.2677 | 1267318.4016
7 | 2635242.3296 | 1267249.0773
8 | 2635193.1381 | 1267291.0418
9 | 2635216.5194 | 1267320.8133
10 | 2635255.1491 | 1267225.0838
11 | 2635213.8292 | 1267328.7533
12 | 2635070.3129 | 1267196.6947
13 | 2635059.9157 | 1267212.609
14 | 2635076.5109 | 1267187.2079
15 | 2635057.792 | 1267215.8596
16 | 2635043.0481 | 1267238.4273
17 | 2635036.617 | 1267248.2709
18 | 2635031.6332 | 1267255.6104
19 | 2635030.5476 | 1267257.2065
20 | 2635030.2975 | 1267257.5744
21 | 2634968.2869 | 1267258.7046
22 | 2634961.7755 | 1267271.6209
23 | 2634973.6571 | 1267248.052
24 | 2634952.1978 | 1267266.821
25 | 2634968.705 | 1267277.0944
26 | 2634931.2764 | 1267256.3361
27 | 2634983.3882 | 1267284.353
28 | 2634930.8666 | 1267256.1307
29 | 2634992.0709 | 1267288.6453
30 | 2635208.2326 | 1267345.2717
31 | 2635193.9491 | 1267377.0901
32 | 2635191.7356 | 1267381.8849
33 | 2635180.7539 | 1267405.6722
34 | 2635174.3098 | 1267419.6308
35 | 2635019.4774 | 1267273.4842
36 | 2635026.9186 | 1267262.5426
37 | 2635008.7687 | 1267289.2303
38 | 2635004.8652 | 1267294.9701
39 | 2634999.7452 | 1267308.202
40 | 2634992.1223 | 1267327.9028
41 | 2634918.219 | 1267249.7924
42 | 2634895.0272 | 1267238.1697
43 | 2634901.2937 | 1267226.4651
44 | 2634890.4503 | 1267245.3138
45 | 2634903.2377 | 1267222.834
46 | 2634885.5973 | 1267252.8889
47 | 2634907.8214 | 1267214.2725
48 | 2634883.3724 | 1267256.3616
49 | 2635139.2927 | 1267437.3206
50 | 2635115.6027 | 1267425.7748
51 | 2635154.1953 | 1267445.8652
52 | 2635088.2392 | 1267414.6829
53 | 2635159.7647 | 1267449.2767
54 | 2635162.2169 | 1267457.1191
55 | 2635167.989 | 1267432.5137
56 | 2635147.7042 | 1267469.2454
57 | 2635173.1881 | 1267475.3306
58 | 2635214.7775 | 1267419.2281
59 | 2635221.1927 | 1267403.5314
60 | 2635199.6795 | 1267445.4779
61 | 2635228.1547 | 1267405.9004
62 | 2635224.1442 | 1267393.5596
63 | 2635219.2055 | 1267455.3567
64 | 2635232.0807 | 1267366.7458
65 | 2635212.4629 | 1267475.6509
66 | 2635170.5646 | 1267478.6023
67 | 2635233.391 | 1267362.319
68 | 2635209.0823 | 1267486.6513
69 | 2635158.9966 | 1267497.2688
70 | 2635235.8906 | 1267354.209
71 | 2635136.2106 | 1267478.8489
72 | 2634870.5013 | 1267297.3341
73 | 2634898.0345 | 1267307.2713
74 | 2634866.5806 | 1267325.2754
75 | 2634990.3566 | 1267332.4661
76 | 2635002.1066 | 1267393.9575
77 | 2634993.3181 | 1267392.2134
78 | 2634973.0262 | 1267386.5362
79 | 2634976.4535 | 1267375.1601
80 | 2634967.1924 | 1267403.1581
81 | 2634979.8942 | 1267363.7394
82 | 2634962.9608 | 1267414.9197
83 | 2634947.141 | 1267394.0361
84 | 2634956.1134 | 1267330.6995
85 | 2634951.0638 | 1267328.3211
86 | 2634936.4446 | 1267321.4354
87 | 2634985.656 | 1267344.6142
88 | 2634980.9722 | 1267360.1612
89 | 2634924.6691 | 1267315.889
90 | 2634917.6443 | 1267316.2367
91 | 2634908.684 | 1267329.3965
92 | 2634906.3646 | 1267334.86
93 | 2634937.9127 | 1267389.8379
94 | 2634911.1011 | 1267377.6405
95 | 2634890.3839 | 1267364.3103
96 | 2634956.3733 | 1267433.2295
97 | 2634898.0199 | 1267354.5171
98 | 2634952.3633 | 1267444.375
99 | 2635094.3612 | 1267518.3534
100 | 2635098.9157 | 1267513.3961
101 | 2635088.8798 | 1267531.2479
102 | 2635105.3042 | 1267506.3808
103 | 2635079.8345 | 1267532.195
104 | 2635111.7938 | 1267529.527
105 | 2635117.5773 | 1267494.4182
106 | 2635057.5631 | 1267527.5631
107 | 2635119.6235 | 1267533.8593
108 | 2635069.9956 | 1267556.7291
109 | 2635064.7178 | 1267565.7183
110 | 2635048.852 | 1267524.3888
111 | 2635142.2689 | 1267524.5711
112 | 2635146.2071 | 1267538.2042
113 | 2635163.7579 | 1267529.8355
114 | 2635152.1655 | 1267511.7162
115 | 2635012.9425 | 1267509.7618
116 | 2635010.5016 | 1267508.7676
117 | 2634972.3816 | 1267487.073
118 | 2634998.8903 | 1267522.862
119 | 2635059.9954 | 1267573.8628
120 | 2635081.4742 | 1267569.9081
121 | 2634959.1861 | 1267479.1652
122 | 2634997.5842 | 1267524.4474
123 | 2635146.3379 | 1267550.0659
124 | 2635143.7639 | 1267566.9662
125 | 2634949.4069 | 1267452.5924
126 | 2634941.688 | 1267468.6877
127 | 2634928.8169 | 1267461.9887
128 | 2634963.7255 | 1267468.8402
129 | 2634907.6743 | 1267453.2345
130 | 2634894.0841 | 1267447.7473
131 | 2634891.4771 | 1267459.9867
132 | 2634890.7655 | 1267485.8549
133 | 2634890.6316 | 1267490.7244
134 | 2634981.7233 | 1267543.7001
135 | 2634890.1374 | 1267507.2256
136 | 2634868.0737 | 1267482.3929
137 | 2634889.9328 | 1267514.057
138 | 2634889.7326 | 1267520.7515
139 | 2635051.0026 | 1267615.5259
140 | 2635050.0761 | 1267626.3839
141 | 2635051.3988 | 1267610.8828
142 | 2635048.2685 | 1267647.5683
143 | 2635039.8941 | 1267602.8006
144 | 2635055.0041 | 1267585.486
145 | 2635026.9508 | 1267637.8129
146 | 2635047.9791 | 1267650.9654
147 | 2635047.2742 | 1267659.2392
148 | 2635141.7659 | 1267580.0856
149 | 2635128.8159 | 1267578.9778
150 | 2635140.844 | 1267592.4912
151 | 2635106.419 | 1267575.8391
152 | 2635140.7821 | 1267593.3247
153 | 2635090.5545 | 1267572.1786
154 | 2635140.9967 | 1267614.2557
155 | 2635011.8858 | 1267557.1076
156 | 2634986.9205 | 1267547.356
157 | 2635124.8182 | 1267699.3733
158 | 2635160.1116 | 1267697.2563
159 | 2635146.429 | 1267657.172
160 | 2635165.766 | 1267659.624
161 | 2635143.4498 | 1267643.6026
162 | 2635168.6421 | 1267639.1731
163 | 2635141.2531 | 1267623.4025
164 | 2634888.2171 | 1267571.6164
165 | 2634889.0112 | 1267544.9654
166 | 2634888.1967 | 1267572.3006
167 | 2634889.1709 | 1267539.6038
168 | 2634887.5608 | 1267600.5757
169 | 2634889.4867 | 1267529.0048
170 | 2635141.0441 | 1267616.7539
171 | 2634972.7023 | 1267550.7407
172 | 2634968.421 | 1267554.4716
173 | 2634955.1146 | 1267566.1315
174 | 2634953.6275 | 1267568.0704
175 | 2635126.0463 | 1267393.2141

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1