## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4261-5_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4261-5_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4261-5_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4261-5_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4261-5_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4261-5_0_7_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4261-5_0_7_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_4261-5_0_7_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_4261-5_0_7_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_4261-5_0_7_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_4261-5_0_7_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_4261-5_0_7_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_4261-5_0_7_node_29 | 0.4 | n |  | TRUE
13 | bus_LV_4261-5_0_7_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_4261-5_0_7_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_4261-5_0_7_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_4261-5_0_7_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_4261-5_0_7_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_4261-5_0_7_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_4261-5_0_7_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_4261-5_0_7_node_43 | 0.4 | n |  | TRUE
21 | bus_LV_4261-5_0_7_node_56 | 0.4 | n |  | TRUE
22 | bus_LV_4261-5_0_7_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_4261-5_0_7_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_4261-5_0_7_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_4261-5_0_7_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_4261-5_0_7_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_4261-5_0_7_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_4261-5_0_7_node_98 | 0.4 | n |  | TRUE
29 | bus_LV_4261-5_0_7_node_97 | 0.4 | n |  | TRUE
30 | bus_LV_4261-5_0_7_node_99 | 0.4 | n |  | TRUE
31 | bus_LV_4261-5_0_7_node_71 | 0.4 | n |  | TRUE
32 | bus_LV_4261-5_0_7_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_4261-5_0_7_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_4261-5_0_7_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_4261-5_0_7_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_4261-5_0_7_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_4261-5_0_7_node_22 | 0.4 | n |  | TRUE
38 | bus_LV_4261-5_0_7_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_4261-5_0_7_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_4261-5_0_7_node_207 | 0.4 | n |  | TRUE
41 | bus_LV_4261-5_0_7_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_4261-5_0_7_node_205 | 0.4 | n |  | TRUE
43 | bus_LV_4261-5_0_7_node_208 | 0.4 | n |  | TRUE
44 | bus_LV_4261-5_0_7_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_4261-5_0_7_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_4261-5_0_7_node_32 | 0.4 | n |  | TRUE
47 | bus_LV_4261-5_0_7_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_4261-5_0_7_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_4261-5_0_7_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_4261-5_0_7_node_85 | 0.4 | n |  | TRUE
51 | bus_LV_4261-5_0_7_node_92 | 0.4 | n |  | TRUE
52 | bus_LV_4261-5_0_7_node_86 | 0.4 | n |  | TRUE
53 | bus_LV_4261-5_0_7_node_94 | 0.4 | n |  | TRUE
54 | bus_LV_4261-5_0_7_node_90 | 0.4 | n |  | TRUE
55 | bus_LV_4261-5_0_7_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_4261-5_0_7_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_4261-5_0_7_node_39 | 0.4 | n |  | TRUE
58 | bus_LV_4261-5_0_7_node_128 | 0.4 | n |  | TRUE
59 | bus_LV_4261-5_0_7_node_132 | 0.4 | n |  | TRUE
60 | bus_LV_4261-5_0_7_node_127 | 0.4 | n |  | TRUE
61 | bus_LV_4261-5_0_7_node_133 | 0.4 | n |  | TRUE
62 | bus_LV_4261-5_0_7_node_105 | 0.4 | n |  | TRUE
63 | bus_LV_4261-5_0_7_node_102 | 0.4 | n |  | TRUE
64 | bus_LV_4261-5_0_7_node_148 | 0.4 | n |  | TRUE
65 | bus_LV_4261-5_0_7_node_144 | 0.4 | n |  | TRUE
66 | bus_LV_4261-5_0_7_node_103 | 0.4 | n |  | TRUE
67 | bus_LV_4261-5_0_7_node_44 | 0.4 | n |  | TRUE
68 | bus_LV_4261-5_0_7_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_4261-5_0_7_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_4261-5_0_7_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_4261-5_0_7_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_4261-5_0_7_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_4261-5_0_7_node_65 | 0.4 | n |  | TRUE
74 | bus_LV_4261-5_0_7_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_4261-5_0_7_node_50 | 0.4 | n |  | TRUE
76 | bus_LV_4261-5_0_7_node_51 | 0.4 | n |  | TRUE
77 | bus_LV_4261-5_0_7_node_68 | 0.4 | n |  | TRUE
78 | bus_LV_4261-5_0_7_node_64 | 0.4 | n |  | TRUE
79 | bus_LV_4261-5_0_7_node_67 | 0.4 | n |  | TRUE
80 | bus_LV_4261-5_0_7_node_52 | 0.4 | n |  | TRUE
81 | bus_LV_4261-5_0_7_node_53 | 0.4 | n |  | TRUE
82 | bus_LV_4261-5_0_7_node_55 | 0.4 | n |  | TRUE
83 | bus_LV_4261-5_0_7_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_4261-5_0_7_node_57 | 0.4 | n |  | TRUE
85 | bus_LV_4261-5_0_7_node_58 | 0.4 | n |  | TRUE
86 | bus_LV_4261-5_0_7_node_59 | 0.4 | n |  | TRUE
87 | bus_LV_4261-5_0_7_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_4261-5_0_7_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_4261-5_0_7_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_4261-5_0_7_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_4261-5_0_7_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_4261-5_0_7_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_4261-5_0_7_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_4261-5_0_7_node_145 | 0.4 | n |  | TRUE
95 | bus_LV_4261-5_0_7_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_4261-5_0_7_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_4261-5_0_7_node_74 | 0.4 | n |  | TRUE
98 | bus_LV_4261-5_0_7_node_73 | 0.4 | n |  | TRUE
99 | bus_LV_4261-5_0_7_node_75 | 0.4 | n |  | TRUE
100 | bus_LV_4261-5_0_7_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_4261-5_0_7_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_4261-5_0_7_node_126 | 0.4 | n |  | TRUE
103 | bus_LV_4261-5_0_7_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_4261-5_0_7_node_80 | 0.4 | n |  | TRUE
105 | bus_LV_4261-5_0_7_node_82 | 0.4 | n |  | TRUE
106 | bus_LV_4261-5_0_7_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_4261-5_0_7_node_84 | 0.4 | n |  | TRUE
108 | bus_LV_4261-5_0_7_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_4261-5_0_7_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_4261-5_0_7_node_100 | 0.4 | n |  | TRUE
111 | bus_LV_4261-5_0_7_node_111 | 0.4 | n |  | TRUE
112 | bus_LV_4261-5_0_7_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_4261-5_0_7_node_88 | 0.4 | n |  | TRUE
114 | bus_LV_4261-5_0_7_node_89 | 0.4 | n |  | TRUE
115 | bus_LV_4261-5_0_7_node_91 | 0.4 | n |  | TRUE
116 | bus_LV_4261-5_0_7_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_4261-5_0_7_node_115 | 0.4 | n |  | TRUE
118 | bus_LV_4261-5_0_7_node_136 | 0.4 | n |  | TRUE
119 | bus_LV_4261-5_0_7_node_116 | 0.4 | n |  | TRUE
120 | bus_LV_4261-5_0_7_node_190 | 0.4 | n |  | TRUE
121 | bus_LV_4261-5_0_7_node_143 | 0.4 | n |  | TRUE
122 | bus_LV_4261-5_0_7_node_109 | 0.4 | n |  | TRUE
123 | bus_LV_4261-5_0_7_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_4261-5_0_7_node_110 | 0.4 | n |  | TRUE
125 | bus_LV_4261-5_0_7_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_4261-5_0_7_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_4261-5_0_7_node_146 | 0.4 | n |  | TRUE
128 | bus_LV_4261-5_0_7_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_4261-5_0_7_node_149 | 0.4 | n |  | TRUE
130 | bus_LV_4261-5_0_7_node_152 | 0.4 | n |  | TRUE
131 | bus_LV_4261-5_0_7_node_140 | 0.4 | n |  | TRUE
132 | bus_LV_4261-5_0_7_node_117 | 0.4 | n |  | TRUE
133 | bus_LV_4261-5_0_7_node_118 | 0.4 | n |  | TRUE
134 | bus_LV_4261-5_0_7_node_119 | 0.4 | n |  | TRUE
135 | bus_LV_4261-5_0_7_node_120 | 0.4 | n |  | TRUE
136 | bus_LV_4261-5_0_7_node_121 | 0.4 | n |  | TRUE
137 | bus_LV_4261-5_0_7_node_123 | 0.4 | n |  | TRUE
138 | bus_LV_4261-5_0_7_node_138 | 0.4 | n |  | TRUE
139 | bus_LV_4261-5_0_7_node_122 | 0.4 | n |  | TRUE
140 | bus_LV_4261-5_0_7_node_137 | 0.4 | n |  | TRUE
141 | bus_LV_4261-5_0_7_node_124 | 0.4 | n |  | TRUE
142 | bus_LV_4261-5_0_7_node_125 | 0.4 | n |  | TRUE
143 | bus_LV_4261-5_0_7_node_129 | 0.4 | n |  | TRUE
144 | bus_LV_4261-5_0_7_node_130 | 0.4 | n |  | TRUE
145 | bus_LV_4261-5_0_7_node_131 | 0.4 | n |  | TRUE
146 | bus_LV_4261-5_0_7_node_134 | 0.4 | n |  | TRUE
147 | bus_LV_4261-5_0_7_node_141 | 0.4 | n |  | TRUE
148 | bus_LV_4261-5_0_7_node_135 | 0.4 | n |  | TRUE
149 | bus_LV_4261-5_0_7_node_139 | 0.4 | n |  | TRUE
150 | bus_LV_4261-5_0_7_node_147 | 0.4 | n |  | TRUE
151 | bus_LV_4261-5_0_7_node_142 | 0.4 | n |  | TRUE
152 | bus_LV_4261-5_0_7_node_150 | 0.4 | n |  | TRUE
153 | bus_LV_4261-5_0_7_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_4261-5_0_7_node_189 | 0.4 | n |  | TRUE
155 | bus_LV_4261-5_0_7_node_153 | 0.4 | n |  | TRUE
156 | bus_LV_4261-5_0_7_node_155 | 0.4 | n |  | TRUE
157 | bus_LV_4261-5_0_7_node_157 | 0.4 | n |  | TRUE
158 | bus_LV_4261-5_0_7_node_158 | 0.4 | n |  | TRUE
159 | bus_LV_4261-5_0_7_node_181 | 0.4 | n |  | TRUE
160 | bus_LV_4261-5_0_7_node_191 | 0.4 | n |  | TRUE
161 | bus_LV_4261-5_0_7_node_173 | 0.4 | n |  | TRUE
162 | bus_LV_4261-5_0_7_node_182 | 0.4 | n |  | TRUE
163 | bus_LV_4261-5_0_7_node_180 | 0.4 | n |  | TRUE
164 | bus_LV_4261-5_0_7_node_194 | 0.4 | n |  | TRUE
165 | bus_LV_4261-5_0_7_node_195 | 0.4 | n |  | TRUE
166 | bus_LV_4261-5_0_7_node_162 | 0.4 | n |  | TRUE
167 | bus_LV_4261-5_0_7_node_192 | 0.4 | n |  | TRUE
168 | bus_LV_4261-5_0_7_node_171 | 0.4 | n |  | TRUE
169 | bus_LV_4261-5_0_7_node_159 | 0.4 | n |  | TRUE
170 | bus_LV_4261-5_0_7_node_160 | 0.4 | n |  | TRUE
171 | bus_LV_4261-5_0_7_node_161 | 0.4 | n |  | TRUE
172 | bus_LV_4261-5_0_7_node_163 | 0.4 | n |  | TRUE
173 | bus_LV_4261-5_0_7_node_164 | 0.4 | n |  | TRUE
174 | bus_LV_4261-5_0_7_node_202 | 0.4 | n |  | TRUE
175 | bus_LV_4261-5_0_7_node_206 | 0.4 | n |  | TRUE
176 | bus_LV_4261-5_0_7_node_169 | 0.4 | n |  | TRUE
177 | bus_LV_4261-5_0_7_node_175 | 0.4 | n |  | TRUE
178 | bus_LV_4261-5_0_7_node_200 | 0.4 | n |  | TRUE
179 | bus_LV_4261-5_0_7_node_204 | 0.4 | n |  | TRUE
180 | bus_LV_4261-5_0_7_node_167 | 0.4 | n |  | TRUE
181 | bus_LV_4261-5_0_7_node_176 | 0.4 | n |  | TRUE
182 | bus_LV_4261-5_0_7_node_165 | 0.4 | n |  | TRUE
183 | bus_LV_4261-5_0_7_node_166 | 0.4 | n |  | TRUE
184 | bus_LV_4261-5_0_7_node_168 | 0.4 | n |  | TRUE
185 | bus_LV_4261-5_0_7_node_185 | 0.4 | n |  | TRUE
186 | bus_LV_4261-5_0_7_node_186 | 0.4 | n |  | TRUE
187 | bus_LV_4261-5_0_7_node_183 | 0.4 | n |  | TRUE
188 | bus_LV_4261-5_0_7_node_170 | 0.4 | n |  | TRUE
189 | bus_LV_4261-5_0_7_node_174 | 0.4 | n |  | TRUE
190 | bus_LV_4261-5_0_7_node_179 | 0.4 | n |  | TRUE
191 | bus_LV_4261-5_0_7_node_178 | 0.4 | n |  | TRUE
192 | bus_LV_4261-5_0_7_node_187 | 0.4 | n |  | TRUE
193 | bus_LV_4261-5_0_7_node_177 | 0.4 | n |  | TRUE
194 | bus_LV_4261-5_0_7_node_188 | 0.4 | n |  | TRUE
195 | bus_LV_4261-5_0_7_node_184 | 0.4 | n |  | TRUE
196 | bus_LV_4261-5_0_7_node_193 | 0.4 | n |  | TRUE
197 | bus_LV_4261-5_0_7_node_211 | 0.4 | n |  | TRUE
198 | bus_LV_4261-5_0_7_node_216 | 0.4 | n |  | TRUE
199 | bus_LV_4261-5_0_7_node_212 | 0.4 | n |  | TRUE
200 | bus_LV_4261-5_0_7_node_209 | 0.4 | n |  | TRUE
201 | bus_LV_4261-5_0_7_node_210 | 0.4 | n |  | TRUE
202 | bus_LV_4261-5_0_7_node_197 | 0.4 | n |  | TRUE
203 | bus_LV_4261-5_0_7_node_198 | 0.4 | n |  | TRUE
204 | bus_LV_4261-5_0_7_node_199 | 0.4 | n |  | TRUE
205 | bus_LV_4261-5_0_7_node_201 | 0.4 | n |  | TRUE
206 | bus_LV_4261-5_0_7_node_203 | 0.4 | n |  | TRUE
207 | bus_LV_4261-5_0_7_node_215 | 0.4 | n |  | TRUE
208 | bus_LV_4261-5_0_7_node_213 | 0.4 | n |  | TRUE
209 | bus_LV_4261-5_0_7_node_214 | 0.4 | n |  | TRUE
210 | bus_MV_298_0_node_128 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4261-5_0_7_load_0 | 0 | 0.0034153 | 0.00085596 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4261-5_0_7_load_1 | 1 | 0.0019042 | 0.00047724 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4261-5_0_7_load_3 | 3 | 0.00076895 | 0.00019272 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4261-5_0_7_load_5 | 5 | 0.0019365 | 0.00048532 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4261-5_0_7_load_12 | 6 | 0.002187 | 0.00054812 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4261-5_0_7_load_27 | 7 | 0.0043767 | 0.0010969 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4261-5_0_7_load_25 | 8 | 0.00088367 | 0.00022147 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4261-5_0_7_load_28 | 9 | 0.0044481 | 0.0011148 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4261-5_0_7_load_13 | 10 | 0.0026179 | 0.0006561 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4261-5_0_7_load_30 | 11 | 0.0036721 | 0.00092031 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4261-5_0_7_load_29 | 12 | 0.0015093 | 0.00037827 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4261-5_0_7_load_6 | 13 | 0.0022895 | 0.00057381 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4261-5_0_7_load_7 | 14 | 0.0021012 | 0.00052661 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4261-5_0_7_load_9 | 16 | 0.0019222 | 0.00048175 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4261-5_0_7_load_11 | 17 | 0.0030785 | 0.00077155 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4261-5_0_7_load_10 | 19 | 0.0015963 | 0.00040008 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4261-5_0_7_load_43 | 20 | 0.0018761 | 0.0004702 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4261-5_0_7_load_56 | 21 | 0.0015863 | 0.00039756 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4261-5_0_7_load_18 | 23 | 0.0017494 | 0.00043843 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4261-5_0_7_load_42 | 24 | 0.0021585 | 0.00054097 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4261-5_0_7_load_54 | 25 | 0.0025449 | 0.00063781 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4261-5_0_7_load_14 | 26 | 0.0015266 | 0.0003826 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4261-5_0_7_load_15 | 27 | 0.00094 | 0.00023559 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4261-5_0_7_load_98 | 28 | 0.0017497 | 0.00043853 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4261-5_0_7_load_97 | 29 | 0.0017159 | 0.00043005 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4261-5_0_7_load_99 | 30 | 0.0010556 | 0.00026456 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4261-5_0_7_load_72 | 32 | 0.0022328 | 0.00055959 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4261-5_0_7_load_69 | 33 | 0.0022565 | 0.00056553 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4261-5_0_7_load_19 | 34 | 0.0041209 | 0.0010328 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4261-5_0_7_load_20 | 35 | 0.0050194 | 0.001258 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4261-5_0_7_load_22 | 37 | 0.003145 | 0.0007882 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4261-5_0_7_load_23 | 38 | 0.0065435 | 0.0016399 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4261-5_0_7_load_24 | 39 | 0.014767 | 0.0037009 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4261-5_0_7_load_40 | 41 | 0.018704 | 0.0046878 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4261-5_0_7_load_205 | 42 | 0.032172 | 0.008063 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4261-5_0_7_load_208 | 43 | 0.0027993 | 0.00070157 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4261-5_0_7_load_31 | 45 | 0.0069774 | 0.0017487 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4261-5_0_7_load_34 | 47 | 0.0030289 | 0.00075911 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4261-5_0_7_load_35 | 48 | 0.0018707 | 0.00046885 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4261-5_0_7_load_33 | 49 | 0.0048 | 0.001203 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4261-5_0_7_load_85 | 50 | 0.0029683 | 0.00074393 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4261-5_0_7_load_86 | 52 | 0.0030251 | 0.00075817 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4261-5_0_7_load_94 | 53 | 0.0011793 | 0.00029556 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4261-5_0_7_load_90 | 54 | 0.002646 | 0.00066314 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4261-5_0_7_load_36 | 55 | 0.0012956 | 0.0003247 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4261-5_0_7_load_128 | 58 | 0.0060262 | 0.0015103 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4261-5_0_7_load_132 | 59 | 0.001255 | 0.00031454 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4261-5_0_7_load_127 | 60 | 0.0016851 | 0.00042234 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4261-5_0_7_load_133 | 61 | 0.0012399 | 0.00031075 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4261-5_0_7_load_102 | 63 | 0.0049841 | 0.0012491 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4261-5_0_7_load_148 | 64 | 0.017483 | 0.0043816 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4261-5_0_7_load_144 | 65 | 0.0039628 | 0.00099317 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4261-5_0_7_load_103 | 66 | 0.0013451 | 0.00033712 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4261-5_0_7_load_44 | 67 | 0.0014313 | 0.00035873 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4261-5_0_7_load_45 | 68 | 0.00059836 | 0.00014996 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4261-5_0_7_load_46 | 69 | 0.00253 | 0.00063409 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4261-5_0_7_load_47 | 70 | 0.0013944 | 0.00034946 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4261-5_0_7_load_48 | 71 | 0.0014115 | 0.00035376 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4261-5_0_7_load_66 | 72 | 0.0015036 | 0.00037685 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4261-5_0_7_load_65 | 73 | 0.0015254 | 0.0003823 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4261-5_0_7_load_49 | 74 | 0.0038097 | 0.00095479 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4261-5_0_7_load_50 | 75 | 0.0039363 | 0.00098653 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4261-5_0_7_load_67 | 79 | 0.0018212 | 0.00045642 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4261-5_0_7_load_52 | 80 | 0.0032572 | 0.00081634 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4261-5_0_7_load_53 | 81 | 0.0018296 | 0.00045853 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4261-5_0_7_load_55 | 82 | 0.0024229 | 0.00060723 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4261-5_0_7_load_63 | 83 | 0.00092443 | 0.00023168 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4261-5_0_7_load_57 | 84 | 0.00194 | 0.00048622 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4261-5_0_7_load_58 | 85 | 0.0033294 | 0.00083442 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4261-5_0_7_load_61 | 88 | 0.0035428 | 0.0008879 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4261-5_0_7_load_62 | 89 | 0.0013621 | 0.00034138 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4261-5_0_7_load_78 | 90 | 0.0028106 | 0.0007044 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4261-5_0_7_load_76 | 91 | 0.0012569 | 0.00031502 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4261-5_0_7_load_70 | 92 | 0.0015839 | 0.00039695 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4261-5_0_7_load_87 | 93 | 0.0015352 | 0.00038475 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4261-5_0_7_load_145 | 94 | 0.0019528 | 0.00048942 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4261-5_0_7_load_77 | 95 | 0.0022545 | 0.00056503 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4261-5_0_7_load_83 | 96 | 0.0022234 | 0.00055725 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4261-5_0_7_load_74 | 97 | 0.000673 | 0.00016867 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4261-5_0_7_load_96 | 100 | 0.0014968 | 0.00037513 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4261-5_0_7_load_95 | 101 | 0.0026743 | 0.00067024 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4261-5_0_7_load_126 | 102 | 0.0017546 | 0.00043974 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4261-5_0_7_load_79 | 103 | 0.0022326 | 0.00055954 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4261-5_0_7_load_80 | 104 | 0.0023178 | 0.0005809 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4261-5_0_7_load_84 | 107 | 0.0025222 | 0.00063212 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4261-5_0_7_load_106 | 108 | 0.0026578 | 0.0006661 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4261-5_0_7_load_100 | 110 | 0.0026804 | 0.00067177 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4261-5_0_7_load_111 | 111 | 0.0043275 | 0.0010846 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4261-5_0_7_load_101 | 112 | 0.0063929 | 0.0016022 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4261-5_0_7_load_88 | 113 | 0.0014438 | 0.00036184 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4261-5_0_7_load_89 | 114 | 0.00096826 | 0.00024267 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4261-5_0_7_load_91 | 115 | 0.0034312 | 0.00085993 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4261-5_0_7_load_93 | 116 | 0.0035036 | 0.00087809 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4261-5_0_7_load_115 | 117 | 0.0025965 | 0.00065073 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4261-5_0_7_load_136 | 118 | 0.0039717 | 0.00099541 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4261-5_0_7_load_116 | 119 | 0.0017627 | 0.00044178 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4261-5_0_7_load_190 | 120 | 0.026632 | 0.0066746 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4261-5_0_7_load_143 | 121 | 0.0011531 | 0.00028899 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4261-5_0_7_load_109 | 122 | 0.0038147 | 0.00095606 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4261-5_0_7_load_108 | 123 | 0.003851 | 0.00096516 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4261-5_0_7_load_112 | 125 | 0.00266 | 0.00066666 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4261-5_0_7_load_146 | 127 | 0.0028855 | 0.00072318 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4261-5_0_7_load_149 | 129 | 0.0023155 | 0.00058032 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4261-5_0_7_load_152 | 130 | 0.0012503 | 0.00031335 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4261-5_0_7_load_140 | 131 | 0.0039822 | 0.00099803 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4261-5_0_7_load_117 | 132 | 0.0052789 | 0.001323 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4261-5_0_7_load_118 | 133 | 0.0036035 | 0.00090313 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4261-5_0_7_load_119 | 134 | 0.011639 | 0.0029171 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4261-5_0_7_load_121 | 136 | 0.0012477 | 0.0003127 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4261-5_0_7_load_123 | 137 | 0.0027955 | 0.00070062 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4261-5_0_7_load_122 | 139 | 0.0040225 | 0.0010081 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4261-5_0_7_load_137 | 140 | 0.0024107 | 0.00060418 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4261-5_0_7_load_124 | 141 | 0.0067793 | 0.0016991 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4261-5_0_7_load_125 | 142 | 0.0073352 | 0.0018384 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4261-5_0_7_load_130 | 144 | 0.0014235 | 0.00035675 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4261-5_0_7_load_131 | 145 | 0.0010544 | 0.00026425 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4261-5_0_7_load_134 | 146 | 0.0012357 | 0.0003097 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4261-5_0_7_load_141 | 147 | 0.0039813 | 0.0009978 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4261-5_0_7_load_135 | 148 | 0.0019823 | 0.00049681 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4261-5_0_7_load_147 | 150 | 0.0011983 | 0.00030033 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4261-5_0_7_load_142 | 151 | 0.0021566 | 0.00054049 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4261-5_0_7_load_150 | 152 | 0.0047716 | 0.0011959 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4261-5_0_7_load_151 | 153 | 0.0020941 | 0.00052483 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4261-5_0_7_load_189 | 154 | 0.066195 | 0.01659 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4261-5_0_7_load_153 | 155 | 0.0021847 | 0.00054753 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4261-5_0_7_load_157 | 157 | 0.0024786 | 0.00062119 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4261-5_0_7_load_181 | 159 | 0.0018156 | 0.00045502 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4261-5_0_7_load_191 | 160 | 0.0021021 | 0.00052684 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4261-5_0_7_load_173 | 161 | 0.0013994 | 0.00035071 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4261-5_0_7_load_182 | 162 | 0.0033861 | 0.00084863 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4261-5_0_7_load_180 | 163 | 0.0014604 | 0.00036601 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4261-5_0_7_load_195 | 165 | 0.0048992 | 0.0012279 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4261-5_0_7_load_162 | 166 | 0.0044465 | 0.0011144 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4261-5_0_7_load_192 | 167 | 0.0021363 | 0.0005354 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4261-5_0_7_load_171 | 168 | 0.0020046 | 0.00050241 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4261-5_0_7_load_159 | 169 | 0.0038538 | 0.00096586 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4261-5_0_7_load_160 | 170 | 0.0020235 | 0.00050713 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4261-5_0_7_load_202 | 174 | 0.001866 | 0.00046766 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4261-5_0_7_load_206 | 175 | 0.0011929 | 0.00029897 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4261-5_0_7_load_169 | 176 | 0.00063021 | 0.00015795 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4261-5_0_7_load_175 | 177 | 0.0041961 | 0.0010516 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4261-5_0_7_load_204 | 179 | 0.0056168 | 0.0014077 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4261-5_0_7_load_167 | 180 | 0.0016942 | 0.00042459 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_4261-5_0_7_load_176 | 181 | 0.0030233 | 0.00075771 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_4261-5_0_7_load_165 | 182 | 0.0035875 | 0.00089911 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_4261-5_0_7_load_166 | 183 | 0.0015814 | 0.00039634 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_4261-5_0_7_load_168 | 184 | 0.0018871 | 0.00047295 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_4261-5_0_7_load_183 | 187 | 0.0013984 | 0.00035047 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_4261-5_0_7_load_170 | 188 | 0.0010125 | 0.00025376 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_4261-5_0_7_load_179 | 190 | 0.0017549 | 0.00043982 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_4261-5_0_7_load_178 | 191 | 0.00071218 | 0.00017849 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_4261-5_0_7_load_187 | 192 | 0.0014 | 0.00035086 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_4261-5_0_7_load_177 | 193 | 0.022593 | 0.0056623 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_4261-5_0_7_load_188 | 194 | 0.0016171 | 0.00040527 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_4261-5_0_7_load_184 | 195 | 0.001886 | 0.00047267 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_4261-5_0_7_load_193 | 196 | 0.0017056 | 0.00042745 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_4261-5_0_7_load_216 | 198 | 0.0015559 | 0.00038994 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_4261-5_0_7_load_212 | 199 | 0.0018144 | 0.00045473 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_4261-5_0_7_load_209 | 200 | 0.0041322 | 0.0010356 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_4261-5_0_7_load_210 | 201 | 0.0016592 | 0.00041582 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_4261-5_0_7_load_197 | 202 | 0.0055589 | 0.0013932 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_4261-5_0_7_load_198 | 203 | 0.0020503 | 0.00051385 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_4261-5_0_7_load_199 | 204 | 0.00094407 | 0.00023661 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_4261-5_0_7_load_201 | 205 | 0.0012392 | 0.00031057 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_4261-5_0_7_load_203 | 206 | 0.00069027 | 0.000173 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_4261-5_0_7_load_215 | 207 | 0.001679 | 0.0004208 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_4261-5_0_7_load_213 | 208 | 0.0014352 | 0.0003597 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_4261-5_0_7_load_214 | 209 | 0.0012172 | 0.00030505 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 149 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4261-5_0_7_line_0 |  | 0 | 1 | 0.023862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4261-5_0_7_line_1 |  | 0 | 2 | 0.021979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4261-5_0_7_line_2 |  | 1 | 3 | 0.014323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4261-5_0_7_line_3 |  | 2 | 4 | 0.01586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4261-5_0_7_line_4 |  | 2 | 5 | 0.034666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4261-5_0_7_line_5 |  | 3 | 6 | 0.0022629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4261-5_0_7_line_6 |  | 4 | 7 | 0.017111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4261-5_0_7_line_7 |  | 4 | 8 | 0.010557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4261-5_0_7_line_8 |  | 5 | 9 | 0.00029712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4261-5_0_7_line_9 |  | 6 | 10 | 0.012712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4261-5_0_7_line_10 |  | 7 | 11 | 0.0082139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4261-5_0_7_line_11 |  | 9 | 12 | 0.010552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4261-5_0_7_line_12 |  | 10 | 26 | 0.013546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4261-5_0_7_line_13 |  | 11 | 45 | 0.011299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4261-5_0_7_line_14 |  | 12 | 46 | 0.0085541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4261-5_0_7_line_15 |  | 13 | 14 | 0.021158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4261-5_0_7_line_16 |  | 13 | 15 | 0.017409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4261-5_0_7_line_17 |  | 14 | 16 | 0.012308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4261-5_0_7_line_18 |  | 15 | 17 | 0.043983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4261-5_0_7_line_19 |  | 16 | 18 | 0.012083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4261-5_0_7_line_20 |  | 17 | 21 | 0.025255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4261-5_0_7_line_21 |  | 18 | 22 | 0.015503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4261-5_0_7_line_22 |  | 18 | 23 | 0.0063193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4261-5_0_7_line_23 |  | 19 | 20 | 0.0076241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4261-5_0_7_line_24 |  | 20 | 24 | 0.017087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4261-5_0_7_line_25 |  | 21 | 25 | 0.011189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4261-5_0_7_line_26 |  | 22 | 30 | 0.030985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4261-5_0_7_line_27 |  | 24 | 67 | 0.00075635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4261-5_0_7_line_28 |  | 25 | 80 | 0.029623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4261-5_0_7_line_29 |  | 26 | 27 | 0.009142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4261-5_0_7_line_30 |  | 27 | 28 | 0.0092147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4261-5_0_7_line_31 |  | 28 | 29 | 0.017682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4261-5_0_7_line_32 |  | 29 | 30 | 0.0091433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4261-5_0_7_line_33 |  | 31 | 32 | 0.017821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4261-5_0_7_line_34 |  | 31 | 33 | 0.017524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4261-5_0_7_line_35 |  | 32 | 100 | 0.020187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4261-5_0_7_line_36 |  | 33 | 92 | 0.0059425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4261-5_0_7_line_37 |  | 34 | 35 | 0.0099866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4261-5_0_7_line_38 |  | 34 | 36 | 0.029217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4261-5_0_7_line_39 |  | 35 | 37 | 0.027199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4261-5_0_7_line_40 |  | 36 | 38 | 0.0025424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4261-5_0_7_line_41 |  | 36 | 39 | 0.012114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4261-5_0_7_line_42 |  | 37 | 40 | 0.029888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4261-5_0_7_line_43 |  | 38 | 41 | 0.013183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4261-5_0_7_line_44 |  | 39 | 42 | 0.0071455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4261-5_0_7_line_45 |  | 40 | 43 | 0.013062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4261-5_0_7_line_46 |  | 41 | 44 | 0.0068741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4261-5_0_7_line_47 |  | 43 | 207 | 0.041549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4261-5_0_7_line_48 |  | 44 | 62 | 0.013775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4261-5_0_7_line_49 |  | 44 | 63 | 0.015527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4261-5_0_7_line_50 |  | 45 | 48 | 0.0038752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4261-5_0_7_line_51 |  | 46 | 47 | 0.010398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4261-5_0_7_line_52 |  | 47 | 51 | 0.01826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4261-5_0_7_line_53 |  | 49 | 50 | 0.025457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4261-5_0_7_line_54 |  | 50 | 52 | 0.00021726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4261-5_0_7_line_55 |  | 51 | 53 | 0.010267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4261-5_0_7_line_56 |  | 51 | 54 | 0.011022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4261-5_0_7_line_57 |  | 52 | 113 | 0.022971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4261-5_0_7_line_58 |  | 53 | 118 | 0.030918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4261-5_0_7_line_59 |  | 54 | 115 | 0.004782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4261-5_0_7_line_60 |  | 55 | 56 | 0.037103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4261-5_0_7_line_61 |  | 56 | 57 | 0.031936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4261-5_0_7_line_62 |  | 57 | 58 | 0.015731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4261-5_0_7_line_63 |  | 57 | 59 | 0.043202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4261-5_0_7_line_64 |  | 58 | 60 | 0.0013103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4261-5_0_7_line_65 |  | 59 | 61 | 0.0043871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4261-5_0_7_line_66 |  | 60 | 143 | 0.017351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4261-5_0_7_line_67 |  | 62 | 64 | 0.02878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_4261-5_0_7_line_68 |  | 62 | 65 | 0.016565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
69 | LV_4261-5_0_7_line_69 |  | 63 | 66 | 0.015417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4261-5_0_7_line_70 |  | 64 | 120 | 0.024294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
71 | LV_4261-5_0_7_line_71 |  | 65 | 121 | 0.013264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
72 | LV_4261-5_0_7_line_72 |  | 67 | 68 | 0.0092173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4261-5_0_7_line_73 |  | 68 | 69 | 0.012202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4261-5_0_7_line_74 |  | 69 | 70 | 0.014827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4261-5_0_7_line_75 |  | 70 | 71 | 0.014876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4261-5_0_7_line_76 |  | 71 | 72 | 0.017722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4261-5_0_7_line_77 |  | 72 | 73 | 0.017733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4261-5_0_7_line_78 |  | 73 | 79 | 0.018378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4261-5_0_7_line_79 |  | 74 | 75 | 0.020022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4261-5_0_7_line_80 |  | 74 | 76 | 0.10718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4261-5_0_7_line_81 |  | 76 | 77 | 0.13511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4261-5_0_7_line_82 |  | 77 | 78 | 0.044678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4261-5_0_7_line_83 |  | 77 | 79 | 0.050974 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4261-5_0_7_line_84 |  | 78 | 97 | 0.024792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4261-5_0_7_line_85 |  | 78 | 83 | 0.00024549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4261-5_0_7_line_86 |  | 80 | 81 | 0.021007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4261-5_0_7_line_87 |  | 81 | 82 | 0.0084828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4261-5_0_7_line_88 |  | 84 | 85 | 0.030047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4261-5_0_7_line_89 |  | 84 | 86 | 0.021056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4261-5_0_7_line_90 |  | 85 | 87 | 0.037683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4261-5_0_7_line_91 |  | 86 | 88 | 0.014632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4261-5_0_7_line_92 |  | 86 | 89 | 0.0089383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4261-5_0_7_line_93 |  | 87 | 90 | 0.013841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4261-5_0_7_line_94 |  | 87 | 91 | 0.068788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4261-5_0_7_line_95 |  | 88 | 92 | 0.017277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4261-5_0_7_line_96 |  | 89 | 93 | 0.015387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4261-5_0_7_line_97 |  | 90 | 94 | 0.017366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4261-5_0_7_line_98 |  | 91 | 95 | 0.028805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4261-5_0_7_line_99 |  | 93 | 96 | 0.0076889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4261-5_0_7_line_100 |  | 94 | 102 | 0.0013535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4261-5_0_7_line_101 |  | 95 | 99 | 0.029911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4261-5_0_7_line_102 |  | 96 | 106 | 0.020687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4261-5_0_7_line_103 |  | 97 | 98 | 0.054161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4261-5_0_7_line_104 |  | 98 | 99 | 0.046181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4261-5_0_7_line_105 |  | 100 | 101 | 0.0077414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4261-5_0_7_line_106 |  | 101 | 114 | 0.0016319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4261-5_0_7_line_107 |  | 102 | 109 | 0.013532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4261-5_0_7_line_108 |  | 103 | 104 | 0.020257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4261-5_0_7_line_109 |  | 104 | 105 | 0.0087552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4261-5_0_7_line_110 |  | 105 | 108 | 0.014361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4261-5_0_7_line_111 |  | 105 | 109 | 0.02737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4261-5_0_7_line_112 |  | 106 | 107 | 0.0029051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4261-5_0_7_line_113 |  | 107 | 110 | 0.021762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4261-5_0_7_line_114 |  | 109 | 111 | 0.023208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
115 | LV_4261-5_0_7_line_115 |  | 110 | 112 | 0.0096496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4261-5_0_7_line_116 |  | 111 | 122 | 0.0022904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
117 | LV_4261-5_0_7_line_117 |  | 113 | 114 | 0.009162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4261-5_0_7_line_118 |  | 115 | 116 | 0.020459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4261-5_0_7_line_119 |  | 116 | 117 | 0.020434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_4261-5_0_7_line_120 |  | 117 | 119 | 0.0040189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
121 | LV_4261-5_0_7_line_121 |  | 119 | 127 | 0.0096902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
122 | LV_4261-5_0_7_line_122 |  | 120 | 154 | 0.01687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
123 | LV_4261-5_0_7_line_123 |  | 121 | 142 | 0.017335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
124 | LV_4261-5_0_7_line_124 |  | 122 | 123 | 0.031965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
125 | LV_4261-5_0_7_line_125 |  | 123 | 124 | 0.022895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
126 | LV_4261-5_0_7_line_126 |  | 124 | 125 | 0.026942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
127 | LV_4261-5_0_7_line_127 |  | 124 | 126 | 0.067804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
128 | LV_4261-5_0_7_line_128 |  | 125 | 127 | 0.0094203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
129 | LV_4261-5_0_7_line_129 |  | 126 | 130 | 0.084386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4261-5_0_7_line_130 |  | 126 | 128 | 0.089566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
131 | LV_4261-5_0_7_line_131 |  | 128 | 129 | 0.065735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
132 | LV_4261-5_0_7_line_132 |  | 129 | 131 | 0.0033498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
133 | LV_4261-5_0_7_line_133 |  | 131 | 138 | 0.012017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
134 | LV_4261-5_0_7_line_134 |  | 132 | 133 | 0.015585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
135 | LV_4261-5_0_7_line_135 |  | 132 | 134 | 0.016161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
136 | LV_4261-5_0_7_line_136 |  | 133 | 135 | 0.0087061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
137 | LV_4261-5_0_7_line_137 |  | 134 | 136 | 0.0080465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
138 | LV_4261-5_0_7_line_138 |  | 135 | 137 | 0.0044653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
139 | LV_4261-5_0_7_line_139 |  | 136 | 138 | 0.0098739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
140 | LV_4261-5_0_7_line_140 |  | 137 | 139 | 0.016191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
141 | LV_4261-5_0_7_line_141 |  | 138 | 140 | 0.039072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
142 | LV_4261-5_0_7_line_142 |  | 139 | 141 | 0.0022619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
143 | LV_4261-5_0_7_line_143 |  | 140 | 149 | 0.0034748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
144 | LV_4261-5_0_7_line_144 |  | 141 | 142 | 0.019591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
145 | LV_4261-5_0_7_line_145 |  | 143 | 144 | 0.013308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4261-5_0_7_line_146 |  | 143 | 145 | 0.010647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4261-5_0_7_line_147 |  | 144 | 146 | 0.017418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4261-5_0_7_line_148 |  | 145 | 147 | 0.0095012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4261-5_0_7_line_149 |  | 146 | 148 | 0.0098819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4261-5_0_7_line_150 |  | 147 | 149 | 0.02638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4261-5_0_7_line_151 |  | 148 | 150 | 0.033735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4261-5_0_7_line_152 |  | 149 | 151 | 0.015424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4261-5_0_7_line_153 |  | 151 | 152 | 0.00042061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4261-5_0_7_line_154 |  | 152 | 153 | 0.018724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4261-5_0_7_line_155 |  | 154 | 193 | 0.0044391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4261-5_0_7_line_156 |  | 155 | 156 | 0.014664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4261-5_0_7_line_157 |  | 156 | 157 | 0.0073928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4261-5_0_7_line_158 |  | 156 | 158 | 0.034537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4261-5_0_7_line_159 |  | 157 | 159 | 0.0196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4261-5_0_7_line_160 |  | 158 | 160 | 0.015013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4261-5_0_7_line_161 |  | 158 | 161 | 0.031613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4261-5_0_7_line_162 |  | 159 | 163 | 0.016959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4261-5_0_7_line_163 |  | 160 | 167 | 0.017497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4261-5_0_7_line_164 |  | 161 | 168 | 0.020885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4261-5_0_7_line_165 |  | 162 | 163 | 0.016735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4261-5_0_7_line_166 |  | 164 | 165 | 0.042566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4261-5_0_7_line_167 |  | 164 | 166 | 0.012084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4261-5_0_7_line_168 |  | 166 | 170 | 0.0061028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4261-5_0_7_line_169 |  | 167 | 196 | 0.00048897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4261-5_0_7_line_170 |  | 168 | 188 | 0.0026947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4261-5_0_7_line_171 |  | 169 | 170 | 0.016361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4261-5_0_7_line_172 |  | 169 | 171 | 0.014766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4261-5_0_7_line_173 |  | 171 | 172 | 0.008286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4261-5_0_7_line_174 |  | 171 | 173 | 0.025014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4261-5_0_7_line_175 |  | 172 | 174 | 0.020972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4261-5_0_7_line_176 |  | 172 | 175 | 0.016185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4261-5_0_7_line_177 |  | 173 | 176 | 0.016495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_4261-5_0_7_line_178 |  | 173 | 177 | 0.029696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_4261-5_0_7_line_179 |  | 174 | 178 | 0.0063977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_4261-5_0_7_line_180 |  | 175 | 179 | 0.01915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_4261-5_0_7_line_181 |  | 176 | 180 | 0.011458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_4261-5_0_7_line_182 |  | 177 | 181 | 0.0099569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
183 | LV_4261-5_0_7_line_183 |  | 178 | 206 | 0.021414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
184 | LV_4261-5_0_7_line_184 |  | 180 | 182 | 0.0052506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
185 | LV_4261-5_0_7_line_185 |  | 181 | 193 | 0.01759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
186 | LV_4261-5_0_7_line_186 |  | 182 | 183 | 0.01459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_4261-5_0_7_line_187 |  | 183 | 184 | 0.014251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_4261-5_0_7_line_188 |  | 184 | 185 | 0.018015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_4261-5_0_7_line_189 |  | 185 | 186 | 0.006519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_4261-5_0_7_line_190 |  | 185 | 187 | 0.01082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_4261-5_0_7_line_191 |  | 186 | 194 | 0.027169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_4261-5_0_7_line_192 |  | 186 | 196 | 0.025844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
193 | LV_4261-5_0_7_line_193 |  | 187 | 195 | 0.022464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_4261-5_0_7_line_194 |  | 189 | 190 | 0.016024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_4261-5_0_7_line_195 |  | 189 | 191 | 0.0069229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_4261-5_0_7_line_196 |  | 190 | 192 | 0.022423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_4261-5_0_7_line_197 |  | 192 | 194 | 0.0023622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_4261-5_0_7_line_198 |  | 197 | 198 | 0.0395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_4261-5_0_7_line_199 |  | 197 | 199 | 0.016032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_4261-5_0_7_line_200 |  | 198 | 209 | 0.0015105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_4261-5_0_7_line_201 |  | 199 | 205 | 0.0021618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_4261-5_0_7_line_202 |  | 200 | 201 | 0.028969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_4261-5_0_7_line_203 |  | 201 | 206 | 0.014794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_4261-5_0_7_line_204 |  | 202 | 203 | 0.0080993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_4261-5_0_7_line_205 |  | 202 | 204 | 0.02221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_4261-5_0_7_line_206 |  | 204 | 205 | 0.0066496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_4261-5_0_7_line_207 |  | 207 | 208 | 0.015607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_4261-5_0_7_line_208 |  | 208 | 209 | 6.1705e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4261-5_0_7_trafo_139 | 0.63 MVA 20/0.4 kV | 210 | 149 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2634735.7206 | 1267502.8962 | 2634712.4985 | 1267497.4086
1 | 2634757.1107 | 1267507.951 | 2634735.7206 | 1267502.8962
2 | 2634698.5592 | 1267494.1145 | 2634712.4985 | 1267497.4086
3 | 2634761.0923 | 1267492.5967 | 2634757.1107 | 1267507.951
4 | 2634757.1107 | 1267507.951 | 2634752.998 | 1267534.09 | 2634752.8713 | 1267542.2949
5 | 2634698.5592 | 1267494.1145 | 2634696.357 | 1267493.5941
6 | 2634761.0923 | 1267492.5967 | 2634777.5435 | 1267497.302
7 | 2634761.0923 | 1267492.5967 | 2634763.4106 | 1267482.2971
8 | 2634752.8667 | 1267542.592 | 2634752.8713 | 1267542.2949
9 | 2634683.9853 | 1267490.6706 | 2634696.357 | 1267493.5941
10 | 2634777.5435 | 1267497.302 | 2634785.4408 | 1267499.5607
11 | 2634752.7106 | 1267553.1427 | 2634752.7184 | 1267552.2013 | 2634752.8667 | 1267542.592
12 | 2634683.9853 | 1267490.6706 | 2634670.8023 | 1267487.5552
13 | 2634785.4408 | 1267499.5607 | 2634796.3047 | 1267502.6679
14 | 2634752.64 | 1267561.6965 | 2634752.7106 | 1267553.1427
15 | 2634553.3613 | 1267498.6243 | 2634573.7698 | 1267493.0439
16 | 2634536.8115 | 1267503.8582 | 2634540.0875 | 1267502.2539 | 2634553.3613 | 1267498.6243
17 | 2634573.7698 | 1267493.0439 | 2634579.1838 | 1267491.5635 | 2634585.6825 | 1267489.9522
18 | 2634536.8115 | 1267503.8582 | 2634543.8229 | 1267547.2792
19 | 2634597.4099 | 1267487.0446 | 2634585.6825 | 1267489.9522
20 | 2634546.7814 | 1267572.3592 | 2634544.0827 | 1267548.8884 | 2634543.8229 | 1267547.2792
21 | 2634597.4099 | 1267487.0446 | 2634596.4392 | 1267471.5723
22 | 2634597.4099 | 1267487.0446 | 2634598.2066 | 1267493.3134
23 | 2634515.104 | 1267602.8722 | 2634515.6371 | 1267598.2688 | 2634515.7752 | 1267595.282
24 | 2634515.4807 | 1267619.8019 | 2634514.147 | 1267611.136 | 2634515.104 | 1267602.8722
25 | 2634546.7814 | 1267572.3592 | 2634548.0596 | 1267583.4751
26 | 2634596.4392 | 1267471.5723 | 2634606.3777 | 1267472.3309 | 2634626.8316 | 1267477.1644
27 | 2634515.4807 | 1267619.8019 | 2634515.5957 | 1267620.5494
28 | 2634552.0833 | 1267612.8223 | 2634548.5809 | 1267588.0093 | 2634548.0596 | 1267583.4751
29 | 2634670.8023 | 1267487.5552 | 2634661.9054 | 1267485.4528
30 | 2634652.9376 | 1267483.3336 | 2634661.9054 | 1267485.4528
31 | 2634635.7299 | 1267479.2672 | 2634652.9376 | 1267483.3336
32 | 2634635.7299 | 1267479.2672 | 2634626.8316 | 1267477.1644
33 | 2634603.9146 | 1267538.2303 | 2634608.7031 | 1267537.9804 | 2634621.5428 | 1267540.1726
34 | 2634603.9146 | 1267538.2303 | 2634605.847 | 1267555.6476
35 | 2634621.5428 | 1267540.1726 | 2634641.4418 | 1267543.57
36 | 2634605.847 | 1267555.6476 | 2634606.5023 | 1267561.5538
37 | 2635103.1271 | 1267700.675 | 2635093.1585 | 1267701.2732
38 | 2635063.9939 | 1267703.0234 | 2635093.1585 | 1267701.2732
39 | 2635130.2769 | 1267699.0457 | 2635103.1271 | 1267700.675
40 | 2635063.9939 | 1267703.0234 | 2635061.4609 | 1267702.8045
41 | 2635063.9939 | 1267703.0234 | 2635064.0782 | 1267715.1372
42 | 2635160.1116 | 1267697.2563 | 2635156.219 | 1267697.4889 | 2635130.2769 | 1267699.0457
43 | 2635061.4609 | 1267702.8045 | 2635048.3271 | 1267701.6694
44 | 2635064.128 | 1267722.2825 | 2635064.0782 | 1267715.1372
45 | 2635160.1116 | 1267697.2563 | 2635162.3407 | 1267710.1268
46 | 2635041.4785 | 1267701.0775 | 2635048.3271 | 1267701.6694
47 | 2635162.3407 | 1267710.1268 | 2635164.2447 | 1267721.1202 | 2635165.4328 | 1267751.489
48 | 2635041.4785 | 1267701.0775 | 2635037.4015 | 1267704.5003 | 2635029.5919 | 1267707.812
49 | 2635041.4785 | 1267701.0775 | 2635044.1915 | 1267695.4229 | 2635044.9772 | 1267686.201
50 | 2634800.0305 | 1267503.7335 | 2634796.3047 | 1267502.6679
51 | 2634752.64 | 1267561.6965 | 2634753.8546 | 1267572.0233
52 | 2634755.9877 | 1267590.1588 | 2634753.8546 | 1267572.0233
53 | 2634707.719 | 1267554.5454 | 2634682.5784 | 1267550.5433
54 | 2634682.5784 | 1267550.5433 | 2634682.3638 | 1267550.5091
55 | 2634755.9877 | 1267590.1588 | 2634766.0556 | 1267592.1722
56 | 2634755.9877 | 1267590.1588 | 2634757.2943 | 1267601.1035
57 | 2634682.3638 | 1267550.5091 | 2634678.233 | 1267549.8515 | 2634659.7127 | 1267546.6895
58 | 2634796.3733 | 1267598.2352 | 2634766.0556 | 1267592.1722
59 | 2634757.2943 | 1267601.1035 | 2634757.8611 | 1267605.8517
60 | 2634887.5417 | 1267602.3639 | 2634887.6763 | 1267589.7668 | 2634888.4061 | 1267565.2728
61 | 2634887.5417 | 1267602.3639 | 2634887.1953 | 1267634.2958
62 | 2634887.1953 | 1267634.2958 | 2634887.2884 | 1267650.027
63 | 2634887.1953 | 1267634.2958 | 2634844.4383 | 1267628.1084
64 | 2634887.2961 | 1267651.3372 | 2634887.2884 | 1267650.027
65 | 2634840.0964 | 1267627.4801 | 2634844.4383 | 1267628.1084
66 | 2634887.3988 | 1267668.6883 | 2634887.2961 | 1267651.3372
67 | 2635029.5919 | 1267707.812 | 2635030.5161 | 1267722.0499 | 2635029.3838 | 1267736.5177
68 | 2635029.5919 | 1267707.812 | 2635013.9873 | 1267713.3701
69 | 2635044.9772 | 1267686.201 | 2635046.2859 | 1267670.8397
70 | 2635027.4882 | 1267760.7375 | 2635029.3838 | 1267736.5177
71 | 2635001.4923 | 1267717.8207 | 2635013.9873 | 1267713.3701
72 | 2634516.8087 | 1267629.6847 | 2634516.2862 | 1267625.0362 | 2634515.5957 | 1267620.5494
73 | 2634516.8087 | 1267629.6847 | 2634518.1717 | 1267641.8107
74 | 2634518.1717 | 1267641.8107 | 2634518.2109 | 1267642.1597 | 2634519.7973 | 1267656.5484
75 | 2634519.7973 | 1267656.5484 | 2634520.3196 | 1267661.2857 | 2634522.5834 | 1267671.1395
76 | 2634526.6804 | 1267688.3816 | 2634523.4685 | 1267674.9917 | 2634522.5834 | 1267671.1395
77 | 2634530.7049 | 1267705.6519 | 2634527.1864 | 1267690.4911 | 2634526.6804 | 1267688.3816
78 | 2634530.7049 | 1267705.6519 | 2634531.3492 | 1267708.4283 | 2634535.0484 | 1267723.509
79 | 2634351.4539 | 1267892.0257 | 2634337.7529 | 1267906.6257
80 | 2634436.597 | 1267828.8178 | 2634417.7241 | 1267837.3141 | 2634396.3043 | 1267850.2433 | 2634374.2559 | 1267867.7277 | 2634351.4539 | 1267892.0257
81 | 2634557.5807 | 1267768.669 | 2634436.597 | 1267828.8178
82 | 2634570.4471 | 1267726.8253 | 2634566.113 | 1267731.7813 | 2634564.2488 | 1267735.2395 | 2634561.9696 | 1267747.8908 | 2634560.8079 | 1267752.1983 | 2634558.6375 | 1267759.1239 | 2634557.5807 | 1267768.669
83 | 2634557.5807 | 1267768.669 | 2634552.6905 | 1267760.6013 | 2634544.8076 | 1267749.4695 | 2634540.3304 | 1267741.5711 | 2634535.4954 | 1267725.3312 | 2634535.0484 | 1267723.509
84 | 2634570.4471 | 1267726.8253 | 2634573.2213 | 1267742.8085 | 2634576.0791 | 1267750.8874
85 | 2634570.4471 | 1267726.8253 | 2634570.4052 | 1267726.5834
86 | 2634552.0833 | 1267612.8223 | 2634555.0194 | 1267633.6233
87 | 2634556.205 | 1267642.0229 | 2634555.0194 | 1267633.6233
88 | 2634622.2295 | 1267611.8939 | 2634622.7138 | 1267613.2162 | 2634632.4298 | 1267640.1561
89 | 2634614.987 | 1267592.1226 | 2634622.2295 | 1267611.8939
90 | 2634645.2141 | 1267675.6037 | 2634632.4298 | 1267640.1561
91 | 2634614.987 | 1267592.1226 | 2634612.1457 | 1267585.0564 | 2634609.9626 | 1267578.3884
92 | 2634614.987 | 1267592.1226 | 2634623.8187 | 1267593.4994
93 | 2634645.2141 | 1267675.6037 | 2634658.8404 | 1267678.0326
94 | 2634645.2141 | 1267675.6037 | 2634638.4306 | 1267687.5392 | 2634640.9901 | 1267699.0179 | 2634641.3453 | 1267706.4698 | 2634631.8458 | 1267709.2273 | 2634625.1838 | 1267709.3995 | 2634620.7528 | 1267707.7613 | 2634617.6867 | 1267713.3807 | 2634617.0411 | 1267720.8156 | 2634617.2773 | 1267721.4686
95 | 2634609.9626 | 1267578.3884 | 2634607.5537 | 1267571.0306 | 2634606.5023 | 1267561.5538
96 | 2634623.8187 | 1267593.4994 | 2634630.3274 | 1267594.514 | 2634639.0081 | 1267595.9551
97 | 2634675.9367 | 1267681.0802 | 2634658.8404 | 1267678.0326
98 | 2634617.2773 | 1267721.4686 | 2634622.0035 | 1267734.5322 | 2634626.6242 | 1267743.6213 | 2634628.4328 | 1267747.977
99 | 2634646.5932 | 1267597.2142 | 2634639.0081 | 1267595.9551
100 | 2634675.9367 | 1267681.0802 | 2634677.2692 | 1267681.3177
101 | 2634631.3657 | 1267777.0508 | 2634629.6914 | 1267771.2146 | 2634630.5296 | 1267761.7572 | 2634631.1366 | 1267754.4889 | 2634628.4328 | 1267747.977
102 | 2634667.0382 | 1267600.3554 | 2634657.9609 | 1267599.1013 | 2634646.5932 | 1267597.2142
103 | 2634594.349 | 1267801.8076 | 2634592.6376 | 1267794.5924 | 2634582.8539 | 1267770.0398 | 2634576.0791 | 1267750.8874
104 | 2634594.349 | 1267801.8076 | 2634625.5229 | 1267776.1715 | 2634631.3657 | 1267777.0508
105 | 2634641.4418 | 1267543.57 | 2634649.0727 | 1267544.8729
106 | 2634650.6813 | 1267545.1475 | 2634649.0727 | 1267544.8729
107 | 2634690.6283 | 1267683.4643 | 2634683.9128 | 1267682.502 | 2634677.2692 | 1267681.3177
108 | 2634677.2419 | 1267638.76 | 2634678.6569 | 1267649.5365 | 2634682.9298 | 1267652.4747 | 2634686.8398 | 1267654.014
109 | 2634695.2273 | 1267656.483 | 2634688.9222 | 1267654.8337 | 2634686.8398 | 1267654.014
110 | 2634695.2273 | 1267656.483 | 2634709.4935 | 1267658.4681
111 | 2634695.2273 | 1267656.483 | 2634690.6283 | 1267683.4643
112 | 2634667.0382 | 1267600.3554 | 2634669.9067 | 1267600.8156
113 | 2634691.3935 | 1267604.2627 | 2634669.9067 | 1267600.8156
114 | 2634690.6283 | 1267683.4643 | 2634713.465 | 1267687.5969
115 | 2634700.9213 | 1267605.7912 | 2634691.3935 | 1267604.2627
116 | 2634715.7188 | 1267688.0047 | 2634713.465 | 1267687.5969
117 | 2634650.6813 | 1267545.1475 | 2634659.7127 | 1267546.6895
118 | 2634760.2839 | 1267626.1667 | 2634760.1626 | 1267625.1305 | 2634757.8611 | 1267605.8517
119 | 2634760.2839 | 1267626.1667 | 2634762.6596 | 1267646.4626
120 | 2634763.1269 | 1267650.4542 | 2634762.6596 | 1267646.4626
121 | 2634763.1269 | 1267650.4542 | 2634764.2535 | 1267660.0787
122 | 2635026.0044 | 1267777.5368 | 2635026.347 | 1267775.3189 | 2635027.4882 | 1267760.7375
123 | 2635001.4923 | 1267717.8207 | 2634985.162 | 1267723.6373
124 | 2634715.7188 | 1267688.0047 | 2634747.1725 | 1267693.6967
125 | 2634769.8696 | 1267695.9272 | 2634759.3402 | 1267695.8986 | 2634747.1725 | 1267693.6967
126 | 2634769.8696 | 1267695.9272 | 2634767.3651 | 1267686.6614 | 2634765.3487 | 1267669.4352
127 | 2634758.8288 | 1267747.0434 | 2634782.6761 | 1267734.9193 | 2634770.9293 | 1267700.0363 | 2634769.8696 | 1267695.9272
128 | 2634765.3487 | 1267669.4352 | 2634764.2535 | 1267660.0787
129 | 2634758.8288 | 1267747.0434 | 2634744.5102 | 1267721.9746 | 2634689.7126 | 1267713.0679
130 | 2634758.8288 | 1267747.0434 | 2634782.6761 | 1267734.9193 | 2634790.9922 | 1267750.3903 | 2634796.6112 | 1267761.1644 | 2634810.9786 | 1267779.1618 | 2634815.1243 | 1267788.3372
131 | 2634815.1243 | 1267788.3372 | 2634875.9153 | 1267763.326
132 | 2634875.9153 | 1267763.326 | 2634879.0132 | 1267762.0514
133 | 2634890.1263 | 1267757.4791 | 2634879.0132 | 1267762.0514
134 | 2634936.9155 | 1267740.8208 | 2634922.2337 | 1267746.048
135 | 2634907.0086 | 1267751.4685 | 2634922.2337 | 1267746.048
136 | 2634945.1173 | 1267737.9007 | 2634936.9155 | 1267740.8208
137 | 2634907.0086 | 1267751.4685 | 2634899.4282 | 1267754.1674
138 | 2634945.1173 | 1267737.9007 | 2634949.3237 | 1267736.4025
139 | 2634890.1263 | 1267757.4791 | 2634899.4282 | 1267754.1674
140 | 2634964.5761 | 1267730.9697 | 2634949.3237 | 1267736.4025
141 | 2634890.1263 | 1267757.4791 | 2634888.164 | 1267750.7405 | 2634887.939 | 1267718.6883
142 | 2634966.7068 | 1267730.2108 | 2634964.5761 | 1267730.9697
143 | 2634887.9145 | 1267715.2136 | 2634887.939 | 1267718.6883
144 | 2634966.7068 | 1267730.2108 | 2634985.162 | 1267723.6373
145 | 2634887.3988 | 1267668.6883 | 2634874.2303 | 1267666.7636
146 | 2634887.3988 | 1267668.6883 | 2634887.5168 | 1267679.3343
147 | 2634856.9958 | 1267664.2445 | 2634874.2303 | 1267666.7636
148 | 2634887.5168 | 1267679.3343 | 2634887.6221 | 1267688.835
149 | 2634856.9958 | 1267664.2445 | 2634847.2178 | 1267662.8153
150 | 2634887.9145 | 1267715.2136 | 2634887.6221 | 1267688.835
151 | 2634813.8374 | 1267657.9363 | 2634847.2178 | 1267662.8153
152 | 2634887.9145 | 1267715.2136 | 2634883.5794 | 1267715.188 | 2634872.5991 | 1267713.6423
153 | 2634872.1826 | 1267713.5836 | 2634872.5991 | 1267713.6423
154 | 2634853.6413 | 1267710.9735 | 2634872.1826 | 1267713.5836
155 | 2635026.0044 | 1267777.5368 | 2635025.3266 | 1267781.9239
156 | 2634950.2377 | 1267934.8499 | 2634945.866 | 1267937.2147 | 2634936.3354 | 1267938.983
157 | 2634950.2377 | 1267934.8499 | 2634953.363 | 1267937.07 | 2634956.7045 | 1267938.2957
158 | 2634953.7136 | 1267900.6793 | 2634952.2061 | 1267929.0685 | 2634950.2377 | 1267934.8499
159 | 2634976.0858 | 1267938.8287 | 2634963.4474 | 1267939.7426 | 2634958.7852 | 1267939.059 | 2634956.7045 | 1267938.2957
160 | 2634953.7136 | 1267900.6793 | 2634954.2636 | 1267890.3974 | 2634954.6317 | 1267885.6952
161 | 2634953.7136 | 1267900.6793 | 2634929.969 | 1267899.2825 | 2634927.7187 | 1267898.0016 | 2634924.6505 | 1267893.7564
162 | 2634993.0004 | 1267937.6056 | 2634976.0858 | 1267938.8287
163 | 2634955.997 | 1267868.2519 | 2634954.6317 | 1267885.6952
164 | 2634913.8678 | 1267879.0105 | 2634919.1581 | 1267880.7054 | 2634918.0661 | 1267884.6462 | 2634924.6505 | 1267893.7564
165 | 2634993.0004 | 1267937.6056 | 2635009.692 | 1267936.3986
166 | 2635055.0179 | 1267899.2554 | 2635081.8996 | 1267898.3474 | 2635081.2189 | 1267882.6935
167 | 2635055.0179 | 1267899.2554 | 2635053.744 | 1267887.2386
168 | 2635053.744 | 1267887.2386 | 2635053.1006 | 1267881.1698
169 | 2634955.997 | 1267868.2519 | 2634956.0352 | 1267867.7644
170 | 2634911.3016 | 1267878.1883 | 2634913.8678 | 1267879.0105
171 | 2635051.3758 | 1267864.8998 | 2635053.1006 | 1267881.1698
172 | 2635047.6063 | 1267850.71 | 2635050.8696 | 1267860.125 | 2635051.3758 | 1267864.8998
173 | 2635047.6063 | 1267850.71 | 2635054.714 | 1267846.4157
174 | 2635047.6063 | 1267850.71 | 2635040.7626 | 1267848.5568 | 2635034.6323 | 1267844.1284 | 2635027.2011 | 1267836.9571
175 | 2635054.714 | 1267846.4157 | 2635070.7425 | 1267836.7037 | 2635072.5657 | 1267835.4179
176 | 2635054.714 | 1267846.4157 | 2635053.0844 | 1267830.3134
177 | 2635027.2011 | 1267836.9571 | 2635017.0908 | 1267839.9105 | 2635011.165 | 1267840.5642
178 | 2635027.2011 | 1267836.9571 | 2635022.5866 | 1267830.7586 | 2635020.1355 | 1267821.4375 | 2635021.0798 | 1267809.4122 | 2635021.1207 | 1267809.1477
179 | 2635077.7941 | 1267831.7308 | 2635072.5657 | 1267835.4179
180 | 2635053.0121 | 1267811.2855 | 2635052.1748 | 1267815.1671 | 2635052.6095 | 1267825.6216 | 2635053.0844 | 1267830.3134
181 | 2635011.165 | 1267840.5642 | 2634999.7765 | 1267841.8205 | 2634999.7765 | 1267841.8205
182 | 2635021.1207 | 1267809.1477 | 2635022.6409 | 1267799.3075
183 | 2635077.7941 | 1267831.7308 | 2635093.6507 | 1267833.237 | 2635098.9444 | 1267834.6777
184 | 2634994.5997 | 1267842.698 | 2634999.7765 | 1267841.8205
185 | 2635025.3266 | 1267781.9239 | 2635022.6409 | 1267799.3075
186 | 2634994.5997 | 1267842.698 | 2634988.4304 | 1267843.7437 | 2634980.0981 | 1267843.8611
187 | 2634980.0981 | 1267843.8611 | 2634980.0981 | 1267843.8611 | 2634979.7607 | 1267837.2767 | 2634972.1042 | 1267837.1523
188 | 2634954.0906 | 1267836.9136 | 2634960.3823 | 1267836.9619 | 2634972.1042 | 1267837.1523
189 | 2634954.0906 | 1267836.9136 | 2634952.1195 | 1267843.1286
190 | 2634954.0906 | 1267836.9136 | 2634954.3381 | 1267834.5133 | 2634954.4368 | 1267826.1073
191 | 2634952.1195 | 1267843.1286 | 2634947.4593 | 1267840.8328 | 2634926.0466 | 1267835.8959
192 | 2634952.1195 | 1267843.1286 | 2634954.6738 | 1267846.4683 | 2634956.3503 | 1267850.6034 | 2634956.4454 | 1267862.5236 | 2634956.0352 | 1267867.7644
193 | 2634954.4368 | 1267826.1073 | 2634954.7007 | 1267803.6453
194 | 2634886.2808 | 1267830.1085 | 2634890.1348 | 1267828.7414 | 2634894.598 | 1267828.7232 | 2634901.8823 | 1267830.3833
195 | 2634886.2808 | 1267830.1085 | 2634881.7583 | 1267824.867
196 | 2634923.7447 | 1267835.3658 | 2634901.8823 | 1267830.3833
197 | 2634923.7447 | 1267835.3658 | 2634923.9489 | 1267835.4123 | 2634926.0466 | 1267835.8959
198 | 2635167.6485 | 1267808.125 | 2635166.1044 | 1267768.6555
199 | 2635167.6485 | 1267808.125 | 2635154.6668 | 1267809.182 | 2635151.6652 | 1267809.3747
200 | 2635166.1044 | 1267768.6555 | 2635166.0453 | 1267767.1461
201 | 2635149.5078 | 1267809.5132 | 2635151.6652 | 1267809.3747
202 | 2635124.0471 | 1267868.3157 | 2635117.8081 | 1267862.7349 | 2635107.3172 | 1267845.0087
203 | 2635107.3172 | 1267845.0087 | 2635105.3268 | 1267841.6457 | 2635104.8559 | 1267837.2842 | 2635101.1273 | 1267835.2717 | 2635098.9444 | 1267834.6777
204 | 2635120.783 | 1267807.944 | 2635112.7309 | 1267807.0711
205 | 2635120.783 | 1267807.944 | 2635140.557 | 1267810.0877 | 2635142.8719 | 1267809.9391
206 | 2635149.5078 | 1267809.5132 | 2635142.8719 | 1267809.9391
207 | 2635166.0429 | 1267767.0845 | 2635165.4328 | 1267751.489
208 | 2635166.0453 | 1267767.1461 | 2635166.0429 | 1267767.0845

## bus_geodata
| x | y | coords
0 | 2634735.7206 | 1267502.8962
1 | 2634712.4985 | 1267497.4086
2 | 2634757.1107 | 1267507.951
3 | 2634698.5592 | 1267494.1145
4 | 2634761.0923 | 1267492.5967
5 | 2634752.8713 | 1267542.2949
6 | 2634696.357 | 1267493.5941
7 | 2634777.5435 | 1267497.302
8 | 2634763.4106 | 1267482.2971
9 | 2634752.8667 | 1267542.592
10 | 2634683.9853 | 1267490.6706
11 | 2634785.4408 | 1267499.5607
12 | 2634752.7106 | 1267553.1427
13 | 2634553.3613 | 1267498.6243
14 | 2634573.7698 | 1267493.0439
15 | 2634536.8115 | 1267503.8582
16 | 2634585.6825 | 1267489.9522
17 | 2634543.8229 | 1267547.2792
18 | 2634597.4099 | 1267487.0446
19 | 2634515.7752 | 1267595.282
20 | 2634515.104 | 1267602.8722
21 | 2634546.7814 | 1267572.3592
22 | 2634596.4392 | 1267471.5723
23 | 2634598.2066 | 1267493.3134
24 | 2634515.4807 | 1267619.8019
25 | 2634548.0596 | 1267583.4751
26 | 2634670.8023 | 1267487.5552
27 | 2634661.9054 | 1267485.4528
28 | 2634652.9376 | 1267483.3336
29 | 2634635.7299 | 1267479.2672
30 | 2634626.8316 | 1267477.1644
31 | 2634603.9146 | 1267538.2303
32 | 2634621.5428 | 1267540.1726
33 | 2634605.847 | 1267555.6476
34 | 2635093.1585 | 1267701.2732
35 | 2635103.1271 | 1267700.675
36 | 2635063.9939 | 1267703.0234
37 | 2635130.2769 | 1267699.0457
38 | 2635061.4609 | 1267702.8045
39 | 2635064.0782 | 1267715.1372
40 | 2635160.1116 | 1267697.2563
41 | 2635048.3271 | 1267701.6694
42 | 2635064.128 | 1267722.2825
43 | 2635162.3407 | 1267710.1268
44 | 2635041.4785 | 1267701.0775
45 | 2634796.3047 | 1267502.6679
46 | 2634752.64 | 1267561.6965
47 | 2634753.8546 | 1267572.0233
48 | 2634800.0305 | 1267503.7335
49 | 2634707.719 | 1267554.5454
50 | 2634682.5784 | 1267550.5433
51 | 2634755.9877 | 1267590.1588
52 | 2634682.3638 | 1267550.5091
53 | 2634766.0556 | 1267592.1722
54 | 2634757.2943 | 1267601.1035
55 | 2634888.4061 | 1267565.2728
56 | 2634887.5417 | 1267602.3639
57 | 2634887.1953 | 1267634.2958
58 | 2634887.2883 | 1267650.027
59 | 2634844.4383 | 1267628.1084
60 | 2634887.2961 | 1267651.3372
61 | 2634840.0964 | 1267627.4801
62 | 2635029.5919 | 1267707.812
63 | 2635044.9772 | 1267686.201
64 | 2635029.3838 | 1267736.5177
65 | 2635013.9873 | 1267713.3701
66 | 2635046.2859 | 1267670.8397
67 | 2634515.5957 | 1267620.5494
68 | 2634516.8087 | 1267629.6847
69 | 2634518.1717 | 1267641.8107
70 | 2634519.7973 | 1267656.5484
71 | 2634522.5834 | 1267671.1395
72 | 2634526.6804 | 1267688.3816
73 | 2634530.7049 | 1267705.6519
74 | 2634351.4539 | 1267892.0257
75 | 2634337.7529 | 1267906.6257
76 | 2634436.597 | 1267828.8178
77 | 2634557.5807 | 1267768.669
78 | 2634570.4471 | 1267726.8253
79 | 2634535.0484 | 1267723.509
80 | 2634552.0833 | 1267612.8223
81 | 2634555.0194 | 1267633.6233
82 | 2634556.205 | 1267642.0229
83 | 2634570.4052 | 1267726.5834
84 | 2634622.2295 | 1267611.8939
85 | 2634632.4298 | 1267640.1561
86 | 2634614.987 | 1267592.1226
87 | 2634645.2141 | 1267675.6037
88 | 2634609.9626 | 1267578.3884
89 | 2634623.8187 | 1267593.4994
90 | 2634658.8404 | 1267678.0326
91 | 2634617.2773 | 1267721.4686
92 | 2634606.5023 | 1267561.5538
93 | 2634639.0081 | 1267595.9551
94 | 2634675.9367 | 1267681.0802
95 | 2634628.4328 | 1267747.977
96 | 2634646.5932 | 1267597.2142
97 | 2634576.0791 | 1267750.8874
98 | 2634594.349 | 1267801.8076
99 | 2634631.3657 | 1267777.0508
100 | 2634641.4418 | 1267543.57
101 | 2634649.0727 | 1267544.8729
102 | 2634677.2692 | 1267681.3177
103 | 2634677.2419 | 1267638.76
104 | 2634686.8398 | 1267654.014
105 | 2634695.2273 | 1267656.483
106 | 2634667.0382 | 1267600.3554
107 | 2634669.9067 | 1267600.8156
108 | 2634709.4935 | 1267658.4681
109 | 2634690.6283 | 1267683.4643
110 | 2634691.3935 | 1267604.2627
111 | 2634713.465 | 1267687.5969
112 | 2634700.9213 | 1267605.7912
113 | 2634659.7127 | 1267546.6895
114 | 2634650.6813 | 1267545.1475
115 | 2634757.8611 | 1267605.8517
116 | 2634760.2839 | 1267626.1667
117 | 2634762.6596 | 1267646.4626
118 | 2634796.3733 | 1267598.2352
119 | 2634763.1269 | 1267650.4542
120 | 2635027.4882 | 1267760.7375
121 | 2635001.4923 | 1267717.8207
122 | 2634715.7188 | 1267688.0047
123 | 2634747.1725 | 1267693.6967
124 | 2634769.8696 | 1267695.9272
125 | 2634765.3487 | 1267669.4352
126 | 2634758.8288 | 1267747.0434
127 | 2634764.2535 | 1267660.0787
128 | 2634815.1243 | 1267788.3372
129 | 2634875.9153 | 1267763.326
130 | 2634689.7126 | 1267713.0679
131 | 2634879.0132 | 1267762.0514
132 | 2634922.2337 | 1267746.048
133 | 2634936.9155 | 1267740.8208
134 | 2634907.0086 | 1267751.4685
135 | 2634945.1173 | 1267737.9007
136 | 2634899.4282 | 1267754.1674
137 | 2634949.3237 | 1267736.4025
138 | 2634890.1263 | 1267757.4791
139 | 2634964.5761 | 1267730.9698
140 | 2634887.939 | 1267718.6883
141 | 2634966.7068 | 1267730.2108
142 | 2634985.162 | 1267723.6373
143 | 2634887.3988 | 1267668.6883
144 | 2634874.2303 | 1267666.7636
145 | 2634887.5168 | 1267679.3343
146 | 2634856.9958 | 1267664.2445
147 | 2634887.6221 | 1267688.835
148 | 2634847.2178 | 1267662.8153
149 | 2634887.9145 | 1267715.2136
150 | 2634813.8374 | 1267657.9363
151 | 2634872.5991 | 1267713.6423
152 | 2634872.1826 | 1267713.5836
153 | 2634853.6413 | 1267710.9735
154 | 2635026.0044 | 1267777.5368
155 | 2634936.3354 | 1267938.983
156 | 2634950.2377 | 1267934.8499
157 | 2634956.7045 | 1267938.2957
158 | 2634953.7136 | 1267900.6793
159 | 2634976.0858 | 1267938.8287
160 | 2634954.6317 | 1267885.6952
161 | 2634924.6505 | 1267893.7565
162 | 2635009.692 | 1267936.3986
163 | 2634993.0004 | 1267937.6056
164 | 2635055.0179 | 1267899.2554
165 | 2635081.2189 | 1267882.6935
166 | 2635053.744 | 1267887.2386
167 | 2634955.997 | 1267868.2519
168 | 2634913.8678 | 1267879.0105
169 | 2635051.3758 | 1267864.8998
170 | 2635053.1006 | 1267881.1698
171 | 2635047.6063 | 1267850.71
172 | 2635054.714 | 1267846.4157
173 | 2635027.2011 | 1267836.9571
174 | 2635072.5657 | 1267835.4179
175 | 2635053.0844 | 1267830.3134
176 | 2635011.165 | 1267840.5642
177 | 2635021.1207 | 1267809.1477
178 | 2635077.7941 | 1267831.7308
179 | 2635053.0121 | 1267811.2855
180 | 2634999.7765 | 1267841.8205
181 | 2635022.6409 | 1267799.3075
182 | 2634994.5997 | 1267842.698
183 | 2634980.0981 | 1267843.8611
184 | 2634972.1042 | 1267837.1523
185 | 2634954.0906 | 1267836.9136
186 | 2634952.1195 | 1267843.1286
187 | 2634954.4368 | 1267826.1073
188 | 2634911.3016 | 1267878.1883
189 | 2634886.2808 | 1267830.1085
190 | 2634901.8823 | 1267830.3833
191 | 2634881.7583 | 1267824.867
192 | 2634923.7447 | 1267835.3658
193 | 2635025.3266 | 1267781.9239
194 | 2634926.0466 | 1267835.8959
195 | 2634954.7007 | 1267803.6453
196 | 2634956.0352 | 1267867.7644
197 | 2635167.6485 | 1267808.125
198 | 2635166.1044 | 1267768.6555
199 | 2635151.6652 | 1267809.3747
200 | 2635124.0471 | 1267868.3157
201 | 2635107.3172 | 1267845.0087
202 | 2635120.783 | 1267807.944
203 | 2635112.7309 | 1267807.0711
204 | 2635142.8719 | 1267809.9391
205 | 2635149.5078 | 1267809.5132
206 | 2635098.9444 | 1267834.6777
207 | 2635165.4328 | 1267751.489
208 | 2635166.0429 | 1267767.0845
209 | 2635166.0453 | 1267767.1461
210 | 2634852.9119 | 1267710.8709

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1