## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4271-15_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4271-15_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4271-15_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4271-15_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4271-15_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4271-15_0_7_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_4271-15_0_7_node_55 | 0.4 | n |  | TRUE
7 | bus_LV_4271-15_0_7_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_4271-15_0_7_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_4271-15_0_7_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_4271-15_0_7_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_4271-15_0_7_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_4271-15_0_7_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_4271-15_0_7_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_4271-15_0_7_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_4271-15_0_7_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_4271-15_0_7_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_4271-15_0_7_node_57 | 0.4 | n |  | TRUE
18 | bus_LV_4271-15_0_7_node_58 | 0.4 | n |  | TRUE
19 | bus_LV_4271-15_0_7_node_56 | 0.4 | n |  | TRUE
20 | bus_LV_4271-15_0_7_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_4271-15_0_7_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_4271-15_0_7_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_4271-15_0_7_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_4271-15_0_7_node_184 | 0.4 | n |  | TRUE
25 | bus_LV_4271-15_0_7_node_187 | 0.4 | n |  | TRUE
26 | bus_LV_4271-15_0_7_node_82 | 0.4 | n |  | TRUE
27 | bus_LV_4271-15_0_7_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_4271-15_0_7_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_4271-15_0_7_node_92 | 0.4 | n |  | TRUE
30 | bus_LV_4271-15_0_7_node_50 | 0.4 | n |  | TRUE
31 | bus_LV_4271-15_0_7_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_4271-15_0_7_node_27 | 0.4 | n |  | TRUE
33 | bus_LV_4271-15_0_7_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_4271-15_0_7_node_69 | 0.4 | n |  | TRUE
35 | bus_LV_4271-15_0_7_node_68 | 0.4 | n |  | TRUE
36 | bus_LV_4271-15_0_7_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_4271-15_0_7_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_4271-15_0_7_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_4271-15_0_7_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_4271-15_0_7_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_4271-15_0_7_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_4271-15_0_7_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_4271-15_0_7_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_4271-15_0_7_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_4271-15_0_7_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_4271-15_0_7_node_49 | 0.4 | n |  | TRUE
47 | bus_LV_4271-15_0_7_node_67 | 0.4 | n |  | TRUE
48 | bus_LV_4271-15_0_7_node_119 | 0.4 | n |  | TRUE
49 | bus_LV_4271-15_0_7_node_38 | 0.4 | n |  | TRUE
50 | bus_LV_4271-15_0_7_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_4271-15_0_7_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_4271-15_0_7_node_64 | 0.4 | n |  | TRUE
53 | bus_LV_4271-15_0_7_node_98 | 0.4 | n |  | TRUE
54 | bus_LV_4271-15_0_7_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_4271-15_0_7_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_4271-15_0_7_node_91 | 0.4 | n |  | TRUE
57 | bus_LV_4271-15_0_7_node_66 | 0.4 | n |  | TRUE
58 | bus_LV_4271-15_0_7_node_62 | 0.4 | n |  | TRUE
59 | bus_LV_4271-15_0_7_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_4271-15_0_7_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_4271-15_0_7_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_4271-15_0_7_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_4271-15_0_7_node_46 | 0.4 | n |  | TRUE
64 | bus_LV_4271-15_0_7_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_4271-15_0_7_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_4271-15_0_7_node_81 | 0.4 | n |  | TRUE
67 | bus_LV_4271-15_0_7_node_74 | 0.4 | n |  | TRUE
68 | bus_LV_4271-15_0_7_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_4271-15_0_7_node_53 | 0.4 | n |  | TRUE
70 | bus_LV_4271-15_0_7_node_107 | 0.4 | n |  | TRUE
71 | bus_LV_4271-15_0_7_node_171 | 0.4 | n |  | TRUE
72 | bus_LV_4271-15_0_7_node_83 | 0.4 | n |  | TRUE
73 | bus_LV_4271-15_0_7_node_97 | 0.4 | n |  | TRUE
74 | bus_LV_4271-15_0_7_node_172 | 0.4 | n |  | TRUE
75 | bus_LV_4271-15_0_7_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_4271-15_0_7_node_186 | 0.4 | n |  | TRUE
77 | bus_LV_4271-15_0_7_node_51 | 0.4 | n |  | TRUE
78 | bus_LV_4271-15_0_7_node_102 | 0.4 | n |  | TRUE
79 | bus_LV_4271-15_0_7_node_103 | 0.4 | n |  | TRUE
80 | bus_LV_4271-15_0_7_node_117 | 0.4 | n |  | TRUE
81 | bus_LV_4271-15_0_7_node_179 | 0.4 | n |  | TRUE
82 | bus_LV_4271-15_0_7_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_4271-15_0_7_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_4271-15_0_7_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_4271-15_0_7_node_87 | 0.4 | n |  | TRUE
86 | bus_LV_4271-15_0_7_node_88 | 0.4 | n |  | TRUE
87 | bus_LV_4271-15_0_7_node_59 | 0.4 | n |  | TRUE
88 | bus_LV_4271-15_0_7_node_60 | 0.4 | n |  | TRUE
89 | bus_LV_4271-15_0_7_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_4271-15_0_7_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_4271-15_0_7_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_4271-15_0_7_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_4271-15_0_7_node_70 | 0.4 | n |  | TRUE
94 | bus_LV_4271-15_0_7_node_71 | 0.4 | n |  | TRUE
95 | bus_LV_4271-15_0_7_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_4271-15_0_7_node_75 | 0.4 | n |  | TRUE
97 | bus_LV_4271-15_0_7_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_4271-15_0_7_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_4271-15_0_7_node_90 | 0.4 | n |  | TRUE
100 | bus_LV_4271-15_0_7_node_174 | 0.4 | n |  | TRUE
101 | bus_LV_4271-15_0_7_node_181 | 0.4 | n |  | TRUE
102 | bus_LV_4271-15_0_7_node_173 | 0.4 | n |  | TRUE
103 | bus_LV_4271-15_0_7_node_162 | 0.4 | n |  | TRUE
104 | bus_LV_4271-15_0_7_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_4271-15_0_7_node_145 | 0.4 | n |  | TRUE
106 | bus_LV_4271-15_0_7_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_4271-15_0_7_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_4271-15_0_7_node_94 | 0.4 | n |  | TRUE
109 | bus_LV_4271-15_0_7_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_4271-15_0_7_node_106 | 0.4 | n |  | TRUE
111 | bus_LV_4271-15_0_7_node_131 | 0.4 | n |  | TRUE
112 | bus_LV_4271-15_0_7_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_4271-15_0_7_node_101 | 0.4 | n |  | TRUE
114 | bus_LV_4271-15_0_7_node_113 | 0.4 | n |  | TRUE
115 | bus_LV_4271-15_0_7_node_114 | 0.4 | n |  | TRUE
116 | bus_LV_4271-15_0_7_node_104 | 0.4 | n |  | TRUE
117 | bus_LV_4271-15_0_7_node_108 | 0.4 | n |  | TRUE
118 | bus_LV_4271-15_0_7_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_4271-15_0_7_node_110 | 0.4 | n |  | TRUE
120 | bus_LV_4271-15_0_7_node_111 | 0.4 | n |  | TRUE
121 | bus_LV_4271-15_0_7_node_112 | 0.4 | n |  | TRUE
122 | bus_LV_4271-15_0_7_node_141 | 0.4 | n |  | TRUE
123 | bus_LV_4271-15_0_7_node_138 | 0.4 | n |  | TRUE
124 | bus_LV_4271-15_0_7_node_115 | 0.4 | n |  | TRUE
125 | bus_LV_4271-15_0_7_node_146 | 0.4 | n |  | TRUE
126 | bus_LV_4271-15_0_7_node_147 | 0.4 | n |  | TRUE
127 | bus_LV_4271-15_0_7_node_116 | 0.4 | n |  | TRUE
128 | bus_LV_4271-15_0_7_node_118 | 0.4 | n |  | TRUE
129 | bus_LV_4271-15_0_7_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_4271-15_0_7_node_135 | 0.4 | n |  | TRUE
131 | bus_LV_4271-15_0_7_node_133 | 0.4 | n |  | TRUE
132 | bus_LV_4271-15_0_7_node_121 | 0.4 | n |  | TRUE
133 | bus_LV_4271-15_0_7_node_122 | 0.4 | n |  | TRUE
134 | bus_LV_4271-15_0_7_node_123 | 0.4 | n |  | TRUE
135 | bus_LV_4271-15_0_7_node_124 | 0.4 | n |  | TRUE
136 | bus_LV_4271-15_0_7_node_125 | 0.4 | n |  | TRUE
137 | bus_LV_4271-15_0_7_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_4271-15_0_7_node_185 | 0.4 | n |  | TRUE
139 | bus_LV_4271-15_0_7_node_132 | 0.4 | n |  | TRUE
140 | bus_LV_4271-15_0_7_node_126 | 0.4 | n |  | TRUE
141 | bus_LV_4271-15_0_7_node_127 | 0.4 | n |  | TRUE
142 | bus_LV_4271-15_0_7_node_128 | 0.4 | n |  | TRUE
143 | bus_LV_4271-15_0_7_node_129 | 0.4 | n |  | TRUE
144 | bus_LV_4271-15_0_7_node_130 | 0.4 | n |  | TRUE
145 | bus_LV_4271-15_0_7_node_169 | 0.4 | n |  | TRUE
146 | bus_LV_4271-15_0_7_node_170 | 0.4 | n |  | TRUE
147 | bus_LV_4271-15_0_7_node_168 | 0.4 | n |  | TRUE
148 | bus_LV_4271-15_0_7_node_180 | 0.4 | n |  | TRUE
149 | bus_LV_4271-15_0_7_node_136 | 0.4 | n |  | TRUE
150 | bus_LV_4271-15_0_7_node_137 | 0.4 | n |  | TRUE
151 | bus_LV_4271-15_0_7_node_139 | 0.4 | n |  | TRUE
152 | bus_LV_4271-15_0_7_node_140 | 0.4 | n |  | TRUE
153 | bus_LV_4271-15_0_7_node_151 | 0.4 | n |  | TRUE
154 | bus_LV_4271-15_0_7_node_153 | 0.4 | n |  | TRUE
155 | bus_LV_4271-15_0_7_node_149 | 0.4 | n |  | TRUE
156 | bus_LV_4271-15_0_7_node_152 | 0.4 | n |  | TRUE
157 | bus_LV_4271-15_0_7_node_156 | 0.4 | n |  | TRUE
158 | bus_LV_4271-15_0_7_node_182 | 0.4 | n |  | TRUE
159 | bus_LV_4271-15_0_7_node_148 | 0.4 | n |  | TRUE
160 | bus_LV_4271-15_0_7_node_142 | 0.4 | n |  | TRUE
161 | bus_LV_4271-15_0_7_node_143 | 0.4 | n |  | TRUE
162 | bus_LV_4271-15_0_7_node_144 | 0.4 | n |  | TRUE
163 | bus_LV_4271-15_0_7_node_158 | 0.4 | n |  | TRUE
164 | bus_LV_4271-15_0_7_node_161 | 0.4 | n |  | TRUE
165 | bus_LV_4271-15_0_7_node_150 | 0.4 | n |  | TRUE
166 | bus_LV_4271-15_0_7_node_154 | 0.4 | n |  | TRUE
167 | bus_LV_4271-15_0_7_node_155 | 0.4 | n |  | TRUE
168 | bus_LV_4271-15_0_7_node_157 | 0.4 | n |  | TRUE
169 | bus_LV_4271-15_0_7_node_159 | 0.4 | n |  | TRUE
170 | bus_LV_4271-15_0_7_node_160 | 0.4 | n |  | TRUE
171 | bus_LV_4271-15_0_7_node_163 | 0.4 | n |  | TRUE
172 | bus_LV_4271-15_0_7_node_164 | 0.4 | n |  | TRUE
173 | bus_LV_4271-15_0_7_node_165 | 0.4 | n |  | TRUE
174 | bus_LV_4271-15_0_7_node_166 | 0.4 | n |  | TRUE
175 | bus_LV_4271-15_0_7_node_167 | 0.4 | n |  | TRUE
176 | bus_LV_4271-15_0_7_node_183 | 0.4 | n |  | TRUE
177 | bus_LV_4271-15_0_7_node_177 | 0.4 | n |  | TRUE
178 | bus_LV_4271-15_0_7_node_175 | 0.4 | n |  | TRUE
179 | bus_LV_4271-15_0_7_node_176 | 0.4 | n |  | TRUE
180 | bus_LV_4271-15_0_7_node_178 | 0.4 | n |  | TRUE
181 | bus_MV_397_0_node_263 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4271-15_0_7_load_0 | 0 | 0.00071223 | 0.0001785 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4271-15_0_7_load_1 | 1 | 0.0012654 | 0.00031714 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4271-15_0_7_load_2 | 2 | 0.0011058 | 0.00027713 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4271-15_0_7_load_3 | 3 | 0.0010349 | 0.00025938 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4271-15_0_7_load_4 | 4 | 0.0010387 | 0.00026033 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4271-15_0_7_load_19 | 5 | 0.00252 | 0.00063158 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4271-15_0_7_load_5 | 7 | 0.0020173 | 0.00050559 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4271-15_0_7_load_12 | 8 | 0.00096232 | 0.00024118 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4271-15_0_7_load_15 | 9 | 0.00072084 | 0.00018066 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4271-15_0_7_load_11 | 10 | 0.00085855 | 0.00021517 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4271-15_0_7_load_16 | 11 | 0.0014386 | 0.00036054 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4271-15_0_7_load_6 | 12 | 0.0018479 | 0.00046313 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4271-15_0_7_load_8 | 14 | 0.002054 | 0.00051477 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4271-15_0_7_load_9 | 15 | 0.0020842 | 0.00052234 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4271-15_0_7_load_10 | 16 | 0.0013846 | 0.00034703 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4271-15_0_7_load_58 | 18 | 0.00054555 | 0.00013673 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4271-15_0_7_load_56 | 19 | 0.002545 | 0.00063783 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4271-15_0_7_load_22 | 21 | 0.0019028 | 0.00047688 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4271-15_0_7_load_23 | 22 | 0.0017317 | 0.000434 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4271-15_0_7_load_17 | 23 | 0.0032494 | 0.00081439 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4271-15_0_7_load_187 | 25 | 0.0039324 | 0.00098555 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4271-15_0_7_load_20 | 27 | 0.0016507 | 0.00041369 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4271-15_0_7_load_21 | 28 | 0.0016374 | 0.00041038 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4271-15_0_7_load_92 | 29 | 0.018915 | 0.0047406 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4271-15_0_7_load_26 | 31 | 0.0021571 | 0.00054063 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4271-15_0_7_load_27 | 32 | 0.001253 | 0.00031404 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4271-15_0_7_load_28 | 33 | 0.0013794 | 0.00034572 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4271-15_0_7_load_69 | 34 | 0.0025912 | 0.00064942 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4271-15_0_7_load_68 | 35 | 0.0013122 | 0.00032886 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4271-15_0_7_load_29 | 36 | 0.0050869 | 0.0012749 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4271-15_0_7_load_32 | 39 | 0.0010368 | 0.00025985 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4271-15_0_7_load_34 | 40 | 0.0042646 | 0.0010688 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4271-15_0_7_load_100 | 45 | 0.0027287 | 0.00068388 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4271-15_0_7_load_67 | 47 | 0.015144 | 0.0037954 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4271-15_0_7_load_119 | 48 | 0.0014662 | 0.00036746 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4271-15_0_7_load_40 | 50 | 0.00083985 | 0.00021049 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4271-15_0_7_load_36 | 51 | 0.00574 | 0.0014386 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4271-15_0_7_load_98 | 53 | 0.0029032 | 0.0007276 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4271-15_0_7_load_91 | 56 | 0.0028416 | 0.00071218 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4271-15_0_7_load_66 | 57 | 0.002696 | 0.00067567 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4271-15_0_7_load_62 | 58 | 0.00074349 | 0.00018634 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4271-15_0_7_load_42 | 59 | 0.024925 | 0.0062469 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4271-15_0_7_load_74 | 67 | 0.005468 | 0.0013704 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4271-15_0_7_load_53 | 69 | 0.024329 | 0.0060975 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4271-15_0_7_load_107 | 70 | 0.025175 | 0.0063095 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4271-15_0_7_load_171 | 71 | 0.0038789 | 0.00097213 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4271-15_0_7_load_97 | 73 | 0.009362 | 0.0023463 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4271-15_0_7_load_172 | 74 | 0.0092941 | 0.0023293 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4271-15_0_7_load_186 | 76 | 0.0032871 | 0.00082382 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4271-15_0_7_load_102 | 78 | 0.025435 | 0.0063747 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4271-15_0_7_load_117 | 80 | 0.0015035 | 0.00037682 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4271-15_0_7_load_179 | 81 | 0.0024073 | 0.00060334 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4271-15_0_7_load_79 | 83 | 0.0023576 | 0.00059088 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4271-15_0_7_load_78 | 84 | 0.0080616 | 0.0020204 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4271-15_0_7_load_87 | 85 | 0.00057331 | 0.00014368 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4271-15_0_7_load_88 | 86 | 0.00081921 | 0.00020531 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4271-15_0_7_load_59 | 87 | 0.0091998 | 0.0023057 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4271-15_0_7_load_60 | 88 | 0.0085459 | 0.0021418 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4271-15_0_7_load_61 | 89 | 0.0090725 | 0.0022738 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4271-15_0_7_load_63 | 90 | 0.0017571 | 0.00044036 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4271-15_0_7_load_84 | 91 | 0.001584 | 0.000397 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4271-15_0_7_load_85 | 92 | 0.0013825 | 0.00034648 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4271-15_0_7_load_70 | 93 | 0.001413 | 0.00035413 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4271-15_0_7_load_77 | 95 | 0.0013824 | 0.00034646 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4271-15_0_7_load_75 | 96 | 0.0010636 | 0.00026657 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4271-15_0_7_load_89 | 97 | 0.0015834 | 0.00039683 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4271-15_0_7_load_76 | 98 | 0.0043802 | 0.0010978 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4271-15_0_7_load_90 | 99 | 0.0023497 | 0.00058889 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4271-15_0_7_load_173 | 102 | 0.0071036 | 0.0017803 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4271-15_0_7_load_162 | 103 | 0.008759 | 0.0021952 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4271-15_0_7_load_95 | 104 | 0.0019768 | 0.00049542 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4271-15_0_7_load_86 | 106 | 0.0020615 | 0.00051666 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4271-15_0_7_load_93 | 107 | 0.018828 | 0.0047188 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4271-15_0_7_load_94 | 108 | 0.004627 | 0.0011596 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4271-15_0_7_load_96 | 109 | 0.0023352 | 0.00058525 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4271-15_0_7_load_131 | 111 | 0.0040577 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4271-15_0_7_load_99 | 112 | 0.0014031 | 0.00035165 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4271-15_0_7_load_101 | 113 | 0.0022503 | 0.00056398 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4271-15_0_7_load_113 | 114 | 0.0019136 | 0.0004796 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4271-15_0_7_load_114 | 115 | 0.0022259 | 0.00055786 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4271-15_0_7_load_108 | 117 | 0.0013367 | 0.00033501 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4271-15_0_7_load_109 | 118 | 0.0015856 | 0.00039739 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4271-15_0_7_load_110 | 119 | 0.0014219 | 0.00035635 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4271-15_0_7_load_111 | 120 | 0.0018255 | 0.00045751 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4271-15_0_7_load_112 | 121 | 0.0014406 | 0.00036106 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4271-15_0_7_load_141 | 122 | 0.0014232 | 0.00035668 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4271-15_0_7_load_115 | 124 | 0.0028837 | 0.00072273 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4271-15_0_7_load_146 | 125 | 0.0020099 | 0.00050372 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4271-15_0_7_load_147 | 126 | 0.0017709 | 0.00044384 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4271-15_0_7_load_116 | 127 | 0.0017522 | 0.00043913 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4271-15_0_7_load_118 | 128 | 0.0019396 | 0.00048611 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4271-15_0_7_load_120 | 129 | 0.0019141 | 0.00047972 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4271-15_0_7_load_135 | 130 | 0.0011382 | 0.00028526 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4271-15_0_7_load_133 | 131 | 0.0017899 | 0.0004486 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4271-15_0_7_load_121 | 132 | 0.0015895 | 0.00039836 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4271-15_0_7_load_122 | 133 | 0.0015759 | 0.00039496 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4271-15_0_7_load_123 | 134 | 0.002944 | 0.00073784 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4271-15_0_7_load_124 | 135 | 0.0016625 | 0.00041667 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4271-15_0_7_load_125 | 136 | 0.0019323 | 0.00048429 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4271-15_0_7_load_134 | 137 | 0.0027542 | 0.00069026 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4271-15_0_7_load_185 | 138 | 0.0021758 | 0.0005453 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4271-15_0_7_load_132 | 139 | 0.0022471 | 0.00056317 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4271-15_0_7_load_126 | 140 | 0.0027323 | 0.00068477 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4271-15_0_7_load_127 | 141 | 0.0043084 | 0.0010798 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4271-15_0_7_load_128 | 142 | 0.0034946 | 0.00087584 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4271-15_0_7_load_129 | 143 | 0.003044 | 0.0007629 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4271-15_0_7_load_170 | 146 | 0.001647 | 0.00041278 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4271-15_0_7_load_168 | 147 | 0.0030129 | 0.00075509 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4271-15_0_7_load_180 | 148 | 0.0045952 | 0.0011517 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4271-15_0_7_load_136 | 149 | 0.0015884 | 0.00039808 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4271-15_0_7_load_137 | 150 | 0.0014776 | 0.00037031 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4271-15_0_7_load_139 | 151 | 0.001888 | 0.00047318 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4271-15_0_7_load_151 | 153 | 0.0067047 | 0.0016804 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4271-15_0_7_load_149 | 155 | 0.0014271 | 0.00035768 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4271-15_0_7_load_152 | 156 | 0.0014868 | 0.00037263 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4271-15_0_7_load_182 | 158 | 0.0099757 | 0.0025001 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4271-15_0_7_load_148 | 159 | 0.0015583 | 0.00039056 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4271-15_0_7_load_142 | 160 | 0.002604 | 0.00065261 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4271-15_0_7_load_143 | 161 | 0.0014915 | 0.00037381 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4271-15_0_7_load_144 | 162 | 0.0023821 | 0.00059701 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4271-15_0_7_load_161 | 164 | 0.0021279 | 0.0005333 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4271-15_0_7_load_150 | 165 | 0.0017051 | 0.00042735 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4271-15_0_7_load_154 | 166 | 0.0015084 | 0.00037804 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4271-15_0_7_load_155 | 167 | 0.0017088 | 0.00042826 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4271-15_0_7_load_157 | 168 | 0.0013711 | 0.00034364 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4271-15_0_7_load_159 | 169 | 0.010407 | 0.0026083 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4271-15_0_7_load_160 | 170 | 0.0082192 | 0.0020599 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4271-15_0_7_load_163 | 171 | 0.0023233 | 0.00058226 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4271-15_0_7_load_164 | 172 | 0.0026987 | 0.00067637 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4271-15_0_7_load_165 | 173 | 0.0031111 | 0.0007797 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4271-15_0_7_load_166 | 174 | 0.0022983 | 0.00057602 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4271-15_0_7_load_167 | 175 | 0.0027771 | 0.000696 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4271-15_0_7_load_183 | 176 | 0.0012746 | 0.00031944 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4271-15_0_7_load_177 | 177 | 0.0016084 | 0.00040311 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4271-15_0_7_load_175 | 178 | 0.0010805 | 0.0002708 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4271-15_0_7_load_176 | 179 | 0.0024499 | 0.000614 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4271-15_0_7_load_178 | 180 | 0.0080757 | 0.002024 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 62 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4271-15_0_7_line_0 |  | 0 | 1 | 0.0090461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4271-15_0_7_line_1 |  | 0 | 2 | 0.0069965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4271-15_0_7_line_2 |  | 1 | 3 | 0.010494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4271-15_0_7_line_3 |  | 2 | 4 | 0.013803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4271-15_0_7_line_4 |  | 3 | 8 | 0.0055038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4271-15_0_7_line_5 |  | 4 | 9 | 0.004031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4271-15_0_7_line_6 |  | 5 | 6 | 0.070385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4271-15_0_7_line_7 |  | 5 | 7 | 0.11925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4271-15_0_7_line_8 |  | 6 | 29 | 0.029552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_4271-15_0_7_line_9 |  | 6 | 30 | 0.018592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_4271-15_0_7_line_10 |  | 7 | 12 | 0.029631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4271-15_0_7_line_11 |  | 7 | 13 | 0.0161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4271-15_0_7_line_12 |  | 8 | 10 | 0.015601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4271-15_0_7_line_13 |  | 9 | 11 | 0.015897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4271-15_0_7_line_14 |  | 10 | 14 | 0.016344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4271-15_0_7_line_15 |  | 11 | 20 | 0.0090187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4271-15_0_7_line_16 |  | 12 | 14 | 0.00020512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4271-15_0_7_line_17 |  | 13 | 15 | 0.0064399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4271-15_0_7_line_18 |  | 13 | 16 | 0.024499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4271-15_0_7_line_19 |  | 17 | 18 | 0.013047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4271-15_0_7_line_20 |  | 17 | 19 | 0.028841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4271-15_0_7_line_21 |  | 18 | 85 | 0.00036694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4271-15_0_7_line_22 |  | 19 | 50 | 0.014607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4271-15_0_7_line_23 |  | 20 | 21 | 0.018168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4271-15_0_7_line_24 |  | 20 | 22 | 0.018437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4271-15_0_7_line_25 |  | 21 | 28 | 0.0081356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4271-15_0_7_line_26 |  | 23 | 24 | 0.03848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4271-15_0_7_line_27 |  | 24 | 25 | 0.039039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_4271-15_0_7_line_28 |  | 24 | 26 | 0.02538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_4271-15_0_7_line_29 |  | 25 | 83 | 0.023921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_4271-15_0_7_line_30 |  | 26 | 71 | 0.013594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_4271-15_0_7_line_31 |  | 27 | 28 | 0.019831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4271-15_0_7_line_32 |  | 29 | 65 | 0.020842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_4271-15_0_7_line_33 |  | 30 | 46 | 0.00999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_4271-15_0_7_line_34 |  | 31 | 32 | 0.010679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4271-15_0_7_line_35 |  | 32 | 33 | 0.010614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4271-15_0_7_line_36 |  | 33 | 34 | 0.0080319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4271-15_0_7_line_37 |  | 34 | 35 | 0.011605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4271-15_0_7_line_38 |  | 35 | 93 | 0.019567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4271-15_0_7_line_39 |  | 36 | 37 | 0.037527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_4271-15_0_7_line_40 |  | 36 | 38 | 0.046711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_4271-15_0_7_line_41 |  | 37 | 39 | 0.019025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_4271-15_0_7_line_42 |  | 38 | 40 | 0.022651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_4271-15_0_7_line_43 |  | 38 | 41 | 0.017336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4271-15_0_7_line_44 |  | 39 | 42 | 0.012296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_4271-15_0_7_line_45 |  | 40 | 46 | 0.03618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_4271-15_0_7_line_46 |  | 41 | 47 | 0.007575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4271-15_0_7_line_47 |  | 42 | 48 | 0.022582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_4271-15_0_7_line_48 |  | 43 | 44 | 0.038622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_4271-15_0_7_line_49 |  | 43 | 45 | 0.014403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_4271-15_0_7_line_50 |  | 44 | 52 | 0.025098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_4271-15_0_7_line_51 |  | 44 | 49 | 0.025923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4271-15_0_7_line_52 |  | 45 | 53 | 0.0078578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_4271-15_0_7_line_53 |  | 48 | 80 | 0.014394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_4271-15_0_7_line_54 |  | 49 | 50 | 0.0054403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4271-15_0_7_line_55 |  | 49 | 51 | 0.015834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4271-15_0_7_line_56 |  | 51 | 54 | 0.016234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4271-15_0_7_line_57 |  | 52 | 57 | 0.0084131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_4271-15_0_7_line_58 |  | 52 | 58 | 0.022514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4271-15_0_7_line_59 |  | 53 | 112 | 0.016478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_4271-15_0_7_line_60 |  | 54 | 55 | 0.02678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4271-15_0_7_line_61 |  | 55 | 56 | 0.0075124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4271-15_0_7_line_62 |  | 57 | 91 | 0.0051532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_4271-15_0_7_line_63 |  | 58 | 90 | 0.021275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4271-15_0_7_line_64 |  | 59 | 60 | 0.02175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4271-15_0_7_line_65 |  | 60 | 64 | 0.029454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_4271-15_0_7_line_66 |  | 60 | 65 | 0.008913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_4271-15_0_7_line_67 |  | 61 | 62 | 0.026686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_4271-15_0_7_line_68 |  | 61 | 63 | 0.013544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
69 | LV_4271-15_0_7_line_69 |  | 62 | 66 | 0.047088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4271-15_0_7_line_70 |  | 62 | 67 | 0.027386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_4271-15_0_7_line_71 |  | 63 | 68 | 0.039983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_4271-15_0_7_line_72 |  | 64 | 69 | 0.026695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_4271-15_0_7_line_73 |  | 66 | 70 | 0.0067851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4271-15_0_7_line_74 |  | 67 | 75 | 0.019932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_4271-15_0_7_line_75 |  | 68 | 76 | 0.022253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4271-15_0_7_line_76 |  | 68 | 77 | 0.002457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_4271-15_0_7_line_77 |  | 69 | 77 | 0.035136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
78 | LV_4271-15_0_7_line_78 |  | 71 | 103 | 0.035125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_4271-15_0_7_line_79 |  | 72 | 73 | 0.015632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4271-15_0_7_line_80 |  | 72 | 74 | 0.017729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4271-15_0_7_line_81 |  | 73 | 104 | 0.044714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4271-15_0_7_line_82 |  | 74 | 105 | 0.006156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4271-15_0_7_line_83 |  | 75 | 82 | 0.020416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_4271-15_0_7_line_84 |  | 75 | 89 | 0.003069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4271-15_0_7_line_85 |  | 76 | 81 | 0.035295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4271-15_0_7_line_86 |  | 78 | 79 | 0.022327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4271-15_0_7_line_87 |  | 79 | 116 | 0.030871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4271-15_0_7_line_88 |  | 80 | 127 | 0.0047995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_4271-15_0_7_line_89 |  | 81 | 116 | 0.017926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4271-15_0_7_line_90 |  | 82 | 83 | 0.005637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
91 | LV_4271-15_0_7_line_91 |  | 82 | 84 | 0.028772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4271-15_0_7_line_92 |  | 85 | 86 | 0.0066449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4271-15_0_7_line_93 |  | 87 | 88 | 0.019153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4271-15_0_7_line_94 |  | 88 | 89 | 0.013043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4271-15_0_7_line_95 |  | 91 | 92 | 0.011295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_4271-15_0_7_line_96 |  | 92 | 106 | 0.00088422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_4271-15_0_7_line_97 |  | 93 | 94 | 0.0042709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4271-15_0_7_line_98 |  | 94 | 95 | 0.014669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4271-15_0_7_line_99 |  | 94 | 96 | 0.022846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4271-15_0_7_line_100 |  | 95 | 97 | 0.011294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_4271-15_0_7_line_101 |  | 96 | 98 | 0.01171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4271-15_0_7_line_102 |  | 97 | 99 | 0.0005824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
103 | LV_4271-15_0_7_line_103 |  | 99 | 106 | 0.01859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
104 | LV_4271-15_0_7_line_104 |  | 100 | 101 | 0.048352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4271-15_0_7_line_105 |  | 100 | 102 | 0.031193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4271-15_0_7_line_106 |  | 101 | 148 | 0.022284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4271-15_0_7_line_107 |  | 101 | 144 | 0.066617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4271-15_0_7_line_108 |  | 102 | 156 | 0.022493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4271-15_0_7_line_109 |  | 103 | 170 | 0.0044366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
110 | LV_4271-15_0_7_line_110 |  | 105 | 163 | 0.015798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4271-15_0_7_line_111 |  | 105 | 161 | 0.0099392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4271-15_0_7_line_112 |  | 107 | 108 | 0.039797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4271-15_0_7_line_113 |  | 108 | 109 | 0.020053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4271-15_0_7_line_114 |  | 109 | 110 | 0.010478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4271-15_0_7_line_115 |  | 110 | 111 | 0.0062954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4271-15_0_7_line_116 |  | 111 | 116 | 0.005691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4271-15_0_7_line_117 |  | 112 | 113 | 0.0050245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
118 | LV_4271-15_0_7_line_118 |  | 113 | 114 | 0.015917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
119 | LV_4271-15_0_7_line_119 |  | 114 | 115 | 3.4469e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
120 | LV_4271-15_0_7_line_120 |  | 115 | 124 | 0.018762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
121 | LV_4271-15_0_7_line_121 |  | 117 | 118 | 0.00095302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4271-15_0_7_line_122 |  | 117 | 119 | 0.0056894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4271-15_0_7_line_123 |  | 118 | 120 | 0.0079135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4271-15_0_7_line_124 |  | 119 | 121 | 0.00038955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4271-15_0_7_line_125 |  | 121 | 122 | 0.0061596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4271-15_0_7_line_126 |  | 122 | 123 | 0.0043642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4271-15_0_7_line_127 |  | 123 | 152 | 0.024433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4271-15_0_7_line_128 |  | 123 | 149 | 0.00221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4271-15_0_7_line_129 |  | 124 | 125 | 0.0020426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
130 | LV_4271-15_0_7_line_130 |  | 125 | 126 | 0.019248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
131 | LV_4271-15_0_7_line_131 |  | 126 | 138 | 0.0055225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
132 | LV_4271-15_0_7_line_132 |  | 127 | 128 | 0.012361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
133 | LV_4271-15_0_7_line_133 |  | 128 | 129 | 0.0065072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
134 | LV_4271-15_0_7_line_134 |  | 129 | 130 | 0.01348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
135 | LV_4271-15_0_7_line_135 |  | 130 | 131 | 0.0083332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
136 | LV_4271-15_0_7_line_136 |  | 131 | 139 | 0.018072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
137 | LV_4271-15_0_7_line_137 |  | 132 | 133 | 0.021357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
138 | LV_4271-15_0_7_line_138 |  | 132 | 134 | 0.0079294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
139 | LV_4271-15_0_7_line_139 |  | 133 | 135 | 0.0068102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
140 | LV_4271-15_0_7_line_140 |  | 134 | 136 | 0.0094367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
141 | LV_4271-15_0_7_line_141 |  | 135 | 137 | 0.0052401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
142 | LV_4271-15_0_7_line_142 |  | 136 | 138 | 0.0086341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
143 | LV_4271-15_0_7_line_143 |  | 137 | 139 | 0.0027166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
144 | LV_4271-15_0_7_line_144 |  | 140 | 141 | 0.0051008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4271-15_0_7_line_145 |  | 140 | 142 | 0.00031769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4271-15_0_7_line_146 |  | 141 | 143 | 0.0057088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4271-15_0_7_line_147 |  | 142 | 144 | 0.023687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4271-15_0_7_line_148 |  | 144 | 145 | 0.018297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4271-15_0_7_line_149 |  | 145 | 146 | 0.03 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4271-15_0_7_line_150 |  | 145 | 147 | 0.021579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4271-15_0_7_line_151 |  | 146 | 176 | 0.011524 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4271-15_0_7_line_152 |  | 148 | 174 | 0.0010095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4271-15_0_7_line_153 |  | 149 | 150 | 0.0092402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4271-15_0_7_line_154 |  | 150 | 151 | 0.0068483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4271-15_0_7_line_155 |  | 151 | 153 | 0.005533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4271-15_0_7_line_156 |  | 152 | 154 | 0.003979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
157 | LV_4271-15_0_7_line_157 |  | 152 | 155 | 0.016077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4271-15_0_7_line_158 |  | 153 | 156 | 0.0013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4271-15_0_7_line_159 |  | 154 | 157 | 0.019063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
160 | LV_4271-15_0_7_line_160 |  | 154 | 158 | 0.017343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4271-15_0_7_line_161 |  | 155 | 159 | 0.0066077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4271-15_0_7_line_162 |  | 157 | 166 | 0.013343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4271-15_0_7_line_163 |  | 157 | 163 | 0.004973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
164 | LV_4271-15_0_7_line_164 |  | 159 | 165 | 0.0059862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4271-15_0_7_line_165 |  | 160 | 161 | 0.0091323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4271-15_0_7_line_166 |  | 160 | 162 | 0.009078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4271-15_0_7_line_167 |  | 163 | 164 | 0.026992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
168 | LV_4271-15_0_7_line_168 |  | 164 | 169 | 0.017187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
169 | LV_4271-15_0_7_line_169 |  | 166 | 167 | 0.0070151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4271-15_0_7_line_170 |  | 167 | 168 | 0.0066847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4271-15_0_7_line_171 |  | 169 | 170 | 0.020343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
172 | LV_4271-15_0_7_line_172 |  | 171 | 172 | 0.0023664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4271-15_0_7_line_173 |  | 171 | 173 | 0.019058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4271-15_0_7_line_174 |  | 172 | 174 | 0.020833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4271-15_0_7_line_175 |  | 173 | 175 | 0.0077369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4271-15_0_7_line_176 |  | 176 | 177 | 0.015511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4271-15_0_7_line_177 |  | 177 | 179 | 0.019298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_4271-15_0_7_line_178 |  | 178 | 179 | 0.020796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_4271-15_0_7_line_179 |  | 178 | 180 | 0.21326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4271-15_0_7_trafo_45 | 0.63 MVA 20/0.4 kV | 181 | 62 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2635555.0852 | 1242755.9569 | 2635551.6123 | 1242747.604
1 | 2635555.0852 | 1242755.9569 | 2635557.7713 | 1242762.4172
2 | 2635551.6123 | 1242747.604 | 2635550.9225 | 1242745.9451 | 2635546.8501 | 1242738.2596
3 | 2635557.7713 | 1242762.4172 | 2635563.0704 | 1242775.1623
4 | 2635546.8501 | 1242738.2596 | 2635544.2732 | 1242733.3963
5 | 2635564.618 | 1242778.8844 | 2635563.0704 | 1242775.1623
6 | 2635368.7088 | 1242803.8282 | 2635437.2367 | 1242787.7647
7 | 2635437.2367 | 1242787.7647 | 2635503.2734 | 1242688.466
8 | 2635368.7088 | 1242803.8282 | 2635380.6947 | 1242830.8407
9 | 2635368.7088 | 1242803.8282 | 2635361.8885 | 1242805.5554 | 2635350.6854 | 1242808.3906
10 | 2635503.2734 | 1242688.466 | 2635522.3922 | 1242702.591 | 2635526.204 | 1242707.0419
11 | 2635490.7463 | 1242678.3641 | 2635498.8911 | 1242685.2283 | 2635503.2734 | 1242688.466
12 | 2635536.9687 | 1242719.6113 | 2635544.2732 | 1242733.3963
13 | 2635564.618 | 1242778.8844 | 2635565.8171 | 1242781.7684 | 2635570.6329 | 1242793.5996
14 | 2635526.3374 | 1242707.1977 | 2635536.9687 | 1242719.6113 | 2635536.9687 | 1242719.6113
15 | 2635574.033 | 1242801.9528 | 2635570.6329 | 1242793.5996
16 | 2635526.204 | 1242707.0419 | 2635526.3374 | 1242707.1977
17 | 2635490.7463 | 1242678.3641 | 2635485.627 | 1242674.4571
18 | 2635490.7463 | 1242678.3641 | 2635513.5085 | 1242669.3036
19 | 2635304.8327 | 1242709.9657 | 2635309.8197 | 1242722.0216
20 | 2635304.8327 | 1242709.9657 | 2635278.4763 | 1242721.6763
21 | 2635309.96 | 1242722.3607 | 2635309.8197 | 1242722.0216
22 | 2635278.4763 | 1242721.6763 | 2635265.1277 | 1242727.6072
23 | 2635574.033 | 1242801.9528 | 2635581.0221 | 1242818.7232
24 | 2635574.033 | 1242801.9528 | 2635591.7032 | 1242796.6925
25 | 2635584.1517 | 1242826.2328 | 2635581.0221 | 1242818.7232
26 | 2635444.9244 | 1242962.4401 | 2635482.2436 | 1242953.0582
27 | 2635444.9244 | 1242962.4401 | 2635419.1599 | 1242947.0766 | 2635414.7582 | 1242939.1783
28 | 2635423.3566 | 1242975.8868 | 2635438.1149 | 1242966.1797 | 2635444.9244 | 1242962.4401
29 | 2635412.793 | 1242917.1527 | 2635409.4159 | 1242923.2698 | 2635411.8987 | 1242934.0471 | 2635414.7582 | 1242939.1783
30 | 2635423.3566 | 1242975.8868 | 2635426.7359 | 1242989.0537
31 | 2635591.7805 | 1242844.5382 | 2635584.1517 | 1242826.2328
32 | 2635390.5726 | 1242848.5984 | 2635387.906 | 1242847.0926 | 2635380.6947 | 1242830.8407
33 | 2635340.9736 | 1242810.8455 | 2635350.6854 | 1242808.3906
34 | 2635120.5376 | 1242712.2866 | 2635125.3276 | 1242721.8307
35 | 2635130.0888 | 1242731.3174 | 2635125.3276 | 1242721.8307
36 | 2635130.0888 | 1242731.3174 | 2635133.6916 | 1242738.496
37 | 2635138.8971 | 1242748.8679 | 2635133.6916 | 1242738.496
38 | 2635138.8971 | 1242748.8679 | 2635147.674 | 1242766.3558
39 | 2635271.241 | 1242789.2172 | 2635295.4579 | 1242789.1944 | 2635296.147 | 1242775.9023
40 | 2635328.1273 | 1242754.4884 | 2635313.8698 | 1242751.0903 | 2635311.1233 | 1242752.8307 | 2635308.7264 | 1242760.6103 | 2635296.3372 | 1242772.2331 | 2635296.147 | 1242775.9023
41 | 2635271.241 | 1242789.2172 | 2635281.2332 | 1242805.4071
42 | 2635328.1273 | 1242754.4884 | 2635330.0622 | 1242757.0349 | 2635328.6315 | 1242767.5554 | 2635331.054 | 1242776.0522
43 | 2635328.1273 | 1242754.4884 | 2635333.455 | 1242745.7478 | 2635340.1287 | 1242743.2525
44 | 2635289.2824 | 1242814.6963 | 2635281.3998 | 1242805.677 | 2635281.2332 | 1242805.4071
45 | 2635340.9736 | 1242810.8455 | 2635331.054 | 1242776.0522
46 | 2635340.1287 | 1242743.2525 | 2635342.0503 | 1242750.5798
47 | 2635289.2824 | 1242814.6963 | 2635273.0439 | 1242830.3891
48 | 2635236.6398 | 1242740.714 | 2635245.2936 | 1242736.9741 | 2635256.2513 | 1242764.0343
49 | 2635256.2513 | 1242764.0343 | 2635245.9774 | 1242774.1283
50 | 2635236.6398 | 1242740.714 | 2635224.2423 | 1242741.0185 | 2635212.1352 | 1242736.9664
51 | 2635236.6398 | 1242740.714 | 2635245.2936 | 1242736.9741 | 2635260.1804 | 1242729.8689
52 | 2635245.9774 | 1242774.1283 | 2635240.3723 | 1242779.6353
53 | 2635273.0439 | 1242830.3891 | 2635262.6935 | 1242840.3916
54 | 2635260.1804 | 1242729.8689 | 2635262.0148 | 1242728.9904 | 2635265.1277 | 1242727.6072
55 | 2635260.1804 | 1242729.8689 | 2635257.3283 | 1242714.2938
56 | 2635254.4042 | 1242698.3255 | 2635257.3283 | 1242714.2938
57 | 2635212.1352 | 1242736.9664 | 2635205.9417 | 1242741.3214 | 2635205.1925 | 1242741.705
58 | 2635212.1352 | 1242736.9664 | 2635201.398 | 1242717.1776
59 | 2635240.3723 | 1242779.6353 | 2635228.6181 | 1242791.1838
60 | 2635227.9086 | 1242702.7156 | 2635254.4042 | 1242698.3255
61 | 2635227.9086 | 1242702.7156 | 2635229.5912 | 1242710.0371
62 | 2635205.1925 | 1242741.705 | 2635200.6055 | 1242744.0534
63 | 2635201.398 | 1242717.1776 | 2635197.5557 | 1242710.096 | 2635190.4656 | 1242698.9405
64 | 2635384.3293 | 1242854.9764 | 2635378.299 | 1242861.1334 | 2635369.6804 | 1242871.041
65 | 2635371.798 | 1242828.3068 | 2635384.3293 | 1242854.9764
66 | 2635390.5726 | 1242848.5984 | 2635384.3293 | 1242854.9764
67 | 2635341.663 | 1242903.2647 | 2635352.8559 | 1242927.5024
68 | 2635341.663 | 1242903.2647 | 2635335.5828 | 1242891.154
69 | 2635336.8016 | 1242965.7538 | 2635358.2986 | 1242938.7865 | 2635356.9853 | 1242937.211 | 2635352.8559 | 1242927.5024
70 | 2635352.8559 | 1242927.5024 | 2635376.0066 | 1242912.8722
71 | 2635316.7307 | 1242855.9082 | 2635322.5781 | 1242865.26 | 2635335.5828 | 1242891.154
72 | 2635371.798 | 1242828.3068 | 2635347.4769 | 1242839.3131
73 | 2635336.8016 | 1242965.7538 | 2635330.4023 | 1242968.0091
74 | 2635392.1102 | 1242901.3081 | 2635388.6727 | 1242904.8677 | 2635376.0066 | 1242912.8722
75 | 2635316.7307 | 1242855.9082 | 2635300.98 | 1242871.6284
76 | 2635316.7307 | 1242855.9082 | 2635315.4659 | 1242853.7993
77 | 2635315.4659 | 1242853.7993 | 2635347.4769 | 1242839.3131
78 | 2635426.7359 | 1242989.0537 | 2635427.0719 | 1242990.3628 | 2635435.4945 | 1243023.0693
79 | 2635358.5824 | 1243019.3179 | 2635345.3548 | 1243027.6477
80 | 2635358.5824 | 1243019.3179 | 2635365.9083 | 1243035.4626
81 | 2635345.3548 | 1243027.6477 | 2635329.2685 | 1243037.7776 | 2635321.8814 | 1243039.5459 | 2635317.9267 | 1243038.5885 | 2635307.0267 | 1243029.7402
82 | 2635368.4521 | 1243041.0684 | 2635365.9083 | 1243035.4626
83 | 2635407.9505 | 1242914.2442 | 2635392.1102 | 1242901.3081
84 | 2635392.1102 | 1242901.3081 | 2635393.9733 | 1242898.8694
85 | 2635275.9981 | 1242896.5618 | 2635300.98 | 1242871.6284
86 | 2635287.2861 | 1242925.5002 | 2635303.4851 | 1242925.1629 | 2635309.0776 | 1242922.6659
87 | 2635263.3102 | 1242909.2252 | 2635279.2811 | 1242925.6639 | 2635287.2861 | 1242925.5002
88 | 2635262.6935 | 1242840.3916 | 2635259.2423 | 1242843.7268
89 | 2635263.3102 | 1242909.2252 | 2635275.9981 | 1242896.5618
90 | 2635407.9505 | 1242914.2442 | 2635412.793 | 1242917.1527
91 | 2635407.9505 | 1242914.2442 | 2635387.8582 | 1242934.8383
92 | 2635312.5 | 1242728.501 | 2635309.96 | 1242722.3607
93 | 2635394.7049 | 1242868.7312 | 2635398.5852 | 1242885.2141 | 2635398.6261 | 1242887.4334
94 | 2635398.6261 | 1242887.4334 | 2635398.7223 | 1242892.6531 | 2635393.9733 | 1242898.8694
95 | 2635200.6055 | 1242744.0534 | 2635190.5518 | 1242749.2008
96 | 2635189.7647 | 1242749.6038 | 2635190.5518 | 1242749.2008
97 | 2635149.5898 | 1242770.173 | 2635147.674 | 1242766.3558
98 | 2635149.5898 | 1242770.173 | 2635162.6465 | 1242763.4881
99 | 2635149.5898 | 1242770.173 | 2635149.3111 | 1242793.017
100 | 2635172.6991 | 1242758.3412 | 2635162.6465 | 1242763.4881
101 | 2635153.7183 | 1242803.0741 | 2635149.252 | 1242797.8666 | 2635149.3111 | 1242793.017
102 | 2635172.6991 | 1242758.3412 | 2635173.2175 | 1242758.0758
103 | 2635189.7647 | 1242749.6038 | 2635173.2175 | 1242758.0758
104 | 2635482.7578 | 1243047.5653 | 2635497.0685 | 1243093.7583
105 | 2635482.7578 | 1243047.5653 | 2635456.1134 | 1243063.7858
106 | 2635497.0685 | 1243093.7583 | 2635477.8593 | 1243105.0532
107 | 2635497.0685 | 1243093.7583 | 2635515.2549 | 1243157.8528
108 | 2635456.1134 | 1243063.7858 | 2635436.9009 | 1243075.482
109 | 2635435.4945 | 1243023.0693 | 2635436.6009 | 1243027.3657
110 | 2635378.7735 | 1243052.9486 | 2635370.2927 | 1243044.2036 | 2635368.4521 | 1243041.0684
111 | 2635368.4521 | 1243041.0684 | 2635360.0147 | 1243046.3218
112 | 2635251.3716 | 1242970.467 | 2635231.994 | 1242949.1874 | 2635239.9239 | 1242941.5406
113 | 2635239.9239 | 1242941.5406 | 2635248.003 | 1242933.7502 | 2635247.2691 | 1242924.9513 | 2635247.2691 | 1242924.9513
114 | 2635254.825 | 1242917.6914 | 2635247.2691 | 1242924.9513
115 | 2635254.825 | 1242917.6914 | 2635259.2815 | 1242913.2449
116 | 2635263.3102 | 1242909.2252 | 2635259.2815 | 1242913.2449
117 | 2635225.034 | 1242794.7051 | 2635228.6181 | 1242791.1838
118 | 2635225.034 | 1242794.7051 | 2635213.6798 | 1242805.8606
119 | 2635213.6798 | 1242805.8606 | 2635213.6553 | 1242805.8847
120 | 2635213.6553 | 1242805.8847 | 2635200.2716 | 1242819.0341
121 | 2635400.5797 | 1243097.9687 | 2635401.3845 | 1243097.4584
122 | 2635401.3845 | 1243097.4584 | 2635406.1894 | 1243094.4117
123 | 2635393.8965 | 1243102.2064 | 2635400.5797 | 1243097.9687
124 | 2635406.1894 | 1243094.4117 | 2635406.5184 | 1243094.2031
125 | 2635411.7204 | 1243090.9046 | 2635406.5184 | 1243094.2031
126 | 2635415.4061 | 1243088.5676 | 2635411.7204 | 1243090.9046
127 | 2635415.4061 | 1243088.5676 | 2635401.5516 | 1243068.4165
128 | 2635415.4061 | 1243088.5676 | 2635417.2938 | 1243087.4184
129 | 2635198.8145 | 1242820.4657 | 2635200.2716 | 1242819.0341
130 | 2635198.8145 | 1242820.4657 | 2635185.0848 | 1242833.9551
131 | 2635181.1455 | 1242837.8255 | 2635181.1455 | 1242837.8255 | 2635185.0848 | 1242833.9551
132 | 2635250.3535 | 1242852.3169 | 2635259.2423 | 1242843.7268
133 | 2635250.3535 | 1242852.3169 | 2635245.6742 | 1242856.8389
134 | 2635245.6742 | 1242856.8389 | 2635237.4834 | 1242864.7544 | 2635235.976 | 1242866.2018
135 | 2635229.965 | 1242871.9732 | 2635235.976 | 1242866.2018
136 | 2635216.929 | 1242884.4897 | 2635229.965 | 1242871.9732
137 | 2635205.8644 | 1242877.2482 | 2635193.405 | 1242859.9027
138 | 2635188.7791 | 1242853.4625 | 2635193.405 | 1242859.9027
139 | 2635205.8644 | 1242877.2482 | 2635209.8374 | 1242882.7794
140 | 2635188.7791 | 1242853.4625 | 2635183.2738 | 1242845.7982
141 | 2635214.2124 | 1242884.4788 | 2635211.0489 | 1242884.466 | 2635209.8374 | 1242882.7794
142 | 2635183.2738 | 1242845.7982 | 2635181.221 | 1242842.9403 | 2635181.1455 | 1242837.8255
143 | 2635216.929 | 1242884.4897 | 2635216.929 | 1242884.4897 | 2635214.2124 | 1242884.4788
144 | 2635487.9057 | 1243167.8117 | 2635492.6986 | 1243166.0664
145 | 2635492.6986 | 1243166.0664 | 2635492.9971 | 1243165.9577
146 | 2635482.5414 | 1243169.765 | 2635487.9057 | 1243167.8117
147 | 2635515.2549 | 1243157.8528 | 2635492.9971 | 1243165.9577
148 | 2635520.1527 | 1243175.4823 | 2635519.1259 | 1243171.5069 | 2635515.2549 | 1243157.8528
149 | 2635520.1527 | 1243175.4823 | 2635527.6538 | 1243204.529
150 | 2635520.1527 | 1243175.4823 | 2635499.9987 | 1243183.1935
151 | 2635527.6538 | 1243204.529 | 2635528.5956 | 1243208.1761 | 2635530.1561 | 1243215.7747
152 | 2635476.9891 | 1243105.5649 | 2635477.8593 | 1243105.0532
153 | 2635417.2938 | 1243087.4184 | 2635425.1865 | 1243082.6135
154 | 2635431.0361 | 1243079.0524 | 2635425.1865 | 1243082.6135
155 | 2635435.7622 | 1243076.1752 | 2635431.0361 | 1243079.0524
156 | 2635399.2963 | 1243065.1343 | 2635401.5516 | 1243068.4165
157 | 2635401.5516 | 1243068.4165 | 2635387.88 | 1243076.8764
158 | 2635435.7622 | 1243076.1752 | 2635436.9009 | 1243075.482
159 | 2635382.2364 | 1243056.5271 | 2635399.2963 | 1243065.1343
160 | 2635399.2963 | 1243065.1343 | 2635415.947 | 1243060.2845
161 | 2635382.261 | 1243080.3533 | 2635387.88 | 1243076.8764
162 | 2635382.2364 | 1243056.5271 | 2635370.8039 | 1243063.4063
163 | 2635378.7735 | 1243052.9486 | 2635382.2364 | 1243056.5271
164 | 2635377.1706 | 1243083.5032 | 2635382.261 | 1243080.3533
165 | 2635352.2622 | 1243051.1487 | 2635360.0147 | 1243046.3218
166 | 2635344.5559 | 1243055.9469 | 2635352.2622 | 1243051.1487
167 | 2635378.7735 | 1243052.9486 | 2635386.6107 | 1243044.1341 | 2635401.0193 | 1243039.301
168 | 2635417.3139 | 1243033.8352 | 2635401.0193 | 1243039.301
169 | 2635370.8039 | 1243063.4063 | 2635364.7931 | 1243067.0231
170 | 2635359.0654 | 1243070.4697 | 2635364.7931 | 1243067.0231
171 | 2635417.3139 | 1243033.8352 | 2635436.6009 | 1243027.3657 | 2635436.6009 | 1243027.3657
172 | 2635459.0303 | 1243116.1246 | 2635456.9904 | 1243117.3241
173 | 2635440.5617 | 1243126.9841 | 2635456.9904 | 1243117.3241
174 | 2635476.9891 | 1243105.5649 | 2635459.0303 | 1243116.1246
175 | 2635433.8923 | 1243130.9057 | 2635440.5617 | 1243126.9841
176 | 2635533.2764 | 1243230.9689 | 2635530.1561 | 1243215.7747
177 | 2635537.0117 | 1243249.8966 | 2635536.7912 | 1243248.0842 | 2635533.2764 | 1243230.9689
178 | 2635537.0117 | 1243249.8966 | 2635539.5228 | 1243270.5401
179 | 2635539.5228 | 1243270.5401 | 2635529.7909 | 1243483.5737

## bus_geodata
| x | y | coords
0 | 2635555.0852 | 1242755.9569
1 | 2635551.6123 | 1242747.604
2 | 2635557.7713 | 1242762.4172
3 | 2635546.8501 | 1242738.2596
4 | 2635563.0704 | 1242775.1623
5 | 2635437.2367 | 1242787.7647
6 | 2635368.7088 | 1242803.8282
7 | 2635503.2734 | 1242688.466
8 | 2635544.2732 | 1242733.3963
9 | 2635564.618 | 1242778.8844
10 | 2635536.9687 | 1242719.6113
11 | 2635570.6329 | 1242793.5996
12 | 2635526.204 | 1242707.0419
13 | 2635490.7463 | 1242678.3641
14 | 2635526.3374 | 1242707.1977
15 | 2635485.627 | 1242674.4571
16 | 2635513.5085 | 1242669.3036
17 | 2635304.8326 | 1242709.9657
18 | 2635309.8197 | 1242722.0216
19 | 2635278.4763 | 1242721.6763
20 | 2635574.033 | 1242801.9528
21 | 2635581.0221 | 1242818.7232
22 | 2635591.7032 | 1242796.6925
23 | 2635482.2436 | 1242953.0582
24 | 2635444.9244 | 1242962.4401
25 | 2635414.7582 | 1242939.1783
26 | 2635423.3566 | 1242975.8868
27 | 2635591.7805 | 1242844.5382
28 | 2635584.1517 | 1242826.2328
29 | 2635380.6947 | 1242830.8407
30 | 2635350.6854 | 1242808.3906
31 | 2635120.5376 | 1242712.2866
32 | 2635125.3276 | 1242721.8307
33 | 2635130.0888 | 1242731.3174
34 | 2635133.6916 | 1242738.496
35 | 2635138.8971 | 1242748.8679
36 | 2635296.147 | 1242775.9023
37 | 2635271.241 | 1242789.2172
38 | 2635328.1273 | 1242754.4884
39 | 2635281.2332 | 1242805.4071
40 | 2635331.054 | 1242776.0522
41 | 2635340.1287 | 1242743.2525
42 | 2635289.2824 | 1242814.6963
43 | 2635256.2513 | 1242764.0343
44 | 2635236.6398 | 1242740.714
45 | 2635245.9774 | 1242774.1283
46 | 2635340.9736 | 1242810.8455
47 | 2635342.0503 | 1242750.5798
48 | 2635273.0439 | 1242830.3891
49 | 2635260.1804 | 1242729.8689
50 | 2635265.1277 | 1242727.6072
51 | 2635257.3283 | 1242714.2938
52 | 2635212.1352 | 1242736.9664
53 | 2635240.3723 | 1242779.6353
54 | 2635254.4042 | 1242698.3255
55 | 2635227.9086 | 1242702.7156
56 | 2635229.5912 | 1242710.0371
57 | 2635205.1925 | 1242741.705
58 | 2635201.3981 | 1242717.1776
59 | 2635369.6804 | 1242871.041
60 | 2635384.3293 | 1242854.9764
61 | 2635341.663 | 1242903.2647
62 | 2635352.8559 | 1242927.5024
63 | 2635335.5828 | 1242891.154
64 | 2635371.798 | 1242828.3068
65 | 2635390.5726 | 1242848.5984
66 | 2635336.8016 | 1242965.7538
67 | 2635376.0066 | 1242912.8722
68 | 2635316.7307 | 1242855.9082
69 | 2635347.4769 | 1242839.3131
70 | 2635330.4023 | 1242968.0091
71 | 2635426.7359 | 1242989.0537
72 | 2635358.5824 | 1243019.3179
73 | 2635345.3548 | 1243027.6477
74 | 2635365.9083 | 1243035.4626
75 | 2635392.1102 | 1242901.3081
76 | 2635300.98 | 1242871.6284
77 | 2635315.4659 | 1242853.7993
78 | 2635309.0776 | 1242922.6659
79 | 2635287.2861 | 1242925.5002
80 | 2635262.6935 | 1242840.3916
81 | 2635275.9981 | 1242896.5618
82 | 2635407.9505 | 1242914.2442
83 | 2635412.793 | 1242917.1527
84 | 2635387.8582 | 1242934.8383
85 | 2635309.96 | 1242722.3607
86 | 2635312.5 | 1242728.501
87 | 2635394.7049 | 1242868.7312
88 | 2635398.6261 | 1242887.4334
89 | 2635393.9733 | 1242898.8694
90 | 2635190.4656 | 1242698.9405
91 | 2635200.6055 | 1242744.0534
92 | 2635190.5518 | 1242749.2008
93 | 2635147.674 | 1242766.3558
94 | 2635149.5898 | 1242770.173
95 | 2635162.6465 | 1242763.4881
96 | 2635149.3111 | 1242793.017
97 | 2635172.6991 | 1242758.3412
98 | 2635153.7183 | 1242803.0741
99 | 2635173.2175 | 1242758.0758
100 | 2635482.7578 | 1243047.5653
101 | 2635497.0685 | 1243093.7583
102 | 2635456.1134 | 1243063.7858
103 | 2635435.4945 | 1243023.0693
104 | 2635307.0267 | 1243029.7402
105 | 2635368.4521 | 1243041.0684
106 | 2635189.7647 | 1242749.6038
107 | 2635251.3716 | 1242970.467
108 | 2635239.9239 | 1242941.5406
109 | 2635247.2691 | 1242924.9513
110 | 2635254.825 | 1242917.6914
111 | 2635259.2815 | 1242913.2449
112 | 2635228.6181 | 1242791.1838
113 | 2635225.034 | 1242794.7051
114 | 2635213.6798 | 1242805.8606
115 | 2635213.6553 | 1242805.8847
116 | 2635263.3102 | 1242909.2252
117 | 2635401.3845 | 1243097.4584
118 | 2635400.5797 | 1243097.9687
119 | 2635406.1894 | 1243094.4117
120 | 2635393.8965 | 1243102.2064
121 | 2635406.5184 | 1243094.2031
122 | 2635411.7204 | 1243090.9046
123 | 2635415.4061 | 1243088.5676
124 | 2635200.2716 | 1242819.0341
125 | 2635198.8145 | 1242820.4657
126 | 2635185.0848 | 1242833.9551
127 | 2635259.2423 | 1242843.7268
128 | 2635250.3535 | 1242852.3169
129 | 2635245.6742 | 1242856.8389
130 | 2635235.976 | 1242866.2018
131 | 2635229.965 | 1242871.9732
132 | 2635193.405 | 1242859.9027
133 | 2635205.8644 | 1242877.2482
134 | 2635188.7791 | 1242853.4625
135 | 2635209.8374 | 1242882.7794
136 | 2635183.2738 | 1242845.7982
137 | 2635214.2124 | 1242884.4788
138 | 2635181.1455 | 1242837.8255
139 | 2635216.929 | 1242884.4897
140 | 2635492.6986 | 1243166.0664
141 | 2635487.9057 | 1243167.8117
142 | 2635492.9971 | 1243165.9577
143 | 2635482.5414 | 1243169.765
144 | 2635515.2549 | 1243157.8528
145 | 2635520.1527 | 1243175.4823
146 | 2635527.6538 | 1243204.529
147 | 2635499.9987 | 1243183.1935
148 | 2635477.8593 | 1243105.0532
149 | 2635417.2938 | 1243087.4184
150 | 2635425.1865 | 1243082.6135
151 | 2635431.0361 | 1243079.0524
152 | 2635401.5516 | 1243068.4165
153 | 2635435.7622 | 1243076.1752
154 | 2635399.2963 | 1243065.1343
155 | 2635387.88 | 1243076.8764
156 | 2635436.9009 | 1243075.482
157 | 2635382.2364 | 1243056.5271
158 | 2635415.947 | 1243060.2845
159 | 2635382.261 | 1243080.3533
160 | 2635352.2622 | 1243051.1487
161 | 2635360.0147 | 1243046.3218
162 | 2635344.5559 | 1243055.9469
163 | 2635378.7735 | 1243052.9486
164 | 2635401.0193 | 1243039.3009
165 | 2635377.1706 | 1243083.5032
166 | 2635370.8039 | 1243063.4063
167 | 2635364.7931 | 1243067.0231
168 | 2635359.0654 | 1243070.4697
169 | 2635417.3139 | 1243033.8352
170 | 2635436.6009 | 1243027.3657
171 | 2635456.9904 | 1243117.3241
172 | 2635459.0303 | 1243116.1246
173 | 2635440.5617 | 1243126.9841
174 | 2635476.9891 | 1243105.5649
175 | 2635433.8923 | 1243130.9057
176 | 2635530.1561 | 1243215.7747
177 | 2635533.2764 | 1243230.9689
178 | 2635539.5228 | 1243270.5401
179 | 2635537.0117 | 1243249.8966
180 | 2635529.7909 | 1243483.5737
181 | 2635358.2986 | 1242938.7865

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1