## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4280-7_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4280-7_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4280-7_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_4280-7_0_6_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_4280-7_0_6_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_4280-7_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_4280-7_0_6_node_52 | 0.4 | n |  | TRUE
7 | bus_LV_4280-7_0_6_node_73 | 0.4 | n |  | TRUE
8 | bus_LV_4280-7_0_6_node_81 | 0.4 | n |  | TRUE
9 | bus_LV_4280-7_0_6_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_4280-7_0_6_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_4280-7_0_6_node_37 | 0.4 | n |  | TRUE
12 | bus_LV_4280-7_0_6_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_4280-7_0_6_node_92 | 0.4 | n |  | TRUE
14 | bus_LV_4280-7_0_6_node_60 | 0.4 | n |  | TRUE
15 | bus_LV_4280-7_0_6_node_50 | 0.4 | n |  | TRUE
16 | bus_LV_4280-7_0_6_node_72 | 0.4 | n |  | TRUE
17 | bus_LV_4280-7_0_6_node_47 | 0.4 | n |  | TRUE
18 | bus_LV_4280-7_0_6_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_4280-7_0_6_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_4280-7_0_6_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_4280-7_0_6_node_75 | 0.4 | n |  | TRUE
22 | bus_LV_4280-7_0_6_node_90 | 0.4 | n |  | TRUE
23 | bus_LV_4280-7_0_6_node_8 | 0.4 | n |  | TRUE
24 | bus_LV_4280-7_0_6_node_9 | 0.4 | n |  | TRUE
25 | bus_LV_4280-7_0_6_node_10 | 0.4 | n |  | TRUE
26 | bus_LV_4280-7_0_6_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_4280-7_0_6_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_4280-7_0_6_node_111 | 0.4 | n |  | TRUE
29 | bus_LV_4280-7_0_6_node_68 | 0.4 | n |  | TRUE
30 | bus_LV_4280-7_0_6_node_69 | 0.4 | n |  | TRUE
31 | bus_LV_4280-7_0_6_node_87 | 0.4 | n |  | TRUE
32 | bus_LV_4280-7_0_6_node_80 | 0.4 | n |  | TRUE
33 | bus_LV_4280-7_0_6_node_13 | 0.4 | n |  | TRUE
34 | bus_LV_4280-7_0_6_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_4280-7_0_6_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_4280-7_0_6_node_18 | 0.4 | n |  | TRUE
37 | bus_LV_4280-7_0_6_node_66 | 0.4 | n |  | TRUE
38 | bus_LV_4280-7_0_6_node_74 | 0.4 | n |  | TRUE
39 | bus_LV_4280-7_0_6_node_67 | 0.4 | n |  | TRUE
40 | bus_LV_4280-7_0_6_node_19 | 0.4 | n |  | TRUE
41 | bus_LV_4280-7_0_6_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_4280-7_0_6_node_21 | 0.4 | n |  | TRUE
43 | bus_LV_4280-7_0_6_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_4280-7_0_6_node_25 | 0.4 | n |  | TRUE
45 | bus_LV_4280-7_0_6_node_76 | 0.4 | n |  | TRUE
46 | bus_LV_4280-7_0_6_node_77 | 0.4 | n |  | TRUE
47 | bus_LV_4280-7_0_6_node_99 | 0.4 | n |  | TRUE
48 | bus_LV_4280-7_0_6_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_4280-7_0_6_node_116 | 0.4 | n |  | TRUE
50 | bus_LV_4280-7_0_6_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_4280-7_0_6_node_159 | 0.4 | n |  | TRUE
52 | bus_LV_4280-7_0_6_node_30 | 0.4 | n |  | TRUE
53 | bus_LV_4280-7_0_6_node_113 | 0.4 | n |  | TRUE
54 | bus_LV_4280-7_0_6_node_115 | 0.4 | n |  | TRUE
55 | bus_LV_4280-7_0_6_node_31 | 0.4 | n |  | TRUE
56 | bus_LV_4280-7_0_6_node_161 | 0.4 | n |  | TRUE
57 | bus_LV_4280-7_0_6_node_35 | 0.4 | n |  | TRUE
58 | bus_LV_4280-7_0_6_node_33 | 0.4 | n |  | TRUE
59 | bus_LV_4280-7_0_6_node_102 | 0.4 | n |  | TRUE
60 | bus_LV_4280-7_0_6_node_34 | 0.4 | n |  | TRUE
61 | bus_LV_4280-7_0_6_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_4280-7_0_6_node_100 | 0.4 | n |  | TRUE
63 | bus_LV_4280-7_0_6_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_4280-7_0_6_node_117 | 0.4 | n |  | TRUE
65 | bus_LV_4280-7_0_6_node_94 | 0.4 | n |  | TRUE
66 | bus_LV_4280-7_0_6_node_125 | 0.4 | n |  | TRUE
67 | bus_LV_4280-7_0_6_node_141 | 0.4 | n |  | TRUE
68 | bus_LV_4280-7_0_6_node_124 | 0.4 | n |  | TRUE
69 | bus_LV_4280-7_0_6_node_112 | 0.4 | n |  | TRUE
70 | bus_LV_4280-7_0_6_node_118 | 0.4 | n |  | TRUE
71 | bus_LV_4280-7_0_6_node_119 | 0.4 | n |  | TRUE
72 | bus_LV_4280-7_0_6_node_121 | 0.4 | n |  | TRUE
73 | bus_LV_4280-7_0_6_node_101 | 0.4 | n |  | TRUE
74 | bus_LV_4280-7_0_6_node_39 | 0.4 | n |  | TRUE
75 | bus_LV_4280-7_0_6_node_40 | 0.4 | n |  | TRUE
76 | bus_LV_4280-7_0_6_node_41 | 0.4 | n |  | TRUE
77 | bus_LV_4280-7_0_6_node_42 | 0.4 | n |  | TRUE
78 | bus_LV_4280-7_0_6_node_43 | 0.4 | n |  | TRUE
79 | bus_LV_4280-7_0_6_node_83 | 0.4 | n |  | TRUE
80 | bus_LV_4280-7_0_6_node_88 | 0.4 | n |  | TRUE
81 | bus_LV_4280-7_0_6_node_89 | 0.4 | n |  | TRUE
82 | bus_LV_4280-7_0_6_node_95 | 0.4 | n |  | TRUE
83 | bus_LV_4280-7_0_6_node_71 | 0.4 | n |  | TRUE
84 | bus_LV_4280-7_0_6_node_103 | 0.4 | n |  | TRUE
85 | bus_LV_4280-7_0_6_node_107 | 0.4 | n |  | TRUE
86 | bus_LV_4280-7_0_6_node_131 | 0.4 | n |  | TRUE
87 | bus_LV_4280-7_0_6_node_44 | 0.4 | n |  | TRUE
88 | bus_LV_4280-7_0_6_node_45 | 0.4 | n |  | TRUE
89 | bus_LV_4280-7_0_6_node_46 | 0.4 | n |  | TRUE
90 | bus_LV_4280-7_0_6_node_48 | 0.4 | n |  | TRUE
91 | bus_LV_4280-7_0_6_node_93 | 0.4 | n |  | TRUE
92 | bus_LV_4280-7_0_6_node_157 | 0.4 | n |  | TRUE
93 | bus_LV_4280-7_0_6_node_82 | 0.4 | n |  | TRUE
94 | bus_LV_4280-7_0_6_node_122 | 0.4 | n |  | TRUE
95 | bus_LV_4280-7_0_6_node_123 | 0.4 | n |  | TRUE
96 | bus_LV_4280-7_0_6_node_49 | 0.4 | n |  | TRUE
97 | bus_LV_4280-7_0_6_node_51 | 0.4 | n |  | TRUE
98 | bus_LV_4280-7_0_6_node_53 | 0.4 | n |  | TRUE
99 | bus_LV_4280-7_0_6_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_4280-7_0_6_node_59 | 0.4 | n |  | TRUE
101 | bus_LV_4280-7_0_6_node_98 | 0.4 | n |  | TRUE
102 | bus_LV_4280-7_0_6_node_54 | 0.4 | n |  | TRUE
103 | bus_LV_4280-7_0_6_node_55 | 0.4 | n |  | TRUE
104 | bus_LV_4280-7_0_6_node_56 | 0.4 | n |  | TRUE
105 | bus_LV_4280-7_0_6_node_57 | 0.4 | n |  | TRUE
106 | bus_LV_4280-7_0_6_node_58 | 0.4 | n |  | TRUE
107 | bus_LV_4280-7_0_6_node_160 | 0.4 | n |  | TRUE
108 | bus_LV_4280-7_0_6_node_61 | 0.4 | n |  | TRUE
109 | bus_LV_4280-7_0_6_node_62 | 0.4 | n |  | TRUE
110 | bus_LV_4280-7_0_6_node_63 | 0.4 | n |  | TRUE
111 | bus_LV_4280-7_0_6_node_64 | 0.4 | n |  | TRUE
112 | bus_LV_4280-7_0_6_node_65 | 0.4 | n |  | TRUE
113 | bus_LV_4280-7_0_6_node_148 | 0.4 | n |  | TRUE
114 | bus_LV_4280-7_0_6_node_85 | 0.4 | n |  | TRUE
115 | bus_LV_4280-7_0_6_node_155 | 0.4 | n |  | TRUE
116 | bus_LV_4280-7_0_6_node_146 | 0.4 | n |  | TRUE
117 | bus_LV_4280-7_0_6_node_84 | 0.4 | n |  | TRUE
118 | bus_LV_4280-7_0_6_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_4280-7_0_6_node_70 | 0.4 | n |  | TRUE
120 | bus_LV_4280-7_0_6_node_96 | 0.4 | n |  | TRUE
121 | bus_LV_4280-7_0_6_node_78 | 0.4 | n |  | TRUE
122 | bus_LV_4280-7_0_6_node_79 | 0.4 | n |  | TRUE
123 | bus_LV_4280-7_0_6_node_108 | 0.4 | n |  | TRUE
124 | bus_LV_4280-7_0_6_node_143 | 0.4 | n |  | TRUE
125 | bus_LV_4280-7_0_6_node_150 | 0.4 | n |  | TRUE
126 | bus_LV_4280-7_0_6_node_142 | 0.4 | n |  | TRUE
127 | bus_LV_4280-7_0_6_node_86 | 0.4 | n |  | TRUE
128 | bus_LV_4280-7_0_6_node_110 | 0.4 | n |  | TRUE
129 | bus_LV_4280-7_0_6_node_104 | 0.4 | n |  | TRUE
130 | bus_LV_4280-7_0_6_node_105 | 0.4 | n |  | TRUE
131 | bus_LV_4280-7_0_6_node_132 | 0.4 | n |  | TRUE
132 | bus_LV_4280-7_0_6_node_91 | 0.4 | n |  | TRUE
133 | bus_LV_4280-7_0_6_node_106 | 0.4 | n |  | TRUE
134 | bus_LV_4280-7_0_6_node_120 | 0.4 | n |  | TRUE
135 | bus_LV_4280-7_0_6_node_126 | 0.4 | n |  | TRUE
136 | bus_LV_4280-7_0_6_node_127 | 0.4 | n |  | TRUE
137 | bus_LV_4280-7_0_6_node_128 | 0.4 | n |  | TRUE
138 | bus_LV_4280-7_0_6_node_129 | 0.4 | n |  | TRUE
139 | bus_LV_4280-7_0_6_node_130 | 0.4 | n |  | TRUE
140 | bus_LV_4280-7_0_6_node_140 | 0.4 | n |  | TRUE
141 | bus_LV_4280-7_0_6_node_137 | 0.4 | n |  | TRUE
142 | bus_LV_4280-7_0_6_node_133 | 0.4 | n |  | TRUE
143 | bus_LV_4280-7_0_6_node_139 | 0.4 | n |  | TRUE
144 | bus_LV_4280-7_0_6_node_135 | 0.4 | n |  | TRUE
145 | bus_LV_4280-7_0_6_node_134 | 0.4 | n |  | TRUE
146 | bus_LV_4280-7_0_6_node_149 | 0.4 | n |  | TRUE
147 | bus_LV_4280-7_0_6_node_156 | 0.4 | n |  | TRUE
148 | bus_LV_4280-7_0_6_node_144 | 0.4 | n |  | TRUE
149 | bus_LV_4280-7_0_6_node_152 | 0.4 | n |  | TRUE
150 | bus_LV_4280-7_0_6_node_151 | 0.4 | n |  | TRUE
151 | bus_LV_4280-7_0_6_node_145 | 0.4 | n |  | TRUE
152 | bus_LV_4280-7_0_6_node_147 | 0.4 | n |  | TRUE
153 | bus_LV_4280-7_0_6_node_153 | 0.4 | n |  | TRUE
154 | bus_LV_4280-7_0_6_node_154 | 0.4 | n |  | TRUE
155 | bus_MV_436_0_node_143 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4280-7_0_6_load_0 | 0 | 0.015327 | 0.0038413 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4280-7_0_6_load_3 | 2 | 0.0017071 | 0.00042784 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4280-7_0_6_load_73 | 7 | 0.012545 | 0.003144 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4280-7_0_6_load_81 | 8 | 0.00077382 | 0.00019394 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4280-7_0_6_load_17 | 10 | 0.0052544 | 0.0013169 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4280-7_0_6_load_37 | 11 | 0.002177 | 0.0005456 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4280-7_0_6_load_38 | 12 | 0.0016822 | 0.0004216 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4280-7_0_6_load_92 | 13 | 0.0068973 | 0.0017286 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4280-7_0_6_load_60 | 14 | 0.01005 | 0.0025187 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4280-7_0_6_load_50 | 15 | 0.014122 | 0.0035392 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4280-7_0_6_load_72 | 16 | 0.00095284 | 0.0002388 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4280-7_0_6_load_47 | 17 | 0.001071 | 0.00026842 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4280-7_0_6_load_23 | 18 | 0.0019881 | 0.00049828 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4280-7_0_6_load_75 | 21 | 0.0019753 | 0.00049506 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4280-7_0_6_load_90 | 22 | 0.012325 | 0.0030891 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4280-7_0_6_load_8 | 23 | 0.002383 | 0.00059725 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4280-7_0_6_load_9 | 24 | 0.00098924 | 0.00024793 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4280-7_0_6_load_10 | 25 | 0.0008651 | 0.00021681 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4280-7_0_6_load_11 | 26 | 0.00064345 | 0.00016126 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4280-7_0_6_load_111 | 28 | 0.00068672 | 0.00017211 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4280-7_0_6_load_68 | 29 | 0.0011213 | 0.00028102 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4280-7_0_6_load_69 | 30 | 0.0031778 | 0.00079644 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4280-7_0_6_load_80 | 32 | 0.0017605 | 0.00044123 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4280-7_0_6_load_13 | 33 | 0.0046254 | 0.0011592 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4280-7_0_6_load_15 | 34 | 0.0006473 | 0.00016223 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4280-7_0_6_load_16 | 35 | 0.0078134 | 0.0019582 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4280-7_0_6_load_18 | 36 | 0.00077723 | 0.00019479 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4280-7_0_6_load_66 | 37 | 0.0020117 | 0.00050417 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4280-7_0_6_load_74 | 38 | 0.00095835 | 0.00024019 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4280-7_0_6_load_67 | 39 | 0.0013113 | 0.00032863 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4280-7_0_6_load_19 | 40 | 0.0022959 | 0.00057542 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4280-7_0_6_load_76 | 45 | 0.00075067 | 0.00018814 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4280-7_0_6_load_77 | 46 | 0.0032924 | 0.00082516 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4280-7_0_6_load_99 | 47 | 0.0040258 | 0.001009 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4280-7_0_6_load_159 | 51 | 0.066969 | 0.016784 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4280-7_0_6_load_115 | 54 | 0.0071374 | 0.0017888 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4280-7_0_6_load_161 | 56 | 0.010221 | 0.0025616 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4280-7_0_6_load_102 | 59 | 6.7987e-05 | 1.7039e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4280-7_0_6_load_100 | 62 | 0.00083498 | 0.00020927 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4280-7_0_6_load_114 | 63 | 0.016382 | 0.0041058 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4280-7_0_6_load_117 | 64 | 0.0016116 | 0.0004039 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4280-7_0_6_load_141 | 67 | 0.0095024 | 0.0023815 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4280-7_0_6_load_124 | 68 | 0.0004161 | 0.00010429 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4280-7_0_6_load_112 | 69 | 0.0018992 | 0.00047598 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4280-7_0_6_load_118 | 70 | 0.0036416 | 0.00091268 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4280-7_0_6_load_119 | 71 | 0.00024225 | 6.0714e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4280-7_0_6_load_121 | 72 | 0.00057141 | 0.00014321 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4280-7_0_6_load_101 | 73 | 4.3908e-05 | 1.1004e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4280-7_0_6_load_39 | 74 | 0.0012968 | 0.00032501 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4280-7_0_6_load_40 | 75 | 0.0013407 | 0.00033602 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4280-7_0_6_load_41 | 76 | 0.0016569 | 0.00041527 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4280-7_0_6_load_42 | 77 | 0.0013281 | 0.00033285 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4280-7_0_6_load_88 | 80 | 0.0038096 | 0.00095478 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4280-7_0_6_load_95 | 82 | 0.0022703 | 0.00056899 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4280-7_0_6_load_71 | 83 | 0.00090671 | 0.00022724 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4280-7_0_6_load_103 | 84 | 0.00094455 | 0.00023673 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4280-7_0_6_load_131 | 86 | 0.002103 | 0.00052706 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4280-7_0_6_load_44 | 87 | 0.0012446 | 0.00031194 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4280-7_0_6_load_45 | 88 | 0.0058805 | 0.0014738 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4280-7_0_6_load_46 | 89 | 0.0010231 | 0.00025642 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4280-7_0_6_load_48 | 90 | 0.0012342 | 0.00030932 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4280-7_0_6_load_93 | 91 | 0.00081991 | 0.00020549 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4280-7_0_6_load_82 | 93 | 0.0010776 | 0.00027006 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4280-7_0_6_load_122 | 94 | 0.01352 | 0.0033885 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4280-7_0_6_load_49 | 96 | 0.014939 | 0.0037441 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4280-7_0_6_load_51 | 97 | 0.0023957 | 0.00060043 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4280-7_0_6_load_53 | 98 | 0.0092028 | 0.0023064 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4280-7_0_6_load_97 | 99 | 0.00028823 | 7.2238e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4280-7_0_6_load_59 | 100 | 0.0077878 | 0.0019518 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4280-7_0_6_load_98 | 101 | 0.0011184 | 0.00028029 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4280-7_0_6_load_54 | 102 | 0.00117 | 0.00029322 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4280-7_0_6_load_55 | 103 | 0.0013957 | 0.00034978 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4280-7_0_6_load_56 | 104 | 5.3508e-05 | 1.341e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4280-7_0_6_load_57 | 105 | 0.017483 | 0.0043816 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4280-7_0_6_load_58 | 106 | 0.00089534 | 0.00022439 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4280-7_0_6_load_160 | 107 | 0.011877 | 0.0029767 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4280-7_0_6_load_61 | 108 | 0.0024748 | 0.00062025 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4280-7_0_6_load_62 | 109 | 0.0013049 | 0.00032704 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4280-7_0_6_load_64 | 111 | 0.0018085 | 0.00045324 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4280-7_0_6_load_65 | 112 | 0.0015335 | 0.00038432 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4280-7_0_6_load_85 | 114 | 0.0014541 | 0.00036442 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4280-7_0_6_load_155 | 115 | 0.0023949 | 0.00060021 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4280-7_0_6_load_146 | 116 | 0.0020454 | 0.00051262 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4280-7_0_6_load_84 | 117 | 0.0029977 | 0.0007513 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4280-7_0_6_load_109 | 118 | 0.0064732 | 0.0016223 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4280-7_0_6_load_70 | 119 | 0.0013599 | 0.00034081 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4280-7_0_6_load_96 | 120 | 0.0011375 | 0.00028508 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4280-7_0_6_load_78 | 121 | 0.0022048 | 0.00055257 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4280-7_0_6_load_108 | 123 | 0.0023899 | 0.00059897 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4280-7_0_6_load_150 | 125 | 0.0016312 | 0.00040882 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4280-7_0_6_load_86 | 127 | 0.0062415 | 0.0015643 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4280-7_0_6_load_110 | 128 | 0.0021918 | 0.00054933 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4280-7_0_6_load_104 | 129 | 0.0024452 | 0.00061282 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4280-7_0_6_load_105 | 130 | 0.0015207 | 0.00038111 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4280-7_0_6_load_132 | 131 | 0.0022179 | 0.00055585 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4280-7_0_6_load_91 | 132 | 0.0080176 | 0.0020094 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4280-7_0_6_load_106 | 133 | 0.0020989 | 0.00052603 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4280-7_0_6_load_120 | 134 | 0.00027215 | 6.8208e-05 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4280-7_0_6_load_126 | 135 | 0.0018189 | 0.00045585 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4280-7_0_6_load_127 | 136 | 0.0022202 | 0.00055643 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4280-7_0_6_load_128 | 137 | 0.0021967 | 0.00055055 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4280-7_0_6_load_129 | 138 | 0.0030721 | 0.00076995 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4280-7_0_6_load_130 | 139 | 0.0020855 | 0.00052268 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4280-7_0_6_load_140 | 140 | 0.001304 | 0.00032683 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4280-7_0_6_load_133 | 142 | 0.0026687 | 0.00066884 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4280-7_0_6_load_139 | 143 | 0.0016329 | 0.00040925 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4280-7_0_6_load_135 | 144 | 0.0023887 | 0.00059866 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4280-7_0_6_load_134 | 145 | 0.0032682 | 0.00081909 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4280-7_0_6_load_149 | 146 | 0.0019519 | 0.00048918 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4280-7_0_6_load_156 | 147 | 0.0017498 | 0.00043854 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4280-7_0_6_load_144 | 148 | 0.0023352 | 0.00058525 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4280-7_0_6_load_152 | 149 | 0.0016743 | 0.00041962 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4280-7_0_6_load_151 | 150 | 0.00178 | 0.00044611 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4280-7_0_6_load_145 | 151 | 0.0012554 | 0.00031465 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4280-7_0_6_load_147 | 152 | 0.0015467 | 0.00038765 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4280-7_0_6_load_153 | 153 | 0.00035488 | 8.894e-05 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4280-7_0_6_load_154 | 154 | 0.00034899 | 8.7464e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4280-7_0_6_line_0 |  | 0 | 1 | 0.044971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4280-7_0_6_line_1 |  | 1 | 2 | 0.098382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4280-7_0_6_line_2 |  | 1 | 3 | 0.21019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4280-7_0_6_line_3 |  | 2 | 4 | 0.044171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4280-7_0_6_line_4 |  | 3 | 13 | 0.053455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4280-7_0_6_line_5 |  | 4 | 11 | 0.030455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_4280-7_0_6_line_6 |  | 4 | 12 | 0.011267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4280-7_0_6_line_7 |  | 4 | 9 | 0.02247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_4280-7_0_6_line_8 |  | 5 | 6 | 0.02395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4280-7_0_6_line_9 |  | 5 | 7 | 0.020559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_4280-7_0_6_line_10 |  | 5 | 8 | 0.057011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_4280-7_0_6_line_11 |  | 6 | 14 | 0.027514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4280-7_0_6_line_12 |  | 6 | 15 | 0.01472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4280-7_0_6_line_13 |  | 7 | 16 | 0.025068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_4280-7_0_6_line_14 |  | 8 | 17 | 0.044274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_4280-7_0_6_line_15 |  | 9 | 10 | 0.025198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_4280-7_0_6_line_16 |  | 10 | 20 | 0.025955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_4280-7_0_6_line_17 |  | 11 | 21 | 0.021917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_4280-7_0_6_line_18 |  | 13 | 22 | 0.015943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4280-7_0_6_line_19 |  | 14 | 100 | 0.0054813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4280-7_0_6_line_20 |  | 15 | 96 | 0.0050361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4280-7_0_6_line_21 |  | 16 | 38 | 0.019357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_4280-7_0_6_line_22 |  | 17 | 88 | 0.013592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_4280-7_0_6_line_23 |  | 18 | 19 | 0.0072985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4280-7_0_6_line_24 |  | 19 | 41 | 0.007754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_4280-7_0_6_line_25 |  | 19 | 40 | 0.016415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4280-7_0_6_line_26 |  | 20 | 35 | 0.028847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4280-7_0_6_line_27 |  | 20 | 36 | 0.034036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_4280-7_0_6_line_28 |  | 20 | 33 | 0.012998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4280-7_0_6_line_29 |  | 21 | 41 | 0.019701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_4280-7_0_6_line_30 |  | 22 | 132 | 0.017863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4280-7_0_6_line_31 |  | 23 | 24 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4280-7_0_6_line_32 |  | 23 | 25 | 0.0071713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4280-7_0_6_line_33 |  | 24 | 26 | 0.019209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4280-7_0_6_line_34 |  | 25 | 27 | 0.014866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4280-7_0_6_line_35 |  | 26 | 28 | 0.0070899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4280-7_0_6_line_36 |  | 27 | 29 | 0.018451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4280-7_0_6_line_37 |  | 27 | 30 | 0.012098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4280-7_0_6_line_38 |  | 28 | 31 | 0.0056133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4280-7_0_6_line_39 |  | 30 | 32 | 0.0077007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4280-7_0_6_line_40 |  | 31 | 128 | 0.018434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4280-7_0_6_line_41 |  | 31 | 127 | 0.0069422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4280-7_0_6_line_42 |  | 33 | 34 | 0.025566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4280-7_0_6_line_43 |  | 35 | 37 | 0.0096708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4280-7_0_6_line_44 |  | 36 | 38 | 0.019583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_4280-7_0_6_line_45 |  | 37 | 39 | 0.016156 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4280-7_0_6_line_46 |  | 39 | 118 | 0.022847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4280-7_0_6_line_47 |  | 41 | 43 | 0.027055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4280-7_0_6_line_48 |  | 41 | 45 | 0.031607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_4280-7_0_6_line_49 |  | 42 | 43 | 0.038267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4280-7_0_6_line_50 |  | 42 | 44 | 0.032163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4280-7_0_6_line_51 |  | 43 | 46 | 0.029401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4280-7_0_6_line_52 |  | 44 | 47 | 0.0135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4280-7_0_6_line_53 |  | 45 | 65 | 0.028659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_4280-7_0_6_line_54 |  | 48 | 49 | 0.066463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4280-7_0_6_line_55 |  | 48 | 50 | 0.11927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4280-7_0_6_line_56 |  | 49 | 66 | 0.23308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4280-7_0_6_line_57 |  | 49 | 67 | 0.043523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4280-7_0_6_line_58 |  | 50 | 51 | 0.012195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4280-7_0_6_line_59 |  | 52 | 53 | 0.019296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4280-7_0_6_line_60 |  | 52 | 54 | 0.011735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4280-7_0_6_line_61 |  | 53 | 69 | 0.012901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4280-7_0_6_line_62 |  | 54 | 60 | 0.063175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4280-7_0_6_line_63 |  | 55 | 56 | 0.031569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4280-7_0_6_line_64 |  | 55 | 57 | 0.13011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4280-7_0_6_line_65 |  | 57 | 61 | 0.018405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4280-7_0_6_line_66 |  | 58 | 59 | 0.032805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4280-7_0_6_line_67 |  | 58 | 60 | 0.085589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4280-7_0_6_line_68 |  | 58 | 61 | 0.083837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4280-7_0_6_line_69 |  | 58 | 62 | 0.017513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4280-7_0_6_line_70 |  | 59 | 71 | 0.028761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4280-7_0_6_line_71 |  | 60 | 63 | 0.028662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4280-7_0_6_line_72 |  | 61 | 64 | 0.026732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4280-7_0_6_line_73 |  | 62 | 73 | 0.018533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4280-7_0_6_line_74 |  | 65 | 82 | 0.019795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_4280-7_0_6_line_75 |  | 65 | 120 | 0.014665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4280-7_0_6_line_76 |  | 66 | 68 | 0.0056301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4280-7_0_6_line_77 |  | 67 | 126 | 0.018496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4280-7_0_6_line_78 |  | 70 | 71 | 0.10703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4280-7_0_6_line_79 |  | 70 | 72 | 0.13679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4280-7_0_6_line_80 |  | 72 | 134 | 0.041145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4280-7_0_6_line_81 |  | 73 | 106 | 0.0038368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4280-7_0_6_line_82 |  | 74 | 75 | 0.011513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_4280-7_0_6_line_83 |  | 74 | 76 | 0.020683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_4280-7_0_6_line_84 |  | 75 | 77 | 0.0067854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_4280-7_0_6_line_85 |  | 76 | 78 | 0.014309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_4280-7_0_6_line_86 |  | 77 | 79 | 0.019895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_4280-7_0_6_line_87 |  | 78 | 80 | 0.021263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4280-7_0_6_line_88 |  | 78 | 81 | 0.017655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_4280-7_0_6_line_89 |  | 79 | 82 | 0.013346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_4280-7_0_6_line_90 |  | 79 | 83 | 0.0064918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4280-7_0_6_line_91 |  | 80 | 84 | 0.010686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4280-7_0_6_line_92 |  | 81 | 85 | 0.015189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_4280-7_0_6_line_93 |  | 81 | 86 | 0.019407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4280-7_0_6_line_94 |  | 83 | 119 | 0.0050673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4280-7_0_6_line_95 |  | 84 | 129 | 0.012149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4280-7_0_6_line_96 |  | 85 | 130 | 0.016671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4280-7_0_6_line_97 |  | 85 | 123 | 0.022967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_4280-7_0_6_line_98 |  | 86 | 131 | 0.0035649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4280-7_0_6_line_99 |  | 87 | 88 | 0.0044687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_4280-7_0_6_line_100 |  | 87 | 89 | 0.016779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_4280-7_0_6_line_101 |  | 89 | 90 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_4280-7_0_6_line_102 |  | 90 | 91 | 0.043485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_4280-7_0_6_line_103 |  | 91 | 92 | 0.14926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4280-7_0_6_line_104 |  | 91 | 93 | 0.026218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
105 | LV_4280-7_0_6_line_105 |  | 92 | 95 | 0.16537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4280-7_0_6_line_106 |  | 92 | 107 | 0.022994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4280-7_0_6_line_107 |  | 93 | 105 | 0.0025294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
108 | LV_4280-7_0_6_line_108 |  | 94 | 95 | 0.070923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4280-7_0_6_line_109 |  | 96 | 97 | 0.024979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4280-7_0_6_line_110 |  | 97 | 98 | 0.0023037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4280-7_0_6_line_111 |  | 98 | 99 | 0.020411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4280-7_0_6_line_112 |  | 99 | 101 | 0.018219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4280-7_0_6_line_113 |  | 102 | 103 | 0.022928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4280-7_0_6_line_114 |  | 102 | 104 | 0.0069689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4280-7_0_6_line_115 |  | 103 | 105 | 0.023808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4280-7_0_6_line_116 |  | 104 | 106 | 0.021145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4280-7_0_6_line_117 |  | 108 | 109 | 0.025845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4280-7_0_6_line_118 |  | 108 | 110 | 0.016808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4280-7_0_6_line_119 |  | 110 | 111 | 0.024815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4280-7_0_6_line_120 |  | 110 | 112 | 0.012625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4280-7_0_6_line_121 |  | 111 | 113 | 0.017067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4280-7_0_6_line_122 |  | 112 | 114 | 0.017041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4280-7_0_6_line_123 |  | 113 | 115 | 0.015784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4280-7_0_6_line_124 |  | 113 | 116 | 0.018056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4280-7_0_6_line_125 |  | 114 | 117 | 0.016742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4280-7_0_6_line_126 |  | 115 | 147 | 0.0019921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4280-7_0_6_line_127 |  | 116 | 151 | 0.013502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4280-7_0_6_line_128 |  | 117 | 127 | 0.014959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4280-7_0_6_line_129 |  | 121 | 122 | 0.047078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4280-7_0_6_line_130 |  | 122 | 123 | 0.004237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_4280-7_0_6_line_131 |  | 122 | 124 | 0.035948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_4280-7_0_6_line_132 |  | 124 | 125 | 0.015854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4280-7_0_6_line_133 |  | 124 | 126 | 0.052577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
134 | LV_4280-7_0_6_line_134 |  | 125 | 146 | 0.005837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4280-7_0_6_line_135 |  | 126 | 148 | 0.019805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4280-7_0_6_line_136 |  | 128 | 129 | 0.0066687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_4280-7_0_6_line_137 |  | 130 | 133 | 0.020566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4280-7_0_6_line_138 |  | 135 | 136 | 0.016073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4280-7_0_6_line_139 |  | 135 | 137 | 0.0052847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4280-7_0_6_line_140 |  | 136 | 138 | 0.010467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_4280-7_0_6_line_141 |  | 137 | 139 | 0.025781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_4280-7_0_6_line_142 |  | 138 | 140 | 0.0097516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4280-7_0_6_line_143 |  | 139 | 141 | 0.0090306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_4280-7_0_6_line_144 |  | 140 | 142 | 0.0066612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_4280-7_0_6_line_145 |  | 141 | 143 | 0.025081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_4280-7_0_6_line_146 |  | 141 | 144 | 0.024612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4280-7_0_6_line_147 |  | 143 | 146 | 0.01778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4280-7_0_6_line_148 |  | 144 | 145 | 0.020254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4280-7_0_6_line_149 |  | 148 | 149 | 0.020623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4280-7_0_6_line_150 |  | 149 | 150 | 0.01352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4280-7_0_6_line_151 |  | 150 | 153 | 0.01645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4280-7_0_6_line_152 |  | 151 | 152 | 0.0010967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4280-7_0_6_line_153 |  | 153 | 154 | 0.01445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4280-7_0_6_trafo_20 | 0.63 MVA 20/0.4 kV | 155 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2636637.8982 | 1240108.6566 | 2636650.2937 | 1240113.2582 | 2636673.6005 | 1240134.8173
1 | 2636637.8982 | 1240108.6566 | 2636708.7617 | 1240040.4122
2 | 2636509.3555 | 1240080.5033 | 2636522.0765 | 1240102.3064 | 2636528.856 | 1240113.9222 | 2636533.9218 | 1240122.6033 | 2636540.8959 | 1240134.5427 | 2636556.6547 | 1240161.5457 | 2636564.9346 | 1240173.8378 | 2636578.9038 | 1240159.8704 | 2636631.7117 | 1240106.3615 | 2636637.8982 | 1240108.6566
3 | 2636740.578 | 1240009.7718 | 2636708.7617 | 1240040.4122
4 | 2636509.3555 | 1240080.5033 | 2636543.5445 | 1240039.4114
5 | 2636740.578 | 1240009.7718 | 2636762.4767 | 1239988.6067
6 | 2636740.578 | 1240009.7718 | 2636745.8575 | 1240019.7253
7 | 2636740.578 | 1240009.7718 | 2636737.8049 | 1240004.5402 | 2636746.2593 | 1239995.9536 | 2636749.4173 | 1239992.7489
8 | 2636624.3133 | 1240050.4469 | 2636641.9494 | 1240034.1896
9 | 2636641.9494 | 1240034.1896 | 2636656.1504 | 1240019.324
10 | 2636641.9494 | 1240034.1896 | 2636610.3099 | 1239986.7634
11 | 2636624.3133 | 1240050.4469 | 2636639.8586 | 1240073.1479
12 | 2636624.3133 | 1240050.4469 | 2636615.9945 | 1240038.3029
13 | 2636673.4665 | 1240001.1974 | 2636656.1504 | 1240019.324
14 | 2636619.4242 | 1239952.8418 | 2636600.7624 | 1239972.4521 | 2636610.3099 | 1239986.7634
15 | 2636749.4173 | 1239992.7489 | 2636736.8353 | 1239970.9174
16 | 2636723.875 | 1239948.4294 | 2636736.8353 | 1239970.9174
17 | 2636778.2364 | 1239973.3749 | 2636762.4767 | 1239988.6067
18 | 2636553.7415 | 1240027.1556 | 2636543.5445 | 1240039.4114
19 | 2636642.9556 | 1240077.6704 | 2636639.8586 | 1240073.1479
20 | 2636615.9945 | 1240038.3029 | 2636613.1485 | 1240034.1481
21 | 2636673.4665 | 1240001.1974 | 2636686.8374 | 1239987.2006
22 | 2636619.4242 | 1239952.8418 | 2636628.7941 | 1239942.9957
23 | 2636788.435 | 1239955.1551 | 2636783.1791 | 1239960.2192
24 | 2636793.4268 | 1239961.1009 | 2636788.435 | 1239955.1551
25 | 2636788.435 | 1239955.1551 | 2636800.204 | 1239943.712
26 | 2636723.875 | 1239948.4294 | 2636743.6634 | 1239927.439
27 | 2636723.875 | 1239948.4294 | 2636700.3641 | 1239973.0407
28 | 2636723.875 | 1239948.4294 | 2636716.0766 | 1239938.0312
29 | 2636793.4268 | 1239961.1009 | 2636787.9797 | 1239963.9579 | 2636778.2364 | 1239973.3749
30 | 2636553.7415 | 1240027.1556 | 2636565.1662 | 1240013.4243
31 | 2636781.8937 | 1240087.3407 | 2636788.3574 | 1240099.3262
32 | 2636778.4897 | 1240081.0288 | 2636781.8937 | 1240087.3407
33 | 2636788.3574 | 1240099.3262 | 2636797.475 | 1240116.233
34 | 2636771.4333 | 1240067.9441 | 2636778.4897 | 1240081.0288
35 | 2636797.475 | 1240116.233 | 2636800.8404 | 1240122.4732
36 | 2636771.4333 | 1240067.9441 | 2636784.5415 | 1240054.9596
37 | 2636771.4333 | 1240067.9441 | 2636765.7643 | 1240057.2562
38 | 2636803.5048 | 1240127.4139 | 2636800.8404 | 1240122.4732
39 | 2636765.7643 | 1240057.2562 | 2636762.1559 | 1240050.4532
40 | 2636803.5048 | 1240127.4139 | 2636818.719 | 1240117.0053
41 | 2636803.5048 | 1240127.4139 | 2636807.2986 | 1240133.2279
42 | 2636700.7371 | 1239917.5779 | 2636716.0766 | 1239938.0312
43 | 2636743.6634 | 1239927.439 | 2636750.2972 | 1239920.4022
44 | 2636686.8374 | 1239987.2006 | 2636700.3641 | 1239973.0407
45 | 2636750.2972 | 1239920.4022 | 2636761.3794 | 1239908.6468
46 | 2636777.0519 | 1239892.0222 | 2636761.3794 | 1239908.6468
47 | 2636793.4268 | 1239961.1009 | 2636808.6722 | 1239947.5867 | 2636812.5628 | 1239942.1073
48 | 2636793.4268 | 1239961.1009 | 2636813.7487 | 1239985.309
49 | 2636812.5628 | 1239942.1073 | 2636818.1468 | 1239934.2591 | 2636834.48 | 1239918.4947 | 2636830.5527 | 1239914.0453
50 | 2636830.5527 | 1239914.0453 | 2636834.48 | 1239918.4947 | 2636841.5202 | 1239925.8097 | 2636852.6627 | 1239937.3972
51 | 2636812.5628 | 1239942.1073 | 2636831.9378 | 1239964.2218
52 | 2636852.6627 | 1239937.3972 | 2636862.0194 | 1239947.1283
53 | 2636832.1753 | 1240007.2593 | 2636813.7487 | 1239985.309
54 | 2637006.1311 | 1239935.1938 | 2636955.9652 | 1239891.4315
55 | 2636955.9652 | 1239891.4315 | 2636985.9544 | 1239864.9789 | 2636993.6227 | 1239864.9155 | 2636998.6677 | 1239859.877 | 2637021.1689 | 1239837.3917 | 2637030.8253 | 1239818.0395 | 2637038.2042 | 1239809.8247
56 | 2637006.1311 | 1239935.1938 | 2637019.0296 | 1239947.682 | 2637025.1798 | 1239948.5209 | 2637034.6001 | 1239945.1774 | 2637150.0026 | 1239832.7926 | 2637166.5611 | 1239817.4641 | 2637166.5175 | 1239814.7732 | 2637177.4235 | 1239808.5041
57 | 2637006.1311 | 1239935.1938 | 2636976.813 | 1239967.3599
58 | 2637038.2042 | 1239809.8247 | 2637046.6566 | 1239818.6385
59 | 2636830.2117 | 1239873.9176 | 2636843.8928 | 1239860.2715
60 | 2636843.8928 | 1239860.2715 | 2636837.649 | 1239850.335
61 | 2636830.2117 | 1239873.9176 | 2636821.0762 | 1239883.0269
62 | 2636854.6885 | 1239798.5768 | 2636847.7882 | 1239805.2605 | 2636835.2308 | 1239820.5814 | 2636829.8924 | 1239827.8307 | 2636829.4239 | 1239836.3221 | 2636835.1467 | 1239846.3528 | 2636837.649 | 1239850.335
63 | 2636892.1847 | 1239670.2165 | 2636890.5668 | 1239672.5746 | 2636913.0667 | 1239690.4924
64 | 2636831.2541 | 1239715.5342 | 2636833.6032 | 1239713.5475 | 2636842.5509 | 1239705.9759 | 2636845.9942 | 1239709.2326 | 2636856.2087 | 1239719.3246 | 2636858.8951 | 1239710.5023 | 2636860.2667 | 1239701.5051 | 2636875.6194 | 1239679.364 | 2636878.4765 | 1239675.9462 | 2636885.7599 | 1239681.8841 | 2636906.8154 | 1239698.581 | 2636913.0667 | 1239690.4924
65 | 2636821.9 | 1239727.6729 | 2636833.4449 | 1239718.3384 | 2636831.2541 | 1239715.5342
66 | 2636790.2905 | 1239784.9692 | 2636771.9759 | 1239757.7532
67 | 2636790.2905 | 1239784.9692 | 2636819.2036 | 1239763.7458 | 2636826.0888 | 1239770.4817 | 2636854.6885 | 1239798.5768
68 | 2636790.2905 | 1239784.9692 | 2636819.2036 | 1239763.7458 | 2636830.6052 | 1239753.1097 | 2636816.9979 | 1239736.5148 | 2636821.7593 | 1239732.0859 | 2636821.9 | 1239727.6729
69 | 2636790.2905 | 1239784.9692 | 2636788.8396 | 1239786.0387 | 2636776.6588 | 1239795.9604
70 | 2636771.9759 | 1239757.7532 | 2636755.9186 | 1239733.8918
71 | 2636854.6885 | 1239798.5768 | 2636875.9318 | 1239817.8182
72 | 2636821.9 | 1239727.6729 | 2636804.7398 | 1239707.1758
73 | 2636762.289 | 1239807.6651 | 2636776.6588 | 1239795.9604
74 | 2636832.1753 | 1240007.2593 | 2636818.2672 | 1240021.3444
75 | 2636832.1753 | 1240007.2593 | 2636841.989 | 1240018.1569
76 | 2637177.4235 | 1239808.5041 | 2637173.5698 | 1239804.3996
77 | 2636964.3535 | 1239981.0297 | 2636976.813 | 1239967.3599
78 | 2636755.9186 | 1239733.8918 | 2636742.1388 | 1239713.4147 | 2636739.6306 | 1239709.3521 | 2636783.5288 | 1239645.9277 | 2636783.7795 | 1239645.5628
79 | 2636783.7795 | 1239645.5628 | 2636674.0413 | 1239563.8989
80 | 2636648.582 | 1239595.7322 | 2636654.4567 | 1239591.7514 | 2636674.0413 | 1239563.8989
81 | 2636762.289 | 1239807.6651 | 2636759.3142 | 1239810.0882
82 | 2636826.8154 | 1240050.6023 | 2636834.5504 | 1240059.1293
83 | 2636848.4467 | 1240074.4486 | 2636834.5504 | 1240059.1293
84 | 2636826.8154 | 1240050.6023 | 2636822.2565 | 1240045.5765
85 | 2636858.0608 | 1240085.0471 | 2636848.4467 | 1240074.4486
86 | 2636808.8898 | 1240030.8412 | 2636822.2565 | 1240045.5765
87 | 2636858.0608 | 1240085.0471 | 2636842.0817 | 1240099.0744
88 | 2636858.0608 | 1240085.0471 | 2636870.4872 | 1240072.4717
89 | 2636808.8898 | 1240030.8412 | 2636818.2672 | 1240021.3444
90 | 2636808.8898 | 1240030.8412 | 2636804.2777 | 1240035.4097
91 | 2636842.0817 | 1240099.0744 | 2636834.0514 | 1240106.1238
92 | 2636881.0283 | 1240061.5079 | 2636870.4872 | 1240072.4717
93 | 2636870.4872 | 1240072.4717 | 2636882.3599 | 1240087.8232
94 | 2636800.6777 | 1240038.9758 | 2636804.2777 | 1240035.4097
95 | 2636824.2229 | 1240113.2399 | 2636832.0276 | 1240107.9004 | 2636834.0514 | 1240106.1238
96 | 2636881.0283 | 1240061.5079 | 2636869.8725 | 1240049.12
97 | 2636881.0283 | 1240061.5079 | 2636897.7438 | 1240045.7579
98 | 2636884.5409 | 1240090.6431 | 2636882.3599 | 1240087.8232
99 | 2636628.7941 | 1239942.9957 | 2636631.8747 | 1239939.7585
100 | 2636643.4418 | 1239927.6036 | 2636631.8747 | 1239939.7585
101 | 2636655.9269 | 1239914.4839 | 2636643.4418 | 1239927.6036
102 | 2636685.9041 | 1239882.9832 | 2636655.9269 | 1239914.4839
103 | 2636685.9041 | 1239882.9832 | 2636582.3294 | 1239775.513
104 | 2636703.9783 | 1239863.9904 | 2636685.9041 | 1239882.9832
105 | 2636473.9267 | 1239827.1131 | 2636476.2975 | 1239831.4193 | 2636483.0634 | 1239821.9214 | 2636501.1731 | 1239797.5393 | 2636503.9969 | 1239793.3428 | 2636515.8721 | 1239775.6934 | 2636527.0604 | 1239759.0738 | 2636536.5621 | 1239744.9565 | 2636544.765 | 1239750.2214 | 2636553.3444 | 1239755.7221 | 2636569.0992 | 1239766.3369 | 2636582.3294 | 1239775.513
106 | 2636595.4302 | 1239756.5927 | 2636582.3294 | 1239775.513
107 | 2636703.9783 | 1239863.9904 | 2636705.722 | 1239862.158
108 | 2636473.9267 | 1239827.1131 | 2636514.3345 | 1239768.8269
109 | 2636599.0323 | 1240013.5408 | 2636613.1485 | 1240034.1481
110 | 2636597.7303 | 1240011.6402 | 2636599.0323 | 1240013.5408
111 | 2636586.1956 | 1239994.8014 | 2636597.7303 | 1240011.6402
112 | 2636575.8992 | 1239979.7703 | 2636586.1956 | 1239994.8014
113 | 2636722.1343 | 1239844.9116 | 2636737.9405 | 1239828.3021
114 | 2636742.9192 | 1239823.4425 | 2636741.3445 | 1239824.7252 | 2636737.9405 | 1239828.3021
115 | 2636722.1343 | 1239844.9116 | 2636705.722 | 1239862.158
116 | 2636742.9192 | 1239823.4425 | 2636759.3142 | 1239810.0882
117 | 2636827.915 | 1240194.4308 | 2636807.297 | 1240210.0156
118 | 2636841.3235 | 1240184.2956 | 2636827.915 | 1240194.4308
119 | 2636841.3235 | 1240184.2956 | 2636850.1136 | 1240177.6459 | 2636861.2595 | 1240169.5207
120 | 2636841.3235 | 1240184.2956 | 2636834.2338 | 1240173.8487
121 | 2636875.0513 | 1240159.4667 | 2636861.2595 | 1240169.5207
122 | 2636824.6644 | 1240159.748 | 2636834.2338 | 1240173.8487
123 | 2636875.0513 | 1240159.4667 | 2636884.488 | 1240172.1187
124 | 2636875.0513 | 1240159.4667 | 2636865.4626 | 1240144.1669
125 | 2636824.6644 | 1240159.748 | 2636823.0776 | 1240157.4098 | 2636815.473 | 1240145.7555
126 | 2636884.488 | 1240172.1187 | 2636885.6791 | 1240173.7156
127 | 2636865.4626 | 1240144.1669 | 2636858.2926 | 1240132.7263
128 | 2636807.2986 | 1240133.2279 | 2636815.473 | 1240145.7555
129 | 2636900.8276 | 1240042.8522 | 2636869.804 | 1240007.4421
130 | 2636900.8276 | 1240042.8522 | 2636897.7438 | 1240045.7579
131 | 2636900.8276 | 1240042.8522 | 2636927.0315 | 1240018.1659
132 | 2636927.0315 | 1240018.1659 | 2636936.5732 | 1240030.8276
133 | 2636964.3535 | 1239981.0297 | 2636927.0315 | 1240018.1659
134 | 2636940.0861 | 1240035.4891 | 2636936.5732 | 1240030.8276
135 | 2636964.3535 | 1239981.0297 | 2636976.8287 | 1239996.4122
136 | 2636818.719 | 1240117.0053 | 2636824.2229 | 1240113.2399
137 | 2636869.8725 | 1240049.12 | 2636856.11 | 1240033.8375
138 | 2636937.0868 | 1240100.3819 | 2636926.1246 | 1240112.1362
139 | 2636940.6912 | 1240096.517 | 2636937.0868 | 1240100.3819
140 | 2636918.9855 | 1240119.7912 | 2636926.1246 | 1240112.1362
141 | 2636940.6912 | 1240096.517 | 2636958.275 | 1240077.6627
142 | 2636918.9855 | 1240119.7912 | 2636914.3457 | 1240124.7662 | 2636911.3972 | 1240124.7289
143 | 2636963.1316 | 1240070.4459 | 2636962.8297 | 1240072.7788 | 2636958.275 | 1240077.6627
144 | 2636911.3972 | 1240124.7289 | 2636910.8978 | 1240124.7226 | 2636907.1281 | 1240119.8484
145 | 2636963.1316 | 1240070.4459 | 2636963.6161 | 1240066.7132 | 2636950.7869 | 1240049.6889
146 | 2636963.1316 | 1240070.4459 | 2636968.0155 | 1240073.0334 | 2636980.1752 | 1240087.7428
147 | 2636940.0861 | 1240035.4891 | 2636950.7869 | 1240049.6889
148 | 2636994.0483 | 1240084.3471 | 2636994.0483 | 1240084.3471 | 2636984.8573 | 1240093.4068 | 2636980.1752 | 1240087.7428
149 | 2636976.8287 | 1239996.4122 | 2636989.8191 | 1240012.4298
150 | 2636998.335 | 1240022.9303 | 2636989.8191 | 1240012.4298
151 | 2636998.335 | 1240022.9303 | 2637008.6965 | 1240035.7064
152 | 2636857.7102 | 1240131.797 | 2636858.2926 | 1240132.7263
153 | 2637017.7983 | 1240046.9292 | 2637008.6965 | 1240035.7064

## bus_geodata
| x | y | coords
0 | 2636673.6005 | 1240134.8173
1 | 2636637.8982 | 1240108.6566
2 | 2636708.7617 | 1240040.4122
3 | 2636509.3555 | 1240080.5033
4 | 2636740.578 | 1240009.7718
5 | 2636641.9494 | 1240034.1896
6 | 2636624.3133 | 1240050.4469
7 | 2636656.1504 | 1240019.324
8 | 2636610.3099 | 1239986.7634
9 | 2636749.4173 | 1239992.7489
10 | 2636736.8353 | 1239970.9174
11 | 2636762.4767 | 1239988.6067
12 | 2636745.8575 | 1240019.7253
13 | 2636543.5445 | 1240039.4114
14 | 2636639.8586 | 1240073.1479
15 | 2636615.9945 | 1240038.3029
16 | 2636673.4665 | 1240001.1974
17 | 2636619.4242 | 1239952.8418
18 | 2636783.1791 | 1239960.2192
19 | 2636788.435 | 1239955.1551
20 | 2636723.875 | 1239948.4294
21 | 2636778.2364 | 1239973.3749
22 | 2636553.7415 | 1240027.1556
23 | 2636781.8937 | 1240087.3407
24 | 2636788.3574 | 1240099.3262
25 | 2636778.4897 | 1240081.0288
26 | 2636797.475 | 1240116.233
27 | 2636771.4333 | 1240067.9441
28 | 2636800.8404 | 1240122.4732
29 | 2636784.5415 | 1240054.9596
30 | 2636765.7643 | 1240057.2562
31 | 2636803.5048 | 1240127.4139
32 | 2636762.1559 | 1240050.4532
33 | 2636716.0766 | 1239938.0312
34 | 2636700.7371 | 1239917.5779
35 | 2636743.6634 | 1239927.439
36 | 2636700.3641 | 1239973.0407
37 | 2636750.2972 | 1239920.4022
38 | 2636686.8374 | 1239987.2006
39 | 2636761.3794 | 1239908.6468
40 | 2636800.204 | 1239943.712
41 | 2636793.4268 | 1239961.1009
42 | 2636830.5527 | 1239914.0453
43 | 2636812.5628 | 1239942.1073
44 | 2636852.6627 | 1239937.3972
45 | 2636813.7487 | 1239985.309
46 | 2636831.9378 | 1239964.2218
47 | 2636862.0194 | 1239947.1283
48 | 2636955.9651 | 1239891.4315
49 | 2637006.1311 | 1239935.1938
50 | 2637038.2042 | 1239809.8247
51 | 2637046.6566 | 1239818.6385
52 | 2636843.8928 | 1239860.2715
53 | 2636830.2117 | 1239873.9176
54 | 2636837.649 | 1239850.335
55 | 2636913.0667 | 1239690.4924
56 | 2636892.1847 | 1239670.2165
57 | 2636831.2541 | 1239715.5342
58 | 2636790.2905 | 1239784.9692
59 | 2636771.9759 | 1239757.7532
60 | 2636854.6885 | 1239798.5768
61 | 2636821.9 | 1239727.6729
62 | 2636776.6588 | 1239795.9604
63 | 2636875.9318 | 1239817.8182
64 | 2636804.7398 | 1239707.1758
65 | 2636832.1753 | 1240007.2593
66 | 2637177.4235 | 1239808.5041
67 | 2636976.813 | 1239967.3599
68 | 2637173.5698 | 1239804.3996
69 | 2636821.0762 | 1239883.0269
70 | 2636783.7795 | 1239645.5628
71 | 2636755.9186 | 1239733.8918
72 | 2636674.0413 | 1239563.8989
73 | 2636762.289 | 1239807.6651
74 | 2636834.5504 | 1240059.1293
75 | 2636826.8154 | 1240050.6023
76 | 2636848.4467 | 1240074.4486
77 | 2636822.2565 | 1240045.5765
78 | 2636858.0608 | 1240085.0471
79 | 2636808.8898 | 1240030.8412
80 | 2636842.0817 | 1240099.0744
81 | 2636870.4872 | 1240072.4717
82 | 2636818.2672 | 1240021.3444
83 | 2636804.2777 | 1240035.4097
84 | 2636834.0514 | 1240106.1238
85 | 2636881.0283 | 1240061.5079
86 | 2636882.3599 | 1240087.8232
87 | 2636631.8747 | 1239939.7585
88 | 2636628.7941 | 1239942.9957
89 | 2636643.4418 | 1239927.6036
90 | 2636655.9269 | 1239914.4839
91 | 2636685.9041 | 1239882.9832
92 | 2636582.3294 | 1239775.513
93 | 2636703.9783 | 1239863.9904
94 | 2636514.3345 | 1239768.8269
95 | 2636473.9267 | 1239827.1131
96 | 2636613.1485 | 1240034.1481
97 | 2636599.0323 | 1240013.5408
98 | 2636597.7303 | 1240011.6402
99 | 2636586.1956 | 1239994.8014
100 | 2636642.9556 | 1240077.6704
101 | 2636575.8992 | 1239979.7703
102 | 2636737.9405 | 1239828.3021
103 | 2636722.1343 | 1239844.9116
104 | 2636742.9192 | 1239823.4425
105 | 2636705.722 | 1239862.158
106 | 2636759.3142 | 1239810.0882
107 | 2636595.4302 | 1239756.5927
108 | 2636827.915 | 1240194.4308
109 | 2636807.297 | 1240210.0156
110 | 2636841.3235 | 1240184.2956
111 | 2636861.2595 | 1240169.5207
112 | 2636834.2338 | 1240173.8487
113 | 2636875.0513 | 1240159.4667
114 | 2636824.6644 | 1240159.748
115 | 2636884.488 | 1240172.1187
116 | 2636865.4626 | 1240144.1669
117 | 2636815.473 | 1240145.7555
118 | 2636777.0519 | 1239892.0222
119 | 2636800.6777 | 1240038.9758
120 | 2636841.989 | 1240018.1569
121 | 2636869.804 | 1240007.4421
122 | 2636900.8276 | 1240042.8522
123 | 2636897.7438 | 1240045.7579
124 | 2636927.0315 | 1240018.1659
125 | 2636936.5732 | 1240030.8276
126 | 2636964.3535 | 1239981.0297
127 | 2636807.2986 | 1240133.2279
128 | 2636818.719 | 1240117.0053
129 | 2636824.2229 | 1240113.2399
130 | 2636869.8725 | 1240049.12
131 | 2636884.5409 | 1240090.6431
132 | 2636565.1662 | 1240013.4243
133 | 2636856.11 | 1240033.8375
134 | 2636648.582 | 1239595.7322
135 | 2636937.0868 | 1240100.3819
136 | 2636926.1246 | 1240112.1362
137 | 2636940.6912 | 1240096.517
138 | 2636918.9855 | 1240119.7912
139 | 2636958.275 | 1240077.6627
140 | 2636911.3972 | 1240124.7289
141 | 2636963.1316 | 1240070.4459
142 | 2636907.1281 | 1240119.8484
143 | 2636950.7869 | 1240049.6889
144 | 2636980.1752 | 1240087.7428
145 | 2636994.0483 | 1240084.3471
146 | 2636940.0861 | 1240035.4891
147 | 2636885.6791 | 1240173.7156
148 | 2636976.8287 | 1239996.4122
149 | 2636989.8191 | 1240012.4298
150 | 2636998.335 | 1240022.9303
151 | 2636858.2926 | 1240132.7263
152 | 2636857.7102 | 1240131.797
153 | 2637008.6965 | 1240035.7064
154 | 2637017.7983 | 1240046.9292
155 | 2636793.4268 | 1239961.1009

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1