## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4289-21_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4289-21_0_8_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_4289-21_0_8_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_4289-21_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4289-21_0_8_node_223 | 0.4 | n |  | TRUE
5 | bus_LV_4289-21_0_8_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_4289-21_0_8_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_4289-21_0_8_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_4289-21_0_8_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_4289-21_0_8_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_4289-21_0_8_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_4289-21_0_8_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_4289-21_0_8_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_4289-21_0_8_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_4289-21_0_8_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_4289-21_0_8_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_4289-21_0_8_node_45 | 0.4 | n |  | TRUE
17 | bus_LV_4289-21_0_8_node_46 | 0.4 | n |  | TRUE
18 | bus_LV_4289-21_0_8_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_4289-21_0_8_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_4289-21_0_8_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_4289-21_0_8_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_4289-21_0_8_node_56 | 0.4 | n |  | TRUE
23 | bus_LV_4289-21_0_8_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_4289-21_0_8_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_4289-21_0_8_node_59 | 0.4 | n |  | TRUE
26 | bus_LV_4289-21_0_8_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_4289-21_0_8_node_50 | 0.4 | n |  | TRUE
28 | bus_LV_4289-21_0_8_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_4289-21_0_8_node_96 | 0.4 | n |  | TRUE
30 | bus_LV_4289-21_0_8_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_4289-21_0_8_node_196 | 0.4 | n |  | TRUE
32 | bus_LV_4289-21_0_8_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_4289-21_0_8_node_195 | 0.4 | n |  | TRUE
34 | bus_LV_4289-21_0_8_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_4289-21_0_8_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_4289-21_0_8_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_4289-21_0_8_node_58 | 0.4 | n |  | TRUE
38 | bus_LV_4289-21_0_8_node_20 | 0.4 | n |  | TRUE
39 | bus_LV_4289-21_0_8_node_21 | 0.4 | n |  | TRUE
40 | bus_LV_4289-21_0_8_node_22 | 0.4 | n |  | TRUE
41 | bus_LV_4289-21_0_8_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_4289-21_0_8_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_4289-21_0_8_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_4289-21_0_8_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_4289-21_0_8_node_35 | 0.4 | n |  | TRUE
46 | bus_LV_4289-21_0_8_node_151 | 0.4 | n |  | TRUE
47 | bus_LV_4289-21_0_8_node_131 | 0.4 | n |  | TRUE
48 | bus_LV_4289-21_0_8_node_150 | 0.4 | n |  | TRUE
49 | bus_LV_4289-21_0_8_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_4289-21_0_8_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_4289-21_0_8_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_4289-21_0_8_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_4289-21_0_8_node_36 | 0.4 | n |  | TRUE
54 | bus_LV_4289-21_0_8_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_4289-21_0_8_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_4289-21_0_8_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_4289-21_0_8_node_53 | 0.4 | n |  | TRUE
58 | bus_LV_4289-21_0_8_node_68 | 0.4 | n |  | TRUE
59 | bus_LV_4289-21_0_8_node_57 | 0.4 | n |  | TRUE
60 | bus_LV_4289-21_0_8_node_66 | 0.4 | n |  | TRUE
61 | bus_LV_4289-21_0_8_node_54 | 0.4 | n |  | TRUE
62 | bus_LV_4289-21_0_8_node_55 | 0.4 | n |  | TRUE
63 | bus_LV_4289-21_0_8_node_154 | 0.4 | n |  | TRUE
64 | bus_LV_4289-21_0_8_node_205 | 0.4 | n |  | TRUE
65 | bus_LV_4289-21_0_8_node_155 | 0.4 | n |  | TRUE
66 | bus_LV_4289-21_0_8_node_117 | 0.4 | n |  | TRUE
67 | bus_LV_4289-21_0_8_node_60 | 0.4 | n |  | TRUE
68 | bus_LV_4289-21_0_8_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_4289-21_0_8_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_4289-21_0_8_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_4289-21_0_8_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_4289-21_0_8_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_4289-21_0_8_node_157 | 0.4 | n |  | TRUE
74 | bus_LV_4289-21_0_8_node_65 | 0.4 | n |  | TRUE
75 | bus_LV_4289-21_0_8_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_4289-21_0_8_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_4289-21_0_8_node_130 | 0.4 | n |  | TRUE
78 | bus_LV_4289-21_0_8_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_4289-21_0_8_node_72 | 0.4 | n |  | TRUE
80 | bus_LV_4289-21_0_8_node_73 | 0.4 | n |  | TRUE
81 | bus_LV_4289-21_0_8_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_4289-21_0_8_node_149 | 0.4 | n |  | TRUE
83 | bus_LV_4289-21_0_8_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_4289-21_0_8_node_111 | 0.4 | n |  | TRUE
85 | bus_LV_4289-21_0_8_node_148 | 0.4 | n |  | TRUE
86 | bus_LV_4289-21_0_8_node_152 | 0.4 | n |  | TRUE
87 | bus_LV_4289-21_0_8_node_153 | 0.4 | n |  | TRUE
88 | bus_LV_4289-21_0_8_node_147 | 0.4 | n |  | TRUE
89 | bus_LV_4289-21_0_8_node_109 | 0.4 | n |  | TRUE
90 | bus_LV_4289-21_0_8_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_4289-21_0_8_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_4289-21_0_8_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_4289-21_0_8_node_79 | 0.4 | n |  | TRUE
94 | bus_LV_4289-21_0_8_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_4289-21_0_8_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_4289-21_0_8_node_116 | 0.4 | n |  | TRUE
97 | bus_LV_4289-21_0_8_node_173 | 0.4 | n |  | TRUE
98 | bus_LV_4289-21_0_8_node_114 | 0.4 | n |  | TRUE
99 | bus_LV_4289-21_0_8_node_174 | 0.4 | n |  | TRUE
100 | bus_LV_4289-21_0_8_node_82 | 0.4 | n |  | TRUE
101 | bus_LV_4289-21_0_8_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_4289-21_0_8_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_4289-21_0_8_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_4289-21_0_8_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_4289-21_0_8_node_87 | 0.4 | n |  | TRUE
106 | bus_LV_4289-21_0_8_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_4289-21_0_8_node_86 | 0.4 | n |  | TRUE
108 | bus_LV_4289-21_0_8_node_225 | 0.4 | n |  | TRUE
109 | bus_LV_4289-21_0_8_node_210 | 0.4 | n |  | TRUE
110 | bus_LV_4289-21_0_8_node_221 | 0.4 | n |  | TRUE
111 | bus_LV_4289-21_0_8_node_192 | 0.4 | n |  | TRUE
112 | bus_LV_4289-21_0_8_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_4289-21_0_8_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_4289-21_0_8_node_211 | 0.4 | n |  | TRUE
115 | bus_LV_4289-21_0_8_node_193 | 0.4 | n |  | TRUE
116 | bus_LV_4289-21_0_8_node_90 | 0.4 | n |  | TRUE
117 | bus_LV_4289-21_0_8_node_91 | 0.4 | n |  | TRUE
118 | bus_LV_4289-21_0_8_node_92 | 0.4 | n |  | TRUE
119 | bus_LV_4289-21_0_8_node_93 | 0.4 | n |  | TRUE
120 | bus_LV_4289-21_0_8_node_94 | 0.4 | n |  | TRUE
121 | bus_LV_4289-21_0_8_node_95 | 0.4 | n |  | TRUE
122 | bus_LV_4289-21_0_8_node_136 | 0.4 | n |  | TRUE
123 | bus_LV_4289-21_0_8_node_159 | 0.4 | n |  | TRUE
124 | bus_LV_4289-21_0_8_node_169 | 0.4 | n |  | TRUE
125 | bus_LV_4289-21_0_8_node_184 | 0.4 | n |  | TRUE
126 | bus_LV_4289-21_0_8_node_160 | 0.4 | n |  | TRUE
127 | bus_LV_4289-21_0_8_node_171 | 0.4 | n |  | TRUE
128 | bus_LV_4289-21_0_8_node_167 | 0.4 | n |  | TRUE
129 | bus_LV_4289-21_0_8_node_97 | 0.4 | n |  | TRUE
130 | bus_LV_4289-21_0_8_node_98 | 0.4 | n |  | TRUE
131 | bus_LV_4289-21_0_8_node_99 | 0.4 | n |  | TRUE
132 | bus_LV_4289-21_0_8_node_100 | 0.4 | n |  | TRUE
133 | bus_LV_4289-21_0_8_node_101 | 0.4 | n |  | TRUE
134 | bus_LV_4289-21_0_8_node_102 | 0.4 | n |  | TRUE
135 | bus_LV_4289-21_0_8_node_187 | 0.4 | n |  | TRUE
136 | bus_LV_4289-21_0_8_node_113 | 0.4 | n |  | TRUE
137 | bus_LV_4289-21_0_8_node_104 | 0.4 | n |  | TRUE
138 | bus_LV_4289-21_0_8_node_106 | 0.4 | n |  | TRUE
139 | bus_LV_4289-21_0_8_node_170 | 0.4 | n |  | TRUE
140 | bus_LV_4289-21_0_8_node_168 | 0.4 | n |  | TRUE
141 | bus_LV_4289-21_0_8_node_107 | 0.4 | n |  | TRUE
142 | bus_LV_4289-21_0_8_node_108 | 0.4 | n |  | TRUE
143 | bus_LV_4289-21_0_8_node_110 | 0.4 | n |  | TRUE
144 | bus_LV_4289-21_0_8_node_112 | 0.4 | n |  | TRUE
145 | bus_LV_4289-21_0_8_node_212 | 0.4 | n |  | TRUE
146 | bus_LV_4289-21_0_8_node_204 | 0.4 | n |  | TRUE
147 | bus_LV_4289-21_0_8_node_202 | 0.4 | n |  | TRUE
148 | bus_LV_4289-21_0_8_node_115 | 0.4 | n |  | TRUE
149 | bus_LV_4289-21_0_8_node_118 | 0.4 | n |  | TRUE
150 | bus_LV_4289-21_0_8_node_140 | 0.4 | n |  | TRUE
151 | bus_LV_4289-21_0_8_node_206 | 0.4 | n |  | TRUE
152 | bus_LV_4289-21_0_8_node_138 | 0.4 | n |  | TRUE
153 | bus_LV_4289-21_0_8_node_119 | 0.4 | n |  | TRUE
154 | bus_LV_4289-21_0_8_node_120 | 0.4 | n |  | TRUE
155 | bus_LV_4289-21_0_8_node_121 | 0.4 | n |  | TRUE
156 | bus_LV_4289-21_0_8_node_122 | 0.4 | n |  | TRUE
157 | bus_LV_4289-21_0_8_node_123 | 0.4 | n |  | TRUE
158 | bus_LV_4289-21_0_8_node_124 | 0.4 | n |  | TRUE
159 | bus_LV_4289-21_0_8_node_185 | 0.4 | n |  | TRUE
160 | bus_LV_4289-21_0_8_node_134 | 0.4 | n |  | TRUE
161 | bus_LV_4289-21_0_8_node_213 | 0.4 | n |  | TRUE
162 | bus_LV_4289-21_0_8_node_186 | 0.4 | n |  | TRUE
163 | bus_LV_4289-21_0_8_node_132 | 0.4 | n |  | TRUE
164 | bus_LV_4289-21_0_8_node_214 | 0.4 | n |  | TRUE
165 | bus_LV_4289-21_0_8_node_125 | 0.4 | n |  | TRUE
166 | bus_LV_4289-21_0_8_node_126 | 0.4 | n |  | TRUE
167 | bus_LV_4289-21_0_8_node_127 | 0.4 | n |  | TRUE
168 | bus_LV_4289-21_0_8_node_128 | 0.4 | n |  | TRUE
169 | bus_LV_4289-21_0_8_node_129 | 0.4 | n |  | TRUE
170 | bus_LV_4289-21_0_8_node_182 | 0.4 | n |  | TRUE
171 | bus_LV_4289-21_0_8_node_158 | 0.4 | n |  | TRUE
172 | bus_LV_4289-21_0_8_node_198 | 0.4 | n |  | TRUE
173 | bus_LV_4289-21_0_8_node_179 | 0.4 | n |  | TRUE
174 | bus_LV_4289-21_0_8_node_180 | 0.4 | n |  | TRUE
175 | bus_LV_4289-21_0_8_node_216 | 0.4 | n |  | TRUE
176 | bus_LV_4289-21_0_8_node_133 | 0.4 | n |  | TRUE
177 | bus_LV_4289-21_0_8_node_135 | 0.4 | n |  | TRUE
178 | bus_LV_4289-21_0_8_node_199 | 0.4 | n |  | TRUE
179 | bus_LV_4289-21_0_8_node_200 | 0.4 | n |  | TRUE
180 | bus_LV_4289-21_0_8_node_183 | 0.4 | n |  | TRUE
181 | bus_LV_4289-21_0_8_node_137 | 0.4 | n |  | TRUE
182 | bus_LV_4289-21_0_8_node_139 | 0.4 | n |  | TRUE
183 | bus_LV_4289-21_0_8_node_141 | 0.4 | n |  | TRUE
184 | bus_LV_4289-21_0_8_node_142 | 0.4 | n |  | TRUE
185 | bus_LV_4289-21_0_8_node_143 | 0.4 | n |  | TRUE
186 | bus_LV_4289-21_0_8_node_144 | 0.4 | n |  | TRUE
187 | bus_LV_4289-21_0_8_node_145 | 0.4 | n |  | TRUE
188 | bus_LV_4289-21_0_8_node_146 | 0.4 | n |  | TRUE
189 | bus_LV_4289-21_0_8_node_172 | 0.4 | n |  | TRUE
190 | bus_LV_4289-21_0_8_node_177 | 0.4 | n |  | TRUE
191 | bus_LV_4289-21_0_8_node_156 | 0.4 | n |  | TRUE
192 | bus_LV_4289-21_0_8_node_197 | 0.4 | n |  | TRUE
193 | bus_LV_4289-21_0_8_node_217 | 0.4 | n |  | TRUE
194 | bus_LV_4289-21_0_8_node_218 | 0.4 | n |  | TRUE
195 | bus_LV_4289-21_0_8_node_219 | 0.4 | n |  | TRUE
196 | bus_LV_4289-21_0_8_node_220 | 0.4 | n |  | TRUE
197 | bus_LV_4289-21_0_8_node_224 | 0.4 | n |  | TRUE
198 | bus_LV_4289-21_0_8_node_161 | 0.4 | n |  | TRUE
199 | bus_LV_4289-21_0_8_node_162 | 0.4 | n |  | TRUE
200 | bus_LV_4289-21_0_8_node_163 | 0.4 | n |  | TRUE
201 | bus_LV_4289-21_0_8_node_164 | 0.4 | n |  | TRUE
202 | bus_LV_4289-21_0_8_node_165 | 0.4 | n |  | TRUE
203 | bus_LV_4289-21_0_8_node_166 | 0.4 | n |  | TRUE
204 | bus_LV_4289-21_0_8_node_215 | 0.4 | n |  | TRUE
205 | bus_LV_4289-21_0_8_node_189 | 0.4 | n |  | TRUE
206 | bus_LV_4289-21_0_8_node_226 | 0.4 | n |  | TRUE
207 | bus_LV_4289-21_0_8_node_188 | 0.4 | n |  | TRUE
208 | bus_LV_4289-21_0_8_node_175 | 0.4 | n |  | TRUE
209 | bus_LV_4289-21_0_8_node_176 | 0.4 | n |  | TRUE
210 | bus_LV_4289-21_0_8_node_178 | 0.4 | n |  | TRUE
211 | bus_LV_4289-21_0_8_node_209 | 0.4 | n |  | TRUE
212 | bus_LV_4289-21_0_8_node_208 | 0.4 | n |  | TRUE
213 | bus_LV_4289-21_0_8_node_181 | 0.4 | n |  | TRUE
214 | bus_LV_4289-21_0_8_node_201 | 0.4 | n |  | TRUE
215 | bus_LV_4289-21_0_8_node_190 | 0.4 | n |  | TRUE
216 | bus_LV_4289-21_0_8_node_191 | 0.4 | n |  | TRUE
217 | bus_LV_4289-21_0_8_node_222 | 0.4 | n |  | TRUE
218 | bus_LV_4289-21_0_8_node_194 | 0.4 | n |  | TRUE
219 | bus_LV_4289-21_0_8_node_207 | 0.4 | n |  | TRUE
220 | bus_LV_4289-21_0_8_node_203 | 0.4 | n |  | TRUE
221 | bus_MV_617_0_node_106 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4289-21_0_8_load_0 | 0 | 0.0068068 | 0.001706 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4289-21_0_8_load_5 | 2 | 0.017153 | 0.004299 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4289-21_0_8_load_223 | 4 | 0.0073401 | 0.0018396 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4289-21_0_8_load_37 | 8 | 0.0084987 | 0.00213 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4289-21_0_8_load_8 | 12 | 0.0024076 | 0.0006034 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4289-21_0_8_load_40 | 14 | 0.0091244 | 0.0022868 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4289-21_0_8_load_46 | 17 | 0.0087838 | 0.0022014 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4289-21_0_8_load_43 | 18 | 0.0042598 | 0.0010676 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4289-21_0_8_load_13 | 19 | 0.0050544 | 0.0012667 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4289-21_0_8_load_18 | 20 | 0.0024978 | 0.00062601 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4289-21_0_8_load_56 | 22 | 0.0030703 | 0.0007695 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4289-21_0_8_load_15 | 23 | 0.0024076 | 0.00060341 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4289-21_0_8_load_16 | 24 | 0.0030882 | 0.00077398 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4289-21_0_8_load_59 | 25 | 0.0045734 | 0.0011462 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4289-21_0_8_load_28 | 26 | 0.0046089 | 0.0011551 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4289-21_0_8_load_49 | 28 | 0.0066473 | 0.001666 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4289-21_0_8_load_96 | 29 | 0.0039027 | 0.0009781 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4289-21_0_8_load_196 | 31 | 0.0025221 | 0.00063209 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4289-21_0_8_load_29 | 32 | 0.0047443 | 0.001189 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4289-21_0_8_load_195 | 33 | 0.0031582 | 0.00079151 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4289-21_0_8_load_27 | 34 | 0.0017524 | 0.0004392 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4289-21_0_8_load_58 | 37 | 0.021888 | 0.0054858 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4289-21_0_8_load_20 | 38 | 0.0043785 | 0.0010973 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4289-21_0_8_load_21 | 39 | 0.0048568 | 0.0012172 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4289-21_0_8_load_23 | 41 | 0.0051113 | 0.001281 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4289-21_0_8_load_24 | 42 | 0.0097228 | 0.0024368 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4289-21_0_8_load_34 | 43 | 0.0044908 | 0.0011255 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4289-21_0_8_load_31 | 44 | 0.0045757 | 0.0011468 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4289-21_0_8_load_35 | 45 | 0.0051818 | 0.0012987 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4289-21_0_8_load_131 | 47 | 0.0016059 | 0.00040248 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4289-21_0_8_load_32 | 49 | 0.0045252 | 0.0011341 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4289-21_0_8_load_33 | 50 | 0.0047389 | 0.0011877 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4289-21_0_8_load_47 | 51 | 0.0045528 | 0.001141 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4289-21_0_8_load_48 | 52 | 0.0017835 | 0.00044698 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4289-21_0_8_load_36 | 53 | 0.0084299 | 0.0021127 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4289-21_0_8_load_41 | 54 | 0.0059774 | 0.0014981 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4289-21_0_8_load_42 | 55 | 0.002615 | 0.00065539 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4289-21_0_8_load_52 | 56 | 0.002288 | 0.00057342 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4289-21_0_8_load_68 | 58 | 0.0058843 | 0.0014747 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4289-21_0_8_load_57 | 59 | 0.0034434 | 0.00086299 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4289-21_0_8_load_66 | 60 | 0.0015838 | 0.00039695 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4289-21_0_8_load_55 | 62 | 0.0015781 | 0.0003955 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4289-21_0_8_load_154 | 63 | 0.0025229 | 0.0006323 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4289-21_0_8_load_205 | 64 | 0.0025256 | 0.00063297 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4289-21_0_8_load_155 | 65 | 0.002761 | 0.00069198 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4289-21_0_8_load_60 | 67 | 0.0023855 | 0.00059786 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4289-21_0_8_load_61 | 68 | 0.0017342 | 0.00043464 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4289-21_0_8_load_63 | 70 | 0.0021005 | 0.00052644 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4289-21_0_8_load_64 | 71 | 0.0023574 | 0.00059082 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4289-21_0_8_load_70 | 72 | 0.00092448 | 0.0002317 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4289-21_0_8_load_157 | 73 | 0.0018866 | 0.00047282 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4289-21_0_8_load_65 | 74 | 0.0013939 | 0.00034934 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4289-21_0_8_load_67 | 75 | 0.002201 | 0.00055162 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4289-21_0_8_load_69 | 76 | 0.0019551 | 0.00049001 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4289-21_0_8_load_71 | 78 | 0.0038147 | 0.00095606 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4289-21_0_8_load_72 | 79 | 0.0039265 | 0.00098406 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4289-21_0_8_load_73 | 80 | 0.0033595 | 0.00084197 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4289-21_0_8_load_149 | 82 | 0.0018994 | 0.00047603 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4289-21_0_8_load_75 | 83 | 0.004176 | 0.0010466 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4289-21_0_8_load_148 | 85 | 0.0033033 | 0.00082789 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4289-21_0_8_load_152 | 86 | 0.0022281 | 0.00055841 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4289-21_0_8_load_153 | 87 | 0.002298 | 0.00057594 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4289-21_0_8_load_147 | 88 | 0.0026314 | 0.0006595 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4289-21_0_8_load_76 | 90 | 0.0033608 | 0.00084229 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4289-21_0_8_load_77 | 91 | 0.0022151 | 0.00055517 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4289-21_0_8_load_79 | 93 | 0.002298 | 0.00057594 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4289-21_0_8_load_80 | 94 | 0.0010747 | 0.00026935 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4289-21_0_8_load_81 | 95 | 0.0026412 | 0.00066194 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4289-21_0_8_load_173 | 97 | 0.00296 | 0.00074185 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4289-21_0_8_load_114 | 98 | 0.0028106 | 0.0007044 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4289-21_0_8_load_174 | 99 | 0.0016812 | 0.00042136 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4289-21_0_8_load_82 | 100 | 0.00083092 | 0.00020825 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4289-21_0_8_load_89 | 106 | 0.00066124 | 0.00016572 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4289-21_0_8_load_225 | 108 | 0.0010203 | 0.0002557 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4289-21_0_8_load_210 | 109 | 0.0014165 | 0.00035501 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4289-21_0_8_load_221 | 110 | 0.0059208 | 0.0014839 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4289-21_0_8_load_192 | 111 | 0.00053095 | 0.00013307 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4289-21_0_8_load_105 | 112 | 0.0012203 | 0.00030583 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4289-21_0_8_load_103 | 113 | 0.001221 | 0.00030602 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4289-21_0_8_load_211 | 114 | 0.00094148 | 0.00023596 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4289-21_0_8_load_193 | 115 | 0.00081335 | 0.00020384 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4289-21_0_8_load_90 | 116 | 0.0014642 | 0.00036696 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4289-21_0_8_load_91 | 117 | 0.0018939 | 0.00047467 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4289-21_0_8_load_93 | 119 | 0.0024602 | 0.00061659 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4289-21_0_8_load_94 | 120 | 0.0010312 | 0.00025844 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4289-21_0_8_load_95 | 121 | 0.0018477 | 0.00046308 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4289-21_0_8_load_136 | 122 | 0.0030738 | 0.00077036 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4289-21_0_8_load_159 | 123 | 0.0020211 | 0.00050654 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4289-21_0_8_load_160 | 126 | 0.0020572 | 0.00051557 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4289-21_0_8_load_171 | 127 | 0.0020704 | 0.00051888 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4289-21_0_8_load_167 | 128 | 0.0017333 | 0.0004344 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4289-21_0_8_load_97 | 129 | 0.002715 | 0.00068045 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4289-21_0_8_load_98 | 130 | 0.0015574 | 0.00039033 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4289-21_0_8_load_100 | 132 | 0.0039953 | 0.0010013 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4289-21_0_8_load_101 | 133 | 0.0027917 | 0.00069967 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4289-21_0_8_load_102 | 134 | 0.0022158 | 0.00055533 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4289-21_0_8_load_187 | 135 | 0.0031409 | 0.00078719 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4289-21_0_8_load_113 | 136 | 0.0016812 | 0.00042135 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4289-21_0_8_load_104 | 137 | 0.0030185 | 0.0007565 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4289-21_0_8_load_106 | 138 | 0.0033726 | 0.00084526 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4289-21_0_8_load_170 | 139 | 0.0032245 | 0.00080815 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4289-21_0_8_load_168 | 140 | 0.002433 | 0.00060977 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4289-21_0_8_load_107 | 141 | 0.0017964 | 0.00045023 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4289-21_0_8_load_108 | 142 | 0.002421 | 0.00060676 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4289-21_0_8_load_110 | 143 | 0.0038838 | 0.00097337 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4289-21_0_8_load_212 | 145 | 0.011395 | 0.0028558 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4289-21_0_8_load_204 | 146 | 0.0023127 | 0.00057963 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4289-21_0_8_load_202 | 147 | 0.0032089 | 0.00080424 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4289-21_0_8_load_115 | 148 | 0.0022949 | 0.00057515 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4289-21_0_8_load_118 | 149 | 0.0019965 | 0.00050037 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4289-21_0_8_load_140 | 150 | 0.001843 | 0.0004619 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4289-21_0_8_load_206 | 151 | 0.0046325 | 0.001161 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4289-21_0_8_load_138 | 152 | 0.0025507 | 0.00063925 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4289-21_0_8_load_119 | 153 | 0.0010759 | 0.00026965 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4289-21_0_8_load_120 | 154 | 0.0024334 | 0.00060987 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4289-21_0_8_load_122 | 156 | 0.00186 | 0.00046617 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4289-21_0_8_load_123 | 157 | 0.0033609 | 0.00084231 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4289-21_0_8_load_124 | 158 | 0.0013097 | 0.00032825 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4289-21_0_8_load_185 | 159 | 0.002667 | 0.0006684 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4289-21_0_8_load_134 | 160 | 0.0033261 | 0.00083359 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4289-21_0_8_load_213 | 161 | 0.0084422 | 0.0021158 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4289-21_0_8_load_186 | 162 | 0.00068569 | 0.00017185 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4289-21_0_8_load_132 | 163 | 0.0068002 | 0.0017043 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4289-21_0_8_load_125 | 165 | 0.000556 | 0.00013935 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4289-21_0_8_load_126 | 166 | 0.0026433 | 0.00066246 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4289-21_0_8_load_128 | 168 | 0.0043473 | 0.0010895 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4289-21_0_8_load_198 | 172 | 0.003177 | 0.00079623 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4289-21_0_8_load_179 | 173 | 0.0028692 | 0.00071909 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4289-21_0_8_load_180 | 174 | 0.0016383 | 0.0004106 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4289-21_0_8_load_216 | 175 | 0.00080549 | 0.00020188 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4289-21_0_8_load_133 | 176 | 0.0052861 | 0.0013248 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4289-21_0_8_load_135 | 177 | 0.0023199 | 0.00058142 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4289-21_0_8_load_199 | 178 | 0.0020439 | 0.00051224 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4289-21_0_8_load_183 | 180 | 0.0023064 | 0.00057804 | 0 | 0 |  | 1 | TRUE | wye
134 | LV_4289-21_0_8_load_137 | 181 | 0.0018721 | 0.00046918 | 0 | 0 |  | 1 | TRUE | wye
135 | LV_4289-21_0_8_load_139 | 182 | 0.0019885 | 0.00049836 | 0 | 0 |  | 1 | TRUE | wye
136 | LV_4289-21_0_8_load_141 | 183 | 0.0015316 | 0.00038386 | 0 | 0 |  | 1 | TRUE | wye
137 | LV_4289-21_0_8_load_142 | 184 | 0.001598 | 0.0004005 | 0 | 0 |  | 1 | TRUE | wye
138 | LV_4289-21_0_8_load_143 | 185 | 0.0027666 | 0.00069337 | 0 | 0 |  | 1 | TRUE | wye
139 | LV_4289-21_0_8_load_144 | 186 | 0.0024543 | 0.00061512 | 0 | 0 |  | 1 | TRUE | wye
140 | LV_4289-21_0_8_load_145 | 187 | 0.0020791 | 0.00052107 | 0 | 0 |  | 1 | TRUE | wye
141 | LV_4289-21_0_8_load_146 | 188 | 0.0031306 | 0.00078461 | 0 | 0 |  | 1 | TRUE | wye
142 | LV_4289-21_0_8_load_172 | 189 | 0.003128 | 0.00078395 | 0 | 0 |  | 1 | TRUE | wye
143 | LV_4289-21_0_8_load_177 | 190 | 0.0032876 | 0.00082394 | 0 | 0 |  | 1 | TRUE | wye
144 | LV_4289-21_0_8_load_156 | 191 | 0.0025192 | 0.00063137 | 0 | 0 |  | 1 | TRUE | wye
145 | LV_4289-21_0_8_load_197 | 192 | 0.0015688 | 0.00039317 | 0 | 0 |  | 1 | TRUE | wye
146 | LV_4289-21_0_8_load_217 | 193 | 0.0010466 | 0.00026229 | 0 | 0 |  | 1 | TRUE | wye
147 | LV_4289-21_0_8_load_218 | 194 | 0.00046826 | 0.00011736 | 0 | 0 |  | 1 | TRUE | wye
148 | LV_4289-21_0_8_load_224 | 197 | 0.0022265 | 0.000558 | 0 | 0 |  | 1 | TRUE | wye
149 | LV_4289-21_0_8_load_161 | 198 | 0.0021425 | 0.00053697 | 0 | 0 |  | 1 | TRUE | wye
150 | LV_4289-21_0_8_load_162 | 199 | 0.0032442 | 0.00081307 | 0 | 0 |  | 1 | TRUE | wye
151 | LV_4289-21_0_8_load_165 | 202 | 0.0016638 | 0.00041698 | 0 | 0 |  | 1 | TRUE | wye
152 | LV_4289-21_0_8_load_166 | 203 | 0.0041425 | 0.0010382 | 0 | 0 |  | 1 | TRUE | wye
153 | LV_4289-21_0_8_load_189 | 205 | 0.0012024 | 0.00030135 | 0 | 0 |  | 1 | TRUE | wye
154 | LV_4289-21_0_8_load_226 | 206 | 0.0011705 | 0.00029336 | 0 | 0 |  | 1 | TRUE | wye
155 | LV_4289-21_0_8_load_188 | 207 | 0.0013943 | 0.00034945 | 0 | 0 |  | 1 | TRUE | wye
156 | LV_4289-21_0_8_load_175 | 208 | 0.0029022 | 0.00072737 | 0 | 0 |  | 1 | TRUE | wye
157 | LV_4289-21_0_8_load_176 | 209 | 0.0021662 | 0.0005429 | 0 | 0 |  | 1 | TRUE | wye
158 | LV_4289-21_0_8_load_178 | 210 | 0.0038532 | 0.00096569 | 0 | 0 |  | 1 | TRUE | wye
159 | LV_4289-21_0_8_load_209 | 211 | 0.0043165 | 0.0010818 | 0 | 0 |  | 1 | TRUE | wye
160 | LV_4289-21_0_8_load_208 | 212 | 0.0030119 | 0.00075487 | 0 | 0 |  | 1 | TRUE | wye
161 | LV_4289-21_0_8_load_181 | 213 | 0.004391 | 0.0011005 | 0 | 0 |  | 1 | TRUE | wye
162 | LV_4289-21_0_8_load_201 | 214 | 0.00375 | 0.00093984 | 0 | 0 |  | 1 | TRUE | wye
163 | LV_4289-21_0_8_load_190 | 215 | 0.00050975 | 0.00012776 | 0 | 0 |  | 1 | TRUE | wye
164 | LV_4289-21_0_8_load_191 | 216 | 0.00052711 | 0.00013211 | 0 | 0 |  | 1 | TRUE | wye
165 | LV_4289-21_0_8_load_222 | 217 | 0.001318 | 0.00033033 | 0 | 0 |  | 1 | TRUE | wye
166 | LV_4289-21_0_8_load_194 | 218 | 0.0010367 | 0.00025982 | 0 | 0 |  | 1 | TRUE | wye
167 | LV_4289-21_0_8_load_207 | 219 | 0.0037745 | 0.00094597 | 0 | 0 |  | 1 | TRUE | wye
168 | LV_4289-21_0_8_load_203 | 220 | 0.0022852 | 0.00057272 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 96 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4289-21_0_8_line_0 |  | 0 | 1 | 0.037798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4289-21_0_8_line_1 |  | 1 | 2 | 0.056047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4289-21_0_8_line_2 |  | 1 | 3 | 0.037685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4289-21_0_8_line_3 |  | 2 | 5 | 0.027632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4289-21_0_8_line_4 |  | 3 | 4 | 0.047961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4289-21_0_8_line_5 |  | 5 | 9 | 0.030733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4289-21_0_8_line_6 |  | 6 | 7 | 0.048579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4289-21_0_8_line_7 |  | 6 | 8 | 0.021437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4289-21_0_8_line_8 |  | 7 | 19 | 0.033064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4289-21_0_8_line_9 |  | 7 | 12 | 0.024492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4289-21_0_8_line_10 |  | 8 | 13 | 0.020095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4289-21_0_8_line_11 |  | 9 | 36 | 0.039497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4289-21_0_8_line_12 |  | 9 | 37 | 0.028576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4289-21_0_8_line_13 |  | 10 | 11 | 0.00488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4289-21_0_8_line_14 |  | 10 | 12 | 0.010935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4289-21_0_8_line_15 |  | 11 | 20 | 0.019584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4289-21_0_8_line_16 |  | 13 | 14 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4289-21_0_8_line_17 |  | 15 | 16 | 0.035681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4289-21_0_8_line_18 |  | 15 | 17 | 0.013372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4289-21_0_8_line_19 |  | 15 | 18 | 0.024143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4289-21_0_8_line_20 |  | 16 | 27 | 0.051947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4289-21_0_8_line_21 |  | 16 | 28 | 0.019808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4289-21_0_8_line_22 |  | 17 | 29 | 0.023631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4289-21_0_8_line_23 |  | 19 | 21 | 0.029583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4289-21_0_8_line_24 |  | 20 | 22 | 0.02257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4289-21_0_8_line_25 |  | 21 | 25 | 0.017492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4289-21_0_8_line_26 |  | 21 | 26 | 0.0018091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4289-21_0_8_line_27 |  | 22 | 35 | 0.015141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4289-21_0_8_line_28 |  | 23 | 24 | 0.022838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4289-21_0_8_line_29 |  | 24 | 30 | 0.020201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4289-21_0_8_line_30 |  | 25 | 29 | 0.018958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4289-21_0_8_line_31 |  | 26 | 34 | 0.021476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4289-21_0_8_line_32 |  | 27 | 58 | 0.037756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4289-21_0_8_line_33 |  | 30 | 31 | 0.032236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4289-21_0_8_line_34 |  | 30 | 32 | 0.014315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4289-21_0_8_line_35 |  | 31 | 33 | 0.0026512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4289-21_0_8_line_36 |  | 32 | 34 | 0.0060058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4289-21_0_8_line_37 |  | 33 | 213 | 0.031341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4289-21_0_8_line_38 |  | 35 | 59 | 0.0097514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_4289-21_0_8_line_39 |  | 35 | 52 | 0.015148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4289-21_0_8_line_40 |  | 36 | 44 | 0.0022545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4289-21_0_8_line_41 |  | 38 | 39 | 0.021999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4289-21_0_8_line_42 |  | 38 | 40 | 0.018234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4289-21_0_8_line_43 |  | 39 | 41 | 0.0058088 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4289-21_0_8_line_44 |  | 40 | 42 | 0.027434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4289-21_0_8_line_45 |  | 41 | 43 | 0.016375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4289-21_0_8_line_46 |  | 43 | 45 | 0.0057564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4289-21_0_8_line_47 |  | 44 | 49 | 0.021757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4289-21_0_8_line_48 |  | 45 | 53 | 0.021163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4289-21_0_8_line_49 |  | 46 | 47 | 0.035077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4289-21_0_8_line_50 |  | 46 | 48 | 0.022906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4289-21_0_8_line_51 |  | 47 | 93 | 0.0090949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4289-21_0_8_line_52 |  | 48 | 85 | 0.0017169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4289-21_0_8_line_53 |  | 49 | 50 | 0.02461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4289-21_0_8_line_54 |  | 50 | 51 | 0.02629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4289-21_0_8_line_55 |  | 51 | 52 | 0.032467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4289-21_0_8_line_56 |  | 53 | 54 | 0.00093121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4289-21_0_8_line_57 |  | 54 | 55 | 0.014221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4289-21_0_8_line_58 |  | 55 | 56 | 0.01917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4289-21_0_8_line_59 |  | 56 | 57 | 0.014638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4289-21_0_8_line_60 |  | 57 | 61 | 0.005487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_4289-21_0_8_line_61 |  | 57 | 62 | 0.014498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_4289-21_0_8_line_62 |  | 58 | 60 | 0.034615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4289-21_0_8_line_63 |  | 59 | 61 | 0.037654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_4289-21_0_8_line_64 |  | 60 | 74 | 0.0283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4289-21_0_8_line_65 |  | 61 | 63 | 0.011268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4289-21_0_8_line_66 |  | 62 | 64 | 0.003488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_4289-21_0_8_line_67 |  | 63 | 65 | 0.02843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4289-21_0_8_line_68 |  | 64 | 66 | 0.0071626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_4289-21_0_8_line_69 |  | 65 | 191 | 0.0080559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4289-21_0_8_line_70 |  | 66 | 148 | 0.0082101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_4289-21_0_8_line_71 |  | 67 | 68 | 0.018852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4289-21_0_8_line_72 |  | 67 | 69 | 0.018232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4289-21_0_8_line_73 |  | 68 | 70 | 0.068308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4289-21_0_8_line_74 |  | 69 | 71 | 0.04544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4289-21_0_8_line_75 |  | 70 | 72 | 0.053045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4289-21_0_8_line_76 |  | 72 | 73 | 0.015182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4289-21_0_8_line_77 |  | 73 | 77 | 0.029663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4289-21_0_8_line_78 |  | 74 | 75 | 0.055842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4289-21_0_8_line_79 |  | 75 | 76 | 0.02695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4289-21_0_8_line_80 |  | 77 | 171 | 0.019104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4289-21_0_8_line_81 |  | 77 | 167 | 0.1037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4289-21_0_8_line_82 |  | 78 | 79 | 0.02323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4289-21_0_8_line_83 |  | 78 | 80 | 0.035012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4289-21_0_8_line_84 |  | 79 | 81 | 0.024522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4289-21_0_8_line_85 |  | 81 | 82 | 0.017629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4289-21_0_8_line_86 |  | 82 | 85 | 0.033419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4289-21_0_8_line_87 |  | 83 | 84 | 0.010782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4289-21_0_8_line_88 |  | 84 | 88 | 0.034826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4289-21_0_8_line_89 |  | 84 | 89 | 0.013428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4289-21_0_8_line_90 |  | 86 | 87 | 0.0020498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4289-21_0_8_line_91 |  | 87 | 134 | 0.022979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4289-21_0_8_line_92 |  | 89 | 144 | 0.00296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_4289-21_0_8_line_93 |  | 89 | 141 | 0.0196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_4289-21_0_8_line_94 |  | 90 | 91 | 0.020131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4289-21_0_8_line_95 |  | 90 | 92 | 0.017047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4289-21_0_8_line_96 |  | 91 | 93 | 0.010154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4289-21_0_8_line_97 |  | 92 | 94 | 0.0035122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_4289-21_0_8_line_98 |  | 92 | 95 | 0.019439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_4289-21_0_8_line_99 |  | 94 | 96 | 0.034725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_4289-21_0_8_line_100 |  | 95 | 97 | 0.0026209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_4289-21_0_8_line_101 |  | 96 | 98 | 0.028362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_4289-21_0_8_line_102 |  | 97 | 99 | 0.021168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_4289-21_0_8_line_103 |  | 98 | 148 | 0.019525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_4289-21_0_8_line_104 |  | 99 | 133 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_4289-21_0_8_line_105 |  | 100 | 101 | 0.020674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4289-21_0_8_line_106 |  | 100 | 102 | 0.035647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4289-21_0_8_line_107 |  | 101 | 103 | 0.007372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4289-21_0_8_line_108 |  | 101 | 104 | 0.13378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4289-21_0_8_line_109 |  | 102 | 105 | 0.005316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4289-21_0_8_line_110 |  | 102 | 106 | 0.011487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4289-21_0_8_line_111 |  | 103 | 107 | 0.049319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4289-21_0_8_line_112 |  | 104 | 110 | 0.038961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4289-21_0_8_line_113 |  | 105 | 109 | 0.020695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4289-21_0_8_line_114 |  | 106 | 111 | 0.02489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4289-21_0_8_line_115 |  | 107 | 108 | 0.028009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4289-21_0_8_line_116 |  | 109 | 114 | 0.035042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4289-21_0_8_line_117 |  | 111 | 115 | 0.013184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4289-21_0_8_line_118 |  | 112 | 113 | 0.027946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4289-21_0_8_line_119 |  | 113 | 137 | 0.026973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4289-21_0_8_line_120 |  | 115 | 218 | 0.012937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4289-21_0_8_line_121 |  | 116 | 117 | 0.026605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_4289-21_0_8_line_122 |  | 116 | 118 | 0.035789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_4289-21_0_8_line_123 |  | 117 | 119 | 0.026151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_4289-21_0_8_line_124 |  | 118 | 120 | 0.014733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4289-21_0_8_line_125 |  | 118 | 121 | 0.015931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_4289-21_0_8_line_126 |  | 119 | 122 | 0.023432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
127 | LV_4289-21_0_8_line_127 |  | 120 | 123 | 0.023685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4289-21_0_8_line_128 |  | 121 | 124 | 0.084322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_4289-21_0_8_line_129 |  | 122 | 125 | 0.0051154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_4289-21_0_8_line_130 |  | 123 | 126 | 0.023548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4289-21_0_8_line_131 |  | 124 | 127 | 0.024015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_4289-21_0_8_line_132 |  | 124 | 128 | 0.028907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4289-21_0_8_line_133 |  | 125 | 179 | 0.017089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_4289-21_0_8_line_134 |  | 125 | 180 | 0.015769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4289-21_0_8_line_135 |  | 126 | 151 | 0.030689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4289-21_0_8_line_136 |  | 127 | 188 | 0.025784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
137 | LV_4289-21_0_8_line_137 |  | 128 | 140 | 0.027783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4289-21_0_8_line_138 |  | 129 | 130 | 0.010812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
139 | LV_4289-21_0_8_line_139 |  | 129 | 131 | 0.015031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
140 | LV_4289-21_0_8_line_140 |  | 130 | 132 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
141 | LV_4289-21_0_8_line_141 |  | 131 | 133 | 0.011662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
142 | LV_4289-21_0_8_line_142 |  | 131 | 134 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_4289-21_0_8_line_143 |  | 132 | 135 | 0.013195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
144 | LV_4289-21_0_8_line_144 |  | 135 | 136 | 0.019585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
145 | LV_4289-21_0_8_line_145 |  | 136 | 143 | 0.013763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
146 | LV_4289-21_0_8_line_146 |  | 137 | 138 | 0.029223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4289-21_0_8_line_147 |  | 138 | 139 | 0.026055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4289-21_0_8_line_148 |  | 139 | 140 | 0.024936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4289-21_0_8_line_149 |  | 141 | 142 | 0.024426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
150 | LV_4289-21_0_8_line_150 |  | 142 | 143 | 0.016444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
151 | LV_4289-21_0_8_line_151 |  | 144 | 145 | 0.032256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4289-21_0_8_line_152 |  | 144 | 146 | 0.014808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
153 | LV_4289-21_0_8_line_153 |  | 146 | 147 | 0.016739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
154 | LV_4289-21_0_8_line_154 |  | 147 | 220 | 0.01728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
155 | LV_4289-21_0_8_line_155 |  | 149 | 150 | 0.020207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4289-21_0_8_line_156 |  | 150 | 152 | 0.018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4289-21_0_8_line_157 |  | 152 | 181 | 0.017014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4289-21_0_8_line_158 |  | 153 | 154 | 0.017305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4289-21_0_8_line_159 |  | 153 | 155 | 0.019224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4289-21_0_8_line_160 |  | 154 | 156 | 0.01251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4289-21_0_8_line_161 |  | 155 | 157 | 0.010323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
162 | LV_4289-21_0_8_line_162 |  | 155 | 158 | 0.030143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
163 | LV_4289-21_0_8_line_163 |  | 156 | 159 | 0.012194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4289-21_0_8_line_164 |  | 157 | 160 | 0.014205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
165 | LV_4289-21_0_8_line_165 |  | 158 | 161 | 0.024137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
166 | LV_4289-21_0_8_line_166 |  | 159 | 162 | 0.0087731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4289-21_0_8_line_167 |  | 160 | 163 | 0.014834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
168 | LV_4289-21_0_8_line_168 |  | 161 | 164 | 0.017521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
169 | LV_4289-21_0_8_line_169 |  | 163 | 176 | 0.0033513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
170 | LV_4289-21_0_8_line_170 |  | 164 | 203 | 0.027343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4289-21_0_8_line_171 |  | 165 | 166 | 0.0073529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4289-21_0_8_line_172 |  | 165 | 167 | 0.018093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4289-21_0_8_line_173 |  | 166 | 168 | 0.0034776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4289-21_0_8_line_174 |  | 167 | 169 | 0.013503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4289-21_0_8_line_175 |  | 169 | 170 | 0.078803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4289-21_0_8_line_176 |  | 170 | 172 | 0.078764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4289-21_0_8_line_177 |  | 171 | 175 | 0.27027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
178 | LV_4289-21_0_8_line_178 |  | 172 | 192 | 0.029473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
179 | LV_4289-21_0_8_line_179 |  | 173 | 174 | 0.0061418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
180 | LV_4289-21_0_8_line_180 |  | 174 | 213 | 0.016777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
181 | LV_4289-21_0_8_line_181 |  | 175 | 193 | 0.029017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
182 | LV_4289-21_0_8_line_182 |  | 176 | 177 | 0.02014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
183 | LV_4289-21_0_8_line_183 |  | 177 | 178 | 0.019115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
184 | LV_4289-21_0_8_line_184 |  | 178 | 179 | 0.015295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
185 | LV_4289-21_0_8_line_185 |  | 179 | 214 | 0.01873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
186 | LV_4289-21_0_8_line_186 |  | 180 | 183 | 0.037691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
187 | LV_4289-21_0_8_line_187 |  | 181 | 182 | 0.003672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
188 | LV_4289-21_0_8_line_188 |  | 182 | 183 | 0.02234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
189 | LV_4289-21_0_8_line_189 |  | 184 | 185 | 0.0013032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
190 | LV_4289-21_0_8_line_190 |  | 184 | 186 | 0.016887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
191 | LV_4289-21_0_8_line_191 |  | 185 | 187 | 0.024791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
192 | LV_4289-21_0_8_line_192 |  | 186 | 188 | 0.0090014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
193 | LV_4289-21_0_8_line_193 |  | 187 | 189 | 0.002537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
194 | LV_4289-21_0_8_line_194 |  | 189 | 190 | 0.021821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
195 | LV_4289-21_0_8_line_195 |  | 190 | 208 | 0.0061449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
196 | LV_4289-21_0_8_line_196 |  | 191 | 192 | 0.021939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
197 | LV_4289-21_0_8_line_197 |  | 193 | 194 | 0.0062869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
198 | LV_4289-21_0_8_line_198 |  | 194 | 195 | 0.085134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
199 | LV_4289-21_0_8_line_199 |  | 195 | 196 | 0.12502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
200 | LV_4289-21_0_8_line_200 |  | 196 | 197 | 0.00688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
201 | LV_4289-21_0_8_line_201 |  | 198 | 199 | 0.048626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
202 | LV_4289-21_0_8_line_202 |  | 198 | 200 | 0.0032334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
203 | LV_4289-21_0_8_line_203 |  | 199 | 201 | 0.034508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
204 | LV_4289-21_0_8_line_204 |  | 200 | 202 | 0.030582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
205 | LV_4289-21_0_8_line_205 |  | 200 | 203 | 0.011691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
206 | LV_4289-21_0_8_line_206 |  | 201 | 204 | 0.047559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
207 | LV_4289-21_0_8_line_207 |  | 202 | 205 | 0.015733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
208 | LV_4289-21_0_8_line_208 |  | 204 | 206 | 0.011655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
209 | LV_4289-21_0_8_line_209 |  | 205 | 207 | 0.010456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
210 | LV_4289-21_0_8_line_210 |  | 207 | 215 | 0.03455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
211 | LV_4289-21_0_8_line_211 |  | 208 | 209 | 0.021806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
212 | LV_4289-21_0_8_line_212 |  | 209 | 210 | 0.0056374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
213 | LV_4289-21_0_8_line_213 |  | 210 | 211 | 0.024507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
214 | LV_4289-21_0_8_line_214 |  | 211 | 212 | 0.010175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
215 | LV_4289-21_0_8_line_215 |  | 212 | 219 | 0.014536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
216 | LV_4289-21_0_8_line_216 |  | 214 | 220 | 0.012981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
217 | LV_4289-21_0_8_line_217 |  | 215 | 216 | 0.015005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
218 | LV_4289-21_0_8_line_218 |  | 216 | 217 | 0.0036192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
219 | LV_4289-21_0_8_line_219 |  | 218 | 219 | 0.011594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4289-21_0_8_trafo_116 | 0.63 MVA 20/0.4 kV | 221 | 96 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2638551.2859 | 1237717.925 | 2638520.7095 | 1237702.6727 | 2638517.5135 | 1237700.9551
1 | 2638551.2859 | 1237717.925 | 2638601.3234 | 1237743.1742
2 | 2638551.2859 | 1237717.925 | 2638558.0656 | 1237702.5147 | 2638559.1482 | 1237700.0646 | 2638575.6276 | 1237707.7208
3 | 2638625.993 | 1237755.6226 | 2638601.3234 | 1237743.1742
4 | 2638575.6276 | 1237707.7208 | 2638585.6891 | 1237685.5498 | 2638588.8416 | 1237687.0268 | 2638597.3648 | 1237668.7594
5 | 2638625.993 | 1237755.6226 | 2638629.1148 | 1237757.1661 | 2638653.591 | 1237769.3107
6 | 2638617.3659 | 1237589.6725 | 2638619.7361 | 1237584.6514 | 2638631.8287 | 1237577.0918 | 2638646.6275 | 1237594.2878 | 2638651.0028 | 1237598.5078
7 | 2638617.3659 | 1237589.6725 | 2638597.4583 | 1237581.7202
8 | 2638651.0028 | 1237598.5078 | 2638670.2985 | 1237571.6582
9 | 2638651.0028 | 1237598.5078 | 2638668.6324 | 1237615.5097
10 | 2638594.1951 | 1237566.2628 | 2638591.1381 | 1237579.1956 | 2638597.4583 | 1237581.7202
11 | 2638653.591 | 1237769.3107 | 2638675.5707 | 1237779.1376 | 2638681.7598 | 1237765.0134
12 | 2638653.591 | 1237769.3107 | 2638644.3046 | 1237796.3362
13 | 2638676.5031 | 1237623.1003 | 2638680.0214 | 1237626.492
14 | 2638676.5031 | 1237623.1003 | 2638668.6324 | 1237615.5097
15 | 2638680.0214 | 1237626.492 | 2638697.422 | 1237635.4791
16 | 2638594.1951 | 1237566.2628 | 2638596.9802 | 1237567.2593 | 2638600.8254 | 1237557.6003
17 | 2638618.5746 | 1237522.4155 | 2638612.8422 | 1237487.2004
18 | 2638618.5746 | 1237522.4155 | 2638631.1337 | 1237527.0067
19 | 2638618.5746 | 1237522.4155 | 2638602.8971 | 1237517.0103 | 2638595.4216 | 1237515.8815
20 | 2638617.0512 | 1237435.5506 | 2638613.252 | 1237468.38 | 2638612.3039 | 1237483.8837 | 2638612.8422 | 1237487.2004
21 | 2638612.8422 | 1237487.2004 | 2638593.6268 | 1237482.3899
22 | 2638653.3283 | 1237535.1204 | 2638631.1337 | 1237527.0067
23 | 2638687.5626 | 1237547.6355 | 2638670.2985 | 1237571.6582
24 | 2638697.422 | 1237635.4791 | 2638717.4757 | 1237645.8364
25 | 2638687.5626 | 1237547.6355 | 2638671.1336 | 1237541.6295
26 | 2638687.5626 | 1237547.6355 | 2638689.2619 | 1237548.2564
27 | 2638730.9284 | 1237652.7845 | 2638717.4757 | 1237645.8364
28 | 2638716.3064 | 1237578.6911 | 2638702.4978 | 1237596.8821
29 | 2638728.5205 | 1237562.6005 | 2638716.3064 | 1237578.6911
30 | 2638653.3283 | 1237535.1204 | 2638671.1336 | 1237541.6295
31 | 2638709.434 | 1237555.6268 | 2638689.2619 | 1237548.2564
32 | 2638617.0512 | 1237435.5506 | 2638640.9484 | 1237448.5252 | 2638650.6964 | 1237452.5965
33 | 2638728.5205 | 1237562.6005 | 2638758.5293 | 1237550.8262
34 | 2638728.5205 | 1237562.6005 | 2638715.0751 | 1237557.6879
35 | 2638758.5293 | 1237550.8262 | 2638760.9973 | 1237549.8579
36 | 2638709.434 | 1237555.6268 | 2638715.0751 | 1237557.6879
37 | 2638790.1728 | 1237538.4105 | 2638760.9973 | 1237549.8579
38 | 2638730.9284 | 1237652.7845 | 2638736.5755 | 1237655.7009 | 2638739.7046 | 1237657.02
39 | 2638730.9284 | 1237652.7845 | 2638724.85 | 1237666.6596
40 | 2638681.7598 | 1237765.0134 | 2638682.6646 | 1237762.9484
41 | 2638742.099 | 1237764.4436 | 2638733.7151 | 1237784.7824
42 | 2638726.7658 | 1237801.6407 | 2638733.7151 | 1237784.7824
43 | 2638742.099 | 1237764.4436 | 2638744.3128 | 1237759.0731
44 | 2638726.7658 | 1237801.6407 | 2638752.4229 | 1237811.3549
45 | 2638750.5534 | 1237743.934 | 2638744.3128 | 1237759.0731
46 | 2638752.7472 | 1237738.612 | 2638750.5534 | 1237743.934
47 | 2638691.3961 | 1237743.0206 | 2638682.6646 | 1237762.9484
48 | 2638752.7472 | 1237738.612 | 2638760.8126 | 1237719.0459
49 | 2638802.3923 | 1237830.2742 | 2638815.7867 | 1237797.8556
50 | 2638802.3923 | 1237830.2742 | 2638824.6561 | 1237835.9231
51 | 2638819.2597 | 1237789.4499 | 2638815.7867 | 1237797.8556
52 | 2638824.6561 | 1237835.9231 | 2638826.3232 | 1237836.3334
53 | 2638701.2726 | 1237720.4792 | 2638699.8206 | 1237723.7936 | 2638691.3961 | 1237743.0206
54 | 2638701.2726 | 1237720.4792 | 2638711.8218 | 1237696.3986
55 | 2638711.8218 | 1237696.3986 | 2638724.85 | 1237666.6596
56 | 2638760.8126 | 1237719.0459 | 2638761.1675 | 1237718.1849
57 | 2638766.5871 | 1237705.0375 | 2638761.1675 | 1237718.1849
58 | 2638766.5871 | 1237705.0375 | 2638773.8927 | 1237687.3147
59 | 2638779.4715 | 1237673.7809 | 2638773.8927 | 1237687.3147
60 | 2638774.4018 | 1237671.6465 | 2638779.4715 | 1237673.7809
61 | 2638779.4715 | 1237673.7809 | 2638792.2927 | 1237680.5498
62 | 2638682.6429 | 1237465.9239 | 2638681.267 | 1237465.3646 | 2638650.6964 | 1237452.5965
63 | 2638774.4018 | 1237671.6465 | 2638739.7046 | 1237657.02
64 | 2638708.8607 | 1237476.5791 | 2638682.6429 | 1237465.9239
65 | 2638774.4018 | 1237671.6465 | 2638780.1568 | 1237661.9588
66 | 2638792.2927 | 1237680.5498 | 2638795.3772 | 1237682.1783
67 | 2638797.162 | 1237639.2897 | 2638794.4165 | 1237641.8248 | 2638782.8233 | 1237657.4702 | 2638780.1568 | 1237661.9588
68 | 2638801.7112 | 1237685.5223 | 2638795.3772 | 1237682.1783
69 | 2638797.162 | 1237639.2897 | 2638803.0807 | 1237633.8246
70 | 2638801.7112 | 1237685.5223 | 2638808.7729 | 1237689.7101
71 | 2638739.7616 | 1237402.9124 | 2638749.4707 | 1237419.0715
72 | 2638731.2247 | 1237386.8068 | 2638738.7115 | 1237401.1646 | 2638739.7616 | 1237402.9124
73 | 2638810.719 | 1237438.7509 | 2638787.7125 | 1237439.2415 | 2638772.6194 | 1237437.0195 | 2638761.0794 | 1237431.6853 | 2638752.5269 | 1237424.1581 | 2638749.4707 | 1237419.0715
74 | 2638731.2247 | 1237386.8068 | 2638741.7323 | 1237388.0538 | 2638755.4416 | 1237390.2 | 2638773.1473 | 1237389.7263 | 2638776.307 | 1237388.8832
75 | 2638810.719 | 1237438.7509 | 2638811.6596 | 1237438.7308 | 2638863.6142 | 1237434.7863
76 | 2638863.6142 | 1237434.7863 | 2638878.7524 | 1237433.6369
77 | 2638908.33 | 1237431.3913 | 2638878.7524 | 1237433.6369
78 | 2638708.8607 | 1237476.5791 | 2638717.0763 | 1237479.918 | 2638737.0635 | 1237485.6963 | 2638754.8133 | 1237487.691 | 2638763.1088 | 1237487.2712
79 | 2638789.6054 | 1237483.0261 | 2638774.4664 | 1237486.6963 | 2638763.1088 | 1237487.2712
80 | 2638927.3918 | 1237429.4593 | 2638908.33 | 1237431.3913
81 | 2638935.5376 | 1237527.875 | 2638912.6306 | 1237490.9127 | 2638906.1854 | 1237458.5278 | 2638908.33 | 1237431.3913
82 | 2638922.2946 | 1237859.8061 | 2638899.7208 | 1237854.3218
83 | 2638956.4485 | 1237867.3141 | 2638950.6707 | 1237866.7002 | 2638922.2946 | 1237859.8061
84 | 2638875.8922 | 1237848.5326 | 2638899.7208 | 1237854.3218
85 | 2638875.8922 | 1237848.5326 | 2638858.7743 | 1237844.3198
86 | 2638858.7743 | 1237844.3198 | 2638826.3232 | 1237836.3334
87 | 2639015.3789 | 1237860.8874 | 2639005.3473 | 1237864.8392
88 | 2639015.3789 | 1237860.8874 | 2639021.0298 | 1237870.0748 | 2639020.6696 | 1237873.0966 | 2639019.2099 | 1237879.9692 | 2639015.6968 | 1237889.6522 | 2639014.6011 | 1237893.1548
89 | 2639015.3789 | 1237860.8874 | 2639025.7908 | 1237852.3726
90 | 2638890.315 | 1237812.083 | 2638889.5608 | 1237813.989
91 | 2638890.315 | 1237812.083 | 2638898.7696 | 1237790.7164
92 | 2639027.7645 | 1237850.1619 | 2639025.7908 | 1237852.3726
93 | 2639025.7908 | 1237852.3726 | 2639012.2119 | 1237838.2385
94 | 2638830.8246 | 1237761.4592 | 2638823.1372 | 1237780.0651
95 | 2638837.3341 | 1237745.7042 | 2638830.8246 | 1237761.4592
96 | 2638819.2597 | 1237789.4499 | 2638823.1372 | 1237780.0651
97 | 2638837.3341 | 1237745.7042 | 2638838.6755 | 1237742.4583
98 | 2638837.3341 | 1237745.7042 | 2638855.4319 | 1237752.8003
99 | 2638851.9382 | 1237710.3661 | 2638838.6755 | 1237742.4583
100 | 2638855.4319 | 1237752.8003 | 2638857.872 | 1237753.757
101 | 2638851.9382 | 1237710.3661 | 2638826.1622 | 1237698.5343
102 | 2638857.872 | 1237753.757 | 2638877.579 | 1237761.4841
103 | 2638808.7729 | 1237689.7101 | 2638815.0568 | 1237693.4367 | 2638826.1622 | 1237698.5343
104 | 2638895.0792 | 1237768.3459 | 2638877.579 | 1237761.4841
105 | 2639287.7258 | 1237699.9787 | 2639279.7834 | 1237719.0663
106 | 2639264.8586 | 1237751.2936 | 2639268.4777 | 1237746.2365 | 2639279.7834 | 1237719.0663
107 | 2639287.7258 | 1237699.9787 | 2639281.1899 | 1237696.5333
108 | 2639287.7258 | 1237699.9787 | 2639308.9985 | 1237709.0695 | 2639342.7028 | 1237723.4794 | 2639383.6782 | 1237742.2181 | 2639388.4497 | 1237758.4823 | 2639388.514 | 1237770.4681
109 | 2639264.8586 | 1237751.2936 | 2639262.9648 | 1237756.262
110 | 2639264.8586 | 1237751.2936 | 2639258.236 | 1237752.9509 | 2639253.6624 | 1237752.0561
111 | 2639281.1899 | 1237696.5333 | 2639303.4098 | 1237671.0751 | 2639308.6129 | 1237656.4447
112 | 2639388.514 | 1237770.4681 | 2639395.7416 | 1237797.3442 | 2639401.56 | 1237806.8329
113 | 2639262.9648 | 1237756.262 | 2639255.5993 | 1237775.6024
114 | 2639253.6624 | 1237752.0561 | 2639229.2356 | 1237747.2774
115 | 2639308.6129 | 1237656.4447 | 2639295.9691 | 1237648.8674 | 2639286.3926 | 1237639.6094
116 | 2639229.055 | 1237794.7515 | 2639251.9793 | 1237785.1078 | 2639255.5993 | 1237775.6024
117 | 2639216.2973 | 1237744.7463 | 2639229.2356 | 1237747.2774
118 | 2639243.4057 | 1237682.1875 | 2639216.5691 | 1237674.3925
119 | 2639216.5691 | 1237674.3925 | 2639206.4256 | 1237671.4462 | 2639190.5554 | 1237667.2712
120 | 2639203.6278 | 1237742.1358 | 2639208.4182 | 1237743.2049 | 2639216.2973 | 1237744.7463
121 | 2638978.5971 | 1237705.0668 | 2638981.6925 | 1237711.1492 | 2638991.0009 | 1237723.2735 | 2638994.3623 | 1237726.258
122 | 2638974.6745 | 1237670.4552 | 2638972.9174 | 1237681.1504 | 2638974.687 | 1237697.3835 | 2638978.5971 | 1237705.0668
123 | 2639014.5109 | 1237742.8985 | 2639004.6891 | 1237735.4266 | 2638994.3623 | 1237726.258
124 | 2638974.6745 | 1237670.4552 | 2638960.1116 | 1237668.2231
125 | 2638974.6745 | 1237670.4552 | 2638979.5297 | 1237659.1465 | 2638981.6446 | 1237656.2031
126 | 2639032.1454 | 1237758.2608 | 2639023.1608 | 1237749.4789 | 2639014.5109 | 1237742.8985
127 | 2638936.5822 | 1237665.9996 | 2638946.9393 | 1237666.2041 | 2638960.1116 | 1237668.2231
128 | 2639057.5002 | 1237635.1096 | 2639034.5745 | 1237632.2572 | 2639018.0872 | 1237632.7716 | 2639000.9467 | 1237638.2737 | 2638988.1568 | 1237647.1399 | 2638981.6446 | 1237656.2031
129 | 2639035.8036 | 1237761.8364 | 2639032.1454 | 1237758.2608
130 | 2638913.061 | 1237666.5381 | 2638925.0267 | 1237665.7714 | 2638936.5822 | 1237665.9996
131 | 2639057.5002 | 1237635.1096 | 2639054.0782 | 1237658.8799
132 | 2639057.5002 | 1237635.1096 | 2639085.6847 | 1237641.5333
133 | 2639044.7249 | 1237776.4265 | 2639035.8036 | 1237761.8364
134 | 2639035.8036 | 1237761.8364 | 2639027.1385 | 1237765.8154 | 2639020.9315 | 1237766.3972
135 | 2638913.061 | 1237666.5381 | 2638901.2554 | 1237667.2946 | 2638882.6144 | 1237670.1553
136 | 2639054.0782 | 1237658.8799 | 2639050.4043 | 1237684.4005
137 | 2639085.6847 | 1237641.5333 | 2639112.7734 | 1237647.7073
138 | 2638929.5137 | 1237783.1852 | 2638919.6501 | 1237778.758
139 | 2638905.9369 | 1237772.6031 | 2638919.6501 | 1237778.758
140 | 2638929.5137 | 1237783.1852 | 2638940.7534 | 1237788.2299 | 2638940.7534 | 1237788.2299
141 | 2638905.9369 | 1237772.6031 | 2638895.0792 | 1237768.3459
142 | 2638905.9369 | 1237772.6031 | 2638898.7696 | 1237790.7164
143 | 2638952.0379 | 1237795.0687 | 2638940.7534 | 1237788.2299
144 | 2638968.7872 | 1237805.2195 | 2638952.0379 | 1237795.0687
145 | 2638968.7872 | 1237805.2195 | 2638977.5306 | 1237810.5183 | 2638980.303 | 1237812.7176
146 | 2639162.2936 | 1237659.8364 | 2639190.5554 | 1237667.2712
147 | 2639162.2936 | 1237659.8364 | 2639138.3235 | 1237653.5306 | 2639137.0859 | 1237653.2485
148 | 2639137.0859 | 1237653.2485 | 2639112.7734 | 1237647.7073
149 | 2639012.2119 | 1237838.2385 | 2639011.3652 | 1237837.3573 | 2638993.1861 | 1237822.9369
150 | 2638993.1861 | 1237822.9369 | 2638980.303 | 1237812.7176
151 | 2639027.7645 | 1237850.1619 | 2639039.0348 | 1237861.8322 | 2639053.9421 | 1237867.7316
152 | 2639027.7645 | 1237850.1619 | 2639033.4801 | 1237843.7621 | 2639037.1143 | 1237838.7046
153 | 2639037.1143 | 1237838.7046 | 2639042.275 | 1237831.5231 | 2639045.0372 | 1237824.1261
154 | 2639049.0648 | 1237807.4093 | 2639047.4726 | 1237817.604 | 2639045.0372 | 1237824.1261
155 | 2638907.1956 | 1237730.4805 | 2638926.4649 | 1237736.5656
156 | 2638926.4649 | 1237736.5656 | 2638943.9603 | 1237742.0905
157 | 2638960.185 | 1237747.2141 | 2638943.9603 | 1237742.0905
158 | 2639159.6623 | 1237813.0995 | 2639142.359 | 1237813.373
159 | 2639123.1378 | 1237813.6767 | 2639142.359 | 1237813.373
160 | 2639159.6623 | 1237813.0995 | 2639161.3738 | 1237813.0725 | 2639172.0929 | 1237811.7631
161 | 2639123.1378 | 1237813.6767 | 2639122.3549 | 1237806.2001 | 2639120.7587 | 1237803.8926
162 | 2639123.1378 | 1237813.6767 | 2639123.5292 | 1237817.415 | 2639116.9963 | 1237829.6131 | 2639109.1071 | 1237839.3698
163 | 2639172.0929 | 1237811.7631 | 2639184.197 | 1237810.2845
164 | 2639111.2838 | 1237793.8056 | 2639115.1388 | 1237795.7683 | 2639120.7587 | 1237803.8926
165 | 2639109.1071 | 1237839.3698 | 2639095.7939 | 1237855.8347 | 2639095.1056 | 1237858.7163
166 | 2639192.6418 | 1237808.0086 | 2639186.2438 | 1237810.0344 | 2639184.197 | 1237810.2845
167 | 2639111.2838 | 1237793.8056 | 2639098.0643 | 1237787.0755
168 | 2639093.7474 | 1237876.0007 | 2639093.2191 | 1237866.6135 | 2639095.1056 | 1237858.7163
169 | 2639095.0777 | 1237785.555 | 2639098.0643 | 1237787.0755
170 | 2639093.7474 | 1237876.0007 | 2639094.1537 | 1237883.2302 | 2639099.6469 | 1237902.5675
171 | 2638948.4304 | 1237540.5688 | 2638953.6699 | 1237545.7275
172 | 2638935.5376 | 1237527.875 | 2638948.4304 | 1237540.5688
173 | 2638956.148 | 1237548.1673 | 2638953.6699 | 1237545.7275
174 | 2638922.0075 | 1237528.4646 | 2638935.5376 | 1237527.875
175 | 2638922.0075 | 1237528.4646 | 2638925.11 | 1237561.8171 | 2638939.3927 | 1237581.4564 | 2638932.4352 | 1237586.8699 | 2638925.8315 | 1237597.1887
176 | 2638925.8315 | 1237597.1887 | 2638922.4534 | 1237596.6663 | 2638862.5059 | 1237608.6373 | 2638848.9487 | 1237612.9097
177 | 2638927.3918 | 1237429.4593 | 2639185.0255 | 1237347.7748
178 | 2638820.8388 | 1237621.7682 | 2638848.9487 | 1237612.9097
179 | 2638812.1287 | 1237532.9991 | 2638805.9916 | 1237533.241
180 | 2638790.1728 | 1237538.4105 | 2638803.0528 | 1237533.3568 | 2638805.9916 | 1237533.241
181 | 2639185.0255 | 1237347.7748 | 2639192.1307 | 1237338.4074 | 2639201.6651 | 1237325.4842 | 2639202.0444 | 1237324.3461
182 | 2639095.0777 | 1237785.555 | 2639077.1294 | 1237776.4174
183 | 2639077.1294 | 1237776.4174 | 2639072.5935 | 1237774.1081 | 2639058.8974 | 1237771.0889
184 | 2639044.7249 | 1237776.4265 | 2639058.0373 | 1237770.8993 | 2639058.8974 | 1237771.0889
185 | 2639044.7249 | 1237776.4265 | 2639048.2056 | 1237786.6447 | 2639049.0498 | 1237794.5349
186 | 2639020.9315 | 1237766.3972 | 2639020.9315 | 1237766.3972 | 2638984.9898 | 1237755.0472
187 | 2638963.6865 | 1237748.3198 | 2638960.185 | 1237747.2141
188 | 2638963.6865 | 1237748.3198 | 2638984.9898 | 1237755.0472
189 | 2639064.4419 | 1237702.4937 | 2639065.6722 | 1237702.9236
190 | 2639064.4419 | 1237702.4937 | 2639056.8025 | 1237699.8239 | 2639050.9021 | 1237693.3022
191 | 2639089.075 | 1237711.1024 | 2639065.6722 | 1237702.9236
192 | 2639050.4043 | 1237684.4005 | 2639050.0886 | 1237686.5936 | 2639050.8017 | 1237693.1913 | 2639050.9021 | 1237693.3022
193 | 2639089.075 | 1237711.1024 | 2639091.4699 | 1237711.9394
194 | 2639112.2574 | 1237718.5698 | 2639095.2569 | 1237713.2629 | 2639091.4699 | 1237711.9394
195 | 2639112.2574 | 1237718.5698 | 2639118.1231 | 1237720.4008
196 | 2638820.8388 | 1237621.7682 | 2638813.7023 | 1237624.0171 | 2638803.0807 | 1237633.8246
197 | 2639202.0444 | 1237324.3461 | 2639204.0322 | 1237318.3817
198 | 2639191.6395 | 1237237.3846 | 2639197.4831 | 1237248.3856 | 2639202.5976 | 1237258.6703 | 2639205.2922 | 1237266.493 | 2639207.8563 | 1237274.6151 | 2639208.9422 | 1237293.4897 | 2639207.0446 | 1237309.3428 | 2639204.0322 | 1237318.3817
199 | 2639091.5507 | 1237211.8095 | 2639107.3163 | 1237188.9431 | 2639191.6395 | 1237237.3846
200 | 2639091.5507 | 1237211.8095 | 2639097.1606 | 1237215.8156
201 | 2639150.4251 | 1237939.6799 | 2639126.14 | 1237926.4014 | 2639111.4278 | 1237915.9313 | 2639109.5175 | 1237913.7618
202 | 2639107.3808 | 1237911.3351 | 2639109.5175 | 1237913.7618
203 | 2639180.7031 | 1237956.2352 | 2639150.4251 | 1237939.6799
204 | 2639107.3808 | 1237911.3351 | 2639120.6311 | 1237902.5722 | 2639125.9973 | 1237888.8905
205 | 2639107.3808 | 1237911.3351 | 2639099.6469 | 1237902.5675
206 | 2639180.7031 | 1237956.2352 | 2639201.1535 | 1237913.2761
207 | 2639125.9973 | 1237888.8905 | 2639127.5554 | 1237884.9177 | 2639134.2729 | 1237875.6258
208 | 2639206.1626 | 1237902.7469 | 2639201.1535 | 1237913.2761
209 | 2639140.7288 | 1237867.5334 | 2639139.7548 | 1237868.0428 | 2639134.2729 | 1237875.6258
210 | 2639173.3914 | 1237857.1131 | 2639163.9975 | 1237859.1635 | 2639151.1334 | 1237862.0917 | 2639140.7288 | 1237867.5334
211 | 2639139.0819 | 1237726.4005 | 2639127.3112 | 1237723.269 | 2639118.1231 | 1237720.4008
212 | 2639139.0819 | 1237726.4005 | 2639144.5298 | 1237727.8498
213 | 2639144.5298 | 1237727.8498 | 2639168.2126 | 1237734.1504
214 | 2639168.2126 | 1237734.1504 | 2639170.1211 | 1237734.6581 | 2639178.1247 | 1237736.4443
215 | 2639178.1247 | 1237736.4443 | 2639192.312 | 1237739.6104
216 | 2639049.0648 | 1237807.4093 | 2639049.8733 | 1237802.2322 | 2639049.0498 | 1237794.5349
217 | 2639188.0517 | 1237853.9133 | 2639173.3914 | 1237857.1131
218 | 2639191.5876 | 1237853.1415 | 2639188.0517 | 1237853.9133
219 | 2639203.6278 | 1237742.1358 | 2639192.312 | 1237739.6104

## bus_geodata
| x | y | coords
0 | 2638517.5135 | 1237700.9551
1 | 2638551.2859 | 1237717.925
2 | 2638601.3234 | 1237743.1742
3 | 2638575.6276 | 1237707.7208
4 | 2638597.3648 | 1237668.7594
5 | 2638625.993 | 1237755.6226
6 | 2638617.3659 | 1237589.6725
7 | 2638651.0028 | 1237598.5078
8 | 2638597.4583 | 1237581.7202
9 | 2638653.591 | 1237769.3107
10 | 2638676.5031 | 1237623.1003
11 | 2638680.0214 | 1237626.492
12 | 2638668.6324 | 1237615.5097
13 | 2638594.1951 | 1237566.2628
14 | 2638600.8254 | 1237557.6003
15 | 2638618.5746 | 1237522.4155
16 | 2638612.8422 | 1237487.2004
17 | 2638631.1337 | 1237527.0067
18 | 2638595.4216 | 1237515.8815
19 | 2638670.2985 | 1237571.6582
20 | 2638697.422 | 1237635.4791
21 | 2638687.5626 | 1237547.6355
22 | 2638717.4757 | 1237645.8364
23 | 2638702.4978 | 1237596.8821
24 | 2638716.3064 | 1237578.6911
25 | 2638671.1336 | 1237541.6295
26 | 2638689.2619 | 1237548.2564
27 | 2638617.0512 | 1237435.5506
28 | 2638593.6268 | 1237482.3899
29 | 2638653.3283 | 1237535.1204
30 | 2638728.5205 | 1237562.6005
31 | 2638758.5293 | 1237550.8262
32 | 2638715.0751 | 1237557.6879
33 | 2638760.9973 | 1237549.8579
34 | 2638709.434 | 1237555.6268
35 | 2638730.9284 | 1237652.7845
36 | 2638681.7598 | 1237765.0134
37 | 2638644.3046 | 1237796.3362
38 | 2638733.7151 | 1237784.7824
39 | 2638742.099 | 1237764.4436
40 | 2638726.7658 | 1237801.6407
41 | 2638744.3128 | 1237759.0731
42 | 2638752.4229 | 1237811.3549
43 | 2638750.5534 | 1237743.934
44 | 2638682.6646 | 1237762.9484
45 | 2638752.7472 | 1237738.612
46 | 2638802.3923 | 1237830.2742
47 | 2638815.7867 | 1237797.8556
48 | 2638824.6561 | 1237835.9231
49 | 2638691.3961 | 1237743.0206
50 | 2638701.2726 | 1237720.4792
51 | 2638711.8218 | 1237696.3986
52 | 2638724.85 | 1237666.6596
53 | 2638760.8126 | 1237719.0459
54 | 2638761.1675 | 1237718.1849
55 | 2638766.5871 | 1237705.0375
56 | 2638773.8927 | 1237687.3147
57 | 2638779.4715 | 1237673.7809
58 | 2638650.6964 | 1237452.5965
59 | 2638739.7046 | 1237657.02
60 | 2638682.6429 | 1237465.9239
61 | 2638774.4018 | 1237671.6465
62 | 2638792.2927 | 1237680.5498
63 | 2638780.1568 | 1237661.9588
64 | 2638795.3772 | 1237682.1783
65 | 2638797.162 | 1237639.2897
66 | 2638801.7112 | 1237685.5223
67 | 2638739.7616 | 1237402.9124
68 | 2638749.4707 | 1237419.0715
69 | 2638731.2247 | 1237386.8068
70 | 2638810.7191 | 1237438.7509
71 | 2638776.307 | 1237388.8832
72 | 2638863.6142 | 1237434.7863
73 | 2638878.7524 | 1237433.6369
74 | 2638708.8606 | 1237476.5791
75 | 2638763.1088 | 1237487.2712
76 | 2638789.6054 | 1237483.0261
77 | 2638908.33 | 1237431.3913
78 | 2638922.2946 | 1237859.8061
79 | 2638899.7208 | 1237854.3218
80 | 2638956.4485 | 1237867.3141
81 | 2638875.8922 | 1237848.5326
82 | 2638858.7743 | 1237844.3198
83 | 2639005.3473 | 1237864.8392
84 | 2639015.3789 | 1237860.8874
85 | 2638826.3232 | 1237836.3334
86 | 2638889.5608 | 1237813.989
87 | 2638890.315 | 1237812.083
88 | 2639014.6011 | 1237893.1548
89 | 2639025.7908 | 1237852.3726
90 | 2638830.8246 | 1237761.4592
91 | 2638823.1372 | 1237780.0651
92 | 2638837.3341 | 1237745.7042
93 | 2638819.2597 | 1237789.4499
94 | 2638838.6755 | 1237742.4583
95 | 2638855.4319 | 1237752.8003
96 | 2638851.9382 | 1237710.3661
97 | 2638857.872 | 1237753.757
98 | 2638826.1622 | 1237698.5343
99 | 2638877.579 | 1237761.4841
100 | 2639279.7834 | 1237719.0663
101 | 2639287.7258 | 1237699.9787
102 | 2639264.8586 | 1237751.2936
103 | 2639281.1899 | 1237696.5334
104 | 2639388.514 | 1237770.4681
105 | 2639262.9648 | 1237756.262
106 | 2639253.6624 | 1237752.0561
107 | 2639308.6129 | 1237656.4447
108 | 2639286.3926 | 1237639.6094
109 | 2639255.5993 | 1237775.6024
110 | 2639401.56 | 1237806.8329
111 | 2639229.2356 | 1237747.2774
112 | 2639243.4057 | 1237682.1875
113 | 2639216.5691 | 1237674.3925
114 | 2639229.055 | 1237794.7515
115 | 2639216.2973 | 1237744.7463
116 | 2638978.5971 | 1237705.0668
117 | 2638994.3623 | 1237726.258
118 | 2638974.6745 | 1237670.4552
119 | 2639014.5109 | 1237742.8985
120 | 2638960.1116 | 1237668.2231
121 | 2638981.6446 | 1237656.2031
122 | 2639032.1454 | 1237758.2608
123 | 2638936.5822 | 1237665.9996
124 | 2639057.5002 | 1237635.1096
125 | 2639035.8036 | 1237761.8364
126 | 2638913.061 | 1237666.5381
127 | 2639054.0782 | 1237658.8799
128 | 2639085.6847 | 1237641.5333
129 | 2638919.6501 | 1237778.758
130 | 2638929.5137 | 1237783.1851
131 | 2638905.9369 | 1237772.6031
132 | 2638940.7534 | 1237788.2299
133 | 2638895.0792 | 1237768.3459
134 | 2638898.7696 | 1237790.7164
135 | 2638952.0379 | 1237795.0687
136 | 2638968.7872 | 1237805.2195
137 | 2639190.5554 | 1237667.2712
138 | 2639162.2936 | 1237659.8364
139 | 2639137.0859 | 1237653.2485
140 | 2639112.7734 | 1237647.7073
141 | 2639012.2119 | 1237838.2385
142 | 2638993.1861 | 1237822.9369
143 | 2638980.303 | 1237812.7176
144 | 2639027.7645 | 1237850.1619
145 | 2639053.9421 | 1237867.7316
146 | 2639037.1144 | 1237838.7046
147 | 2639045.0372 | 1237824.1261
148 | 2638808.7729 | 1237689.7101
149 | 2638907.1956 | 1237730.4805
150 | 2638926.4649 | 1237736.5656
151 | 2638882.6144 | 1237670.1553
152 | 2638943.9603 | 1237742.0905
153 | 2639142.359 | 1237813.373
154 | 2639159.6623 | 1237813.0995
155 | 2639123.1378 | 1237813.6767
156 | 2639172.0929 | 1237811.7631
157 | 2639120.7587 | 1237803.8926
158 | 2639109.1071 | 1237839.3698
159 | 2639184.197 | 1237810.2845
160 | 2639111.2838 | 1237793.8056
161 | 2639095.1056 | 1237858.7163
162 | 2639192.6418 | 1237808.0086
163 | 2639098.0643 | 1237787.0755
164 | 2639093.7474 | 1237876.0007
165 | 2638948.4304 | 1237540.5688
166 | 2638953.6699 | 1237545.7275
167 | 2638935.5376 | 1237527.875
168 | 2638956.148 | 1237548.1673
169 | 2638922.0075 | 1237528.4646
170 | 2638925.8315 | 1237597.1887
171 | 2638927.3918 | 1237429.4593
172 | 2638848.9487 | 1237612.9097
173 | 2638812.1287 | 1237532.9991
174 | 2638805.9916 | 1237533.241
175 | 2639185.0255 | 1237347.7748
176 | 2639095.0777 | 1237785.555
177 | 2639077.1294 | 1237776.4174
178 | 2639058.8974 | 1237771.0889
179 | 2639044.7249 | 1237776.4265
180 | 2639020.9315 | 1237766.3972
181 | 2638960.185 | 1237747.2141
182 | 2638963.6865 | 1237748.3198
183 | 2638984.9898 | 1237755.0472
184 | 2639064.4419 | 1237702.4937
185 | 2639065.6722 | 1237702.9236
186 | 2639050.9021 | 1237693.3022
187 | 2639089.075 | 1237711.1024
188 | 2639050.4043 | 1237684.4005
189 | 2639091.4699 | 1237711.9394
190 | 2639112.2574 | 1237718.5698
191 | 2638803.0807 | 1237633.8246
192 | 2638820.8388 | 1237621.7682
193 | 2639202.0444 | 1237324.3461
194 | 2639204.0322 | 1237318.3817
195 | 2639191.6395 | 1237237.3846
196 | 2639091.5507 | 1237211.8095
197 | 2639097.1606 | 1237215.8156
198 | 2639109.5175 | 1237913.7618
199 | 2639150.4251 | 1237939.6799
200 | 2639107.3807 | 1237911.3351
201 | 2639180.7031 | 1237956.2352
202 | 2639125.9973 | 1237888.8905
203 | 2639099.6469 | 1237902.5675
204 | 2639201.1535 | 1237913.2761
205 | 2639134.2729 | 1237875.6258
206 | 2639206.1626 | 1237902.7469
207 | 2639140.7288 | 1237867.5334
208 | 2639118.1231 | 1237720.4008
209 | 2639139.0819 | 1237726.4005
210 | 2639144.5298 | 1237727.8498
211 | 2639168.2126 | 1237734.1504
212 | 2639178.1247 | 1237736.4443
213 | 2638790.1728 | 1237538.4105
214 | 2639049.0498 | 1237794.5349
215 | 2639173.3914 | 1237857.1131
216 | 2639188.0517 | 1237853.9133
217 | 2639191.5876 | 1237853.1415
218 | 2639203.6278 | 1237742.1358
219 | 2639192.312 | 1237739.6104
220 | 2639049.0648 | 1237807.4093
221 | 2638837.3341 | 1237745.7042

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1