## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4401-12_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4401-12_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4401-12_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4401-12_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4401-12_0_4_node_20 | 0.4 | n |  | TRUE
5 | bus_LV_4401-12_0_4_node_14 | 0.4 | n |  | TRUE
6 | bus_LV_4401-12_0_4_node_80 | 0.4 | n |  | TRUE
7 | bus_LV_4401-12_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_4401-12_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_4401-12_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_4401-12_0_4_node_73 | 0.4 | n |  | TRUE
11 | bus_LV_4401-12_0_4_node_67 | 0.4 | n |  | TRUE
12 | bus_LV_4401-12_0_4_node_61 | 0.4 | n |  | TRUE
13 | bus_LV_4401-12_0_4_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_4401-12_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_4401-12_0_4_node_176 | 0.4 | n |  | TRUE
16 | bus_LV_4401-12_0_4_node_175 | 0.4 | n |  | TRUE
17 | bus_LV_4401-12_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_4401-12_0_4_node_69 | 0.4 | n |  | TRUE
19 | bus_LV_4401-12_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_4401-12_0_4_node_9 | 0.4 | n |  | TRUE
21 | bus_LV_4401-12_0_4_node_96 | 0.4 | n |  | TRUE
22 | bus_LV_4401-12_0_4_node_97 | 0.4 | n |  | TRUE
23 | bus_LV_4401-12_0_4_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_4401-12_0_4_node_62 | 0.4 | n |  | TRUE
25 | bus_LV_4401-12_0_4_node_78 | 0.4 | n |  | TRUE
26 | bus_LV_4401-12_0_4_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_4401-12_0_4_node_104 | 0.4 | n |  | TRUE
28 | bus_LV_4401-12_0_4_node_98 | 0.4 | n |  | TRUE
29 | bus_LV_4401-12_0_4_node_45 | 0.4 | n |  | TRUE
30 | bus_LV_4401-12_0_4_node_44 | 0.4 | n |  | TRUE
31 | bus_LV_4401-12_0_4_node_13 | 0.4 | n |  | TRUE
32 | bus_LV_4401-12_0_4_node_84 | 0.4 | n |  | TRUE
33 | bus_LV_4401-12_0_4_node_83 | 0.4 | n |  | TRUE
34 | bus_LV_4401-12_0_4_node_15 | 0.4 | n |  | TRUE
35 | bus_LV_4401-12_0_4_node_16 | 0.4 | n |  | TRUE
36 | bus_LV_4401-12_0_4_node_132 | 0.4 | n |  | TRUE
37 | bus_LV_4401-12_0_4_node_179 | 0.4 | n |  | TRUE
38 | bus_LV_4401-12_0_4_node_17 | 0.4 | n |  | TRUE
39 | bus_LV_4401-12_0_4_node_126 | 0.4 | n |  | TRUE
40 | bus_LV_4401-12_0_4_node_124 | 0.4 | n |  | TRUE
41 | bus_LV_4401-12_0_4_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_4401-12_0_4_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_4401-12_0_4_node_38 | 0.4 | n |  | TRUE
44 | bus_LV_4401-12_0_4_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_4401-12_0_4_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_4401-12_0_4_node_81 | 0.4 | n |  | TRUE
47 | bus_LV_4401-12_0_4_node_74 | 0.4 | n |  | TRUE
48 | bus_LV_4401-12_0_4_node_68 | 0.4 | n |  | TRUE
49 | bus_LV_4401-12_0_4_node_60 | 0.4 | n |  | TRUE
50 | bus_LV_4401-12_0_4_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_4401-12_0_4_node_95 | 0.4 | n |  | TRUE
52 | bus_LV_4401-12_0_4_node_76 | 0.4 | n |  | TRUE
53 | bus_LV_4401-12_0_4_node_110 | 0.4 | n |  | TRUE
54 | bus_LV_4401-12_0_4_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_4401-12_0_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_4401-12_0_4_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_4401-12_0_4_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_4401-12_0_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_4401-12_0_4_node_85 | 0.4 | n |  | TRUE
60 | bus_LV_4401-12_0_4_node_82 | 0.4 | n |  | TRUE
61 | bus_LV_4401-12_0_4_node_28 | 0.4 | n |  | TRUE
62 | bus_LV_4401-12_0_4_node_30 | 0.4 | n |  | TRUE
63 | bus_LV_4401-12_0_4_node_174 | 0.4 | n |  | TRUE
64 | bus_LV_4401-12_0_4_node_130 | 0.4 | n |  | TRUE
65 | bus_LV_4401-12_0_4_node_91 | 0.4 | n |  | TRUE
66 | bus_LV_4401-12_0_4_node_125 | 0.4 | n |  | TRUE
67 | bus_LV_4401-12_0_4_node_40 | 0.4 | n |  | TRUE
68 | bus_LV_4401-12_0_4_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_4401-12_0_4_node_154 | 0.4 | n |  | TRUE
70 | bus_LV_4401-12_0_4_node_27 | 0.4 | n |  | TRUE
71 | bus_LV_4401-12_0_4_node_21 | 0.4 | n |  | TRUE
72 | bus_LV_4401-12_0_4_node_22 | 0.4 | n |  | TRUE
73 | bus_LV_4401-12_0_4_node_24 | 0.4 | n |  | TRUE
74 | bus_LV_4401-12_0_4_node_23 | 0.4 | n |  | TRUE
75 | bus_LV_4401-12_0_4_node_26 | 0.4 | n |  | TRUE
76 | bus_LV_4401-12_0_4_node_72 | 0.4 | n |  | TRUE
77 | bus_LV_4401-12_0_4_node_70 | 0.4 | n |  | TRUE
78 | bus_LV_4401-12_0_4_node_71 | 0.4 | n |  | TRUE
79 | bus_LV_4401-12_0_4_node_32 | 0.4 | n |  | TRUE
80 | bus_LV_4401-12_0_4_node_29 | 0.4 | n |  | TRUE
81 | bus_LV_4401-12_0_4_node_37 | 0.4 | n |  | TRUE
82 | bus_LV_4401-12_0_4_node_169 | 0.4 | n |  | TRUE
83 | bus_LV_4401-12_0_4_node_168 | 0.4 | n |  | TRUE
84 | bus_LV_4401-12_0_4_node_135 | 0.4 | n |  | TRUE
85 | bus_LV_4401-12_0_4_node_134 | 0.4 | n |  | TRUE
86 | bus_LV_4401-12_0_4_node_171 | 0.4 | n |  | TRUE
87 | bus_LV_4401-12_0_4_node_170 | 0.4 | n |  | TRUE
88 | bus_LV_4401-12_0_4_node_34 | 0.4 | n |  | TRUE
89 | bus_LV_4401-12_0_4_node_35 | 0.4 | n |  | TRUE
90 | bus_LV_4401-12_0_4_node_152 | 0.4 | n |  | TRUE
91 | bus_LV_4401-12_0_4_node_139 | 0.4 | n |  | TRUE
92 | bus_LV_4401-12_0_4_node_138 | 0.4 | n |  | TRUE
93 | bus_LV_4401-12_0_4_node_133 | 0.4 | n |  | TRUE
94 | bus_LV_4401-12_0_4_node_153 | 0.4 | n |  | TRUE
95 | bus_LV_4401-12_0_4_node_36 | 0.4 | n |  | TRUE
96 | bus_LV_4401-12_0_4_node_41 | 0.4 | n |  | TRUE
97 | bus_LV_4401-12_0_4_node_42 | 0.4 | n |  | TRUE
98 | bus_LV_4401-12_0_4_node_56 | 0.4 | n |  | TRUE
99 | bus_LV_4401-12_0_4_node_172 | 0.4 | n |  | TRUE
100 | bus_LV_4401-12_0_4_node_166 | 0.4 | n |  | TRUE
101 | bus_LV_4401-12_0_4_node_55 | 0.4 | n |  | TRUE
102 | bus_LV_4401-12_0_4_node_53 | 0.4 | n |  | TRUE
103 | bus_LV_4401-12_0_4_node_58 | 0.4 | n |  | TRUE
104 | bus_LV_4401-12_0_4_node_47 | 0.4 | n |  | TRUE
105 | bus_LV_4401-12_0_4_node_48 | 0.4 | n |  | TRUE
106 | bus_LV_4401-12_0_4_node_51 | 0.4 | n |  | TRUE
107 | bus_LV_4401-12_0_4_node_52 | 0.4 | n |  | TRUE
108 | bus_LV_4401-12_0_4_node_54 | 0.4 | n |  | TRUE
109 | bus_LV_4401-12_0_4_node_57 | 0.4 | n |  | TRUE
110 | bus_LV_4401-12_0_4_node_59 | 0.4 | n |  | TRUE
111 | bus_LV_4401-12_0_4_node_65 | 0.4 | n |  | TRUE
112 | bus_LV_4401-12_0_4_node_66 | 0.4 | n |  | TRUE
113 | bus_LV_4401-12_0_4_node_177 | 0.4 | n |  | TRUE
114 | bus_LV_4401-12_0_4_node_178 | 0.4 | n |  | TRUE
115 | bus_LV_4401-12_0_4_node_75 | 0.4 | n |  | TRUE
116 | bus_LV_4401-12_0_4_node_77 | 0.4 | n |  | TRUE
117 | bus_LV_4401-12_0_4_node_79 | 0.4 | n |  | TRUE
118 | bus_LV_4401-12_0_4_node_86 | 0.4 | n |  | TRUE
119 | bus_LV_4401-12_0_4_node_87 | 0.4 | n |  | TRUE
120 | bus_LV_4401-12_0_4_node_88 | 0.4 | n |  | TRUE
121 | bus_LV_4401-12_0_4_node_89 | 0.4 | n |  | TRUE
122 | bus_LV_4401-12_0_4_node_90 | 0.4 | n |  | TRUE
123 | bus_LV_4401-12_0_4_node_92 | 0.4 | n |  | TRUE
124 | bus_LV_4401-12_0_4_node_101 | 0.4 | n |  | TRUE
125 | bus_LV_4401-12_0_4_node_93 | 0.4 | n |  | TRUE
126 | bus_LV_4401-12_0_4_node_99 | 0.4 | n |  | TRUE
127 | bus_LV_4401-12_0_4_node_94 | 0.4 | n |  | TRUE
128 | bus_LV_4401-12_0_4_node_100 | 0.4 | n |  | TRUE
129 | bus_LV_4401-12_0_4_node_102 | 0.4 | n |  | TRUE
130 | bus_LV_4401-12_0_4_node_103 | 0.4 | n |  | TRUE
131 | bus_LV_4401-12_0_4_node_111 | 0.4 | n |  | TRUE
132 | bus_LV_4401-12_0_4_node_106 | 0.4 | n |  | TRUE
133 | bus_LV_4401-12_0_4_node_105 | 0.4 | n |  | TRUE
134 | bus_LV_4401-12_0_4_node_107 | 0.4 | n |  | TRUE
135 | bus_LV_4401-12_0_4_node_109 | 0.4 | n |  | TRUE
136 | bus_LV_4401-12_0_4_node_112 | 0.4 | n |  | TRUE
137 | bus_LV_4401-12_0_4_node_113 | 0.4 | n |  | TRUE
138 | bus_LV_4401-12_0_4_node_114 | 0.4 | n |  | TRUE
139 | bus_LV_4401-12_0_4_node_115 | 0.4 | n |  | TRUE
140 | bus_LV_4401-12_0_4_node_116 | 0.4 | n |  | TRUE
141 | bus_LV_4401-12_0_4_node_117 | 0.4 | n |  | TRUE
142 | bus_LV_4401-12_0_4_node_118 | 0.4 | n |  | TRUE
143 | bus_LV_4401-12_0_4_node_121 | 0.4 | n |  | TRUE
144 | bus_LV_4401-12_0_4_node_148 | 0.4 | n |  | TRUE
145 | bus_LV_4401-12_0_4_node_123 | 0.4 | n |  | TRUE
146 | bus_LV_4401-12_0_4_node_119 | 0.4 | n |  | TRUE
147 | bus_LV_4401-12_0_4_node_144 | 0.4 | n |  | TRUE
148 | bus_LV_4401-12_0_4_node_147 | 0.4 | n |  | TRUE
149 | bus_LV_4401-12_0_4_node_120 | 0.4 | n |  | TRUE
150 | bus_LV_4401-12_0_4_node_122 | 0.4 | n |  | TRUE
151 | bus_LV_4401-12_0_4_node_150 | 0.4 | n |  | TRUE
152 | bus_LV_4401-12_0_4_node_149 | 0.4 | n |  | TRUE
153 | bus_LV_4401-12_0_4_node_128 | 0.4 | n |  | TRUE
154 | bus_LV_4401-12_0_4_node_127 | 0.4 | n |  | TRUE
155 | bus_LV_4401-12_0_4_node_129 | 0.4 | n |  | TRUE
156 | bus_LV_4401-12_0_4_node_131 | 0.4 | n |  | TRUE
157 | bus_LV_4401-12_0_4_node_143 | 0.4 | n |  | TRUE
158 | bus_LV_4401-12_0_4_node_137 | 0.4 | n |  | TRUE
159 | bus_LV_4401-12_0_4_node_136 | 0.4 | n |  | TRUE
160 | bus_LV_4401-12_0_4_node_142 | 0.4 | n |  | TRUE
161 | bus_LV_4401-12_0_4_node_140 | 0.4 | n |  | TRUE
162 | bus_LV_4401-12_0_4_node_141 | 0.4 | n |  | TRUE
163 | bus_LV_4401-12_0_4_node_145 | 0.4 | n |  | TRUE
164 | bus_LV_4401-12_0_4_node_146 | 0.4 | n |  | TRUE
165 | bus_LV_4401-12_0_4_node_151 | 0.4 | n |  | TRUE
166 | bus_LV_4401-12_0_4_node_155 | 0.4 | n |  | TRUE
167 | bus_LV_4401-12_0_4_node_156 | 0.4 | n |  | TRUE
168 | bus_LV_4401-12_0_4_node_157 | 0.4 | n |  | TRUE
169 | bus_LV_4401-12_0_4_node_158 | 0.4 | n |  | TRUE
170 | bus_LV_4401-12_0_4_node_159 | 0.4 | n |  | TRUE
171 | bus_LV_4401-12_0_4_node_164 | 0.4 | n |  | TRUE
172 | bus_LV_4401-12_0_4_node_162 | 0.4 | n |  | TRUE
173 | bus_LV_4401-12_0_4_node_160 | 0.4 | n |  | TRUE
174 | bus_LV_4401-12_0_4_node_161 | 0.4 | n |  | TRUE
175 | bus_LV_4401-12_0_4_node_163 | 0.4 | n |  | TRUE
176 | bus_LV_4401-12_0_4_node_165 | 0.4 | n |  | TRUE
177 | bus_LV_4401-12_0_4_node_167 | 0.4 | n |  | TRUE
178 | bus_LV_4401-12_0_4_node_173 | 0.4 | n |  | TRUE
179 | bus_MV_406_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4401-12_0_4_load_0 | 0 | 0.0075187 | 0.0018844 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4401-12_0_4_load_20 | 4 | 0.012486 | 0.0031292 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4401-12_0_4_load_80 | 6 | 0.0011603 | 0.00029081 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4401-12_0_4_load_73 | 10 | 0.0011199 | 0.00028066 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4401-12_0_4_load_67 | 11 | 0.0010496 | 0.00026307 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4401-12_0_4_load_61 | 12 | 0.0024033 | 0.00060231 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4401-12_0_4_load_63 | 13 | 0.002419 | 0.00060625 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4401-12_0_4_load_176 | 15 | 0.0017979 | 0.00045061 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4401-12_0_4_load_175 | 16 | 0.0042528 | 0.0010658 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4401-12_0_4_load_69 | 18 | 0.00096846 | 0.00024272 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4401-12_0_4_load_96 | 21 | 0.0015373 | 0.00038528 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4401-12_0_4_load_62 | 24 | 0.0081137 | 0.0020335 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4401-12_0_4_load_78 | 25 | 0.0023668 | 0.00059316 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4401-12_0_4_load_98 | 28 | 0.0015441 | 0.00038699 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4401-12_0_4_load_44 | 30 | 0.0013496 | 0.00033824 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4401-12_0_4_load_84 | 32 | 3.2713e-05 | 8.1986e-06 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4401-12_0_4_load_83 | 33 | 3.6753e-05 | 9.2111e-06 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4401-12_0_4_load_132 | 36 | 0.0028651 | 0.00071807 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4401-12_0_4_load_179 | 37 | 0.0031872 | 0.00079879 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4401-12_0_4_load_124 | 40 | 4.6217e-05 | 1.1583e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4401-12_0_4_load_38 | 43 | 0.003236 | 0.00081102 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4401-12_0_4_load_33 | 44 | 0.0014331 | 0.00035918 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4401-12_0_4_load_31 | 45 | 0.0030262 | 0.00075843 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4401-12_0_4_load_81 | 46 | 3.9082e-05 | 9.7948e-06 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4401-12_0_4_load_74 | 47 | 0.0012325 | 0.00030889 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4401-12_0_4_load_68 | 48 | 0.00097901 | 0.00024536 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4401-12_0_4_load_60 | 49 | 0.0022834 | 0.00057228 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4401-12_0_4_load_95 | 51 | 0.0017758 | 0.00044507 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4401-12_0_4_load_76 | 52 | 0.00095596 | 0.00023959 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4401-12_0_4_load_110 | 53 | 0.0020069 | 0.00050297 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4401-12_0_4_load_108 | 54 | 0.0062598 | 0.0015689 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4401-12_0_4_load_49 | 55 | 0.0017891 | 0.0004484 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4401-12_0_4_load_50 | 56 | 0.0025193 | 0.00063139 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4401-12_0_4_load_46 | 57 | 0.0028187 | 0.00070644 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4401-12_0_4_load_43 | 58 | 0.0013124 | 0.00032891 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4401-12_0_4_load_85 | 59 | 0.0015064 | 0.00037753 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4401-12_0_4_load_82 | 60 | 5.1413e-05 | 1.2885e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4401-12_0_4_load_174 | 63 | 0.0030483 | 0.00076396 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4401-12_0_4_load_130 | 64 | 0.0038796 | 0.00097232 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4401-12_0_4_load_125 | 66 | 0.0002274 | 5.6992e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4401-12_0_4_load_40 | 67 | 0.0022092 | 0.00055368 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4401-12_0_4_load_39 | 68 | 0.0082496 | 0.0020675 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4401-12_0_4_load_154 | 69 | 0.0027474 | 0.00068856 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4401-12_0_4_load_21 | 71 | 0.029119 | 0.007298 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4401-12_0_4_load_72 | 76 | 0.00047212 | 0.00011832 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4401-12_0_4_load_70 | 77 | 0.00022457 | 5.6282e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4401-12_0_4_load_71 | 78 | 0.00074357 | 0.00018636 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4401-12_0_4_load_169 | 82 | 0.0016148 | 0.00040471 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4401-12_0_4_load_168 | 83 | 0.0015762 | 0.00039502 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4401-12_0_4_load_134 | 85 | 0.0017679 | 0.00044308 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4401-12_0_4_load_171 | 86 | 0.0025728 | 0.00064482 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4401-12_0_4_load_170 | 87 | 0.00092753 | 0.00023246 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4401-12_0_4_load_34 | 88 | 0.0033639 | 0.00084306 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4401-12_0_4_load_35 | 89 | 0.0031783 | 0.00079657 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4401-12_0_4_load_152 | 90 | 0.003331 | 0.00083484 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4401-12_0_4_load_139 | 91 | 0.0021417 | 0.00053676 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4401-12_0_4_load_138 | 92 | 0.0016284 | 0.00040811 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4401-12_0_4_load_133 | 93 | 0.0017778 | 0.00044557 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4401-12_0_4_load_153 | 94 | 0.0022428 | 0.0005621 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4401-12_0_4_load_41 | 96 | 0.0021862 | 0.00054792 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4401-12_0_4_load_42 | 97 | 0.0017606 | 0.00044125 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4401-12_0_4_load_56 | 98 | 0.003 | 0.00075188 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4401-12_0_4_load_172 | 99 | 0.00078806 | 0.00019751 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4401-12_0_4_load_55 | 101 | 0.0024674 | 0.0006184 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4401-12_0_4_load_53 | 102 | 0.0025461 | 0.0006381 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4401-12_0_4_load_58 | 103 | 0.0031447 | 0.00078812 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4401-12_0_4_load_47 | 104 | 0.0024985 | 0.00062619 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4401-12_0_4_load_48 | 105 | 0.0015524 | 0.00038906 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4401-12_0_4_load_51 | 106 | 0.0028847 | 0.00072298 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4401-12_0_4_load_52 | 107 | 0.0027942 | 0.00070029 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4401-12_0_4_load_54 | 108 | 0.0017069 | 0.0004278 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4401-12_0_4_load_57 | 109 | 0.0023507 | 0.00058913 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4401-12_0_4_load_59 | 110 | 0.0064435 | 0.0016149 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4401-12_0_4_load_65 | 111 | 0.00094964 | 0.000238 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4401-12_0_4_load_66 | 112 | 0.00095503 | 0.00023935 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4401-12_0_4_load_177 | 113 | 0.0020485 | 0.00051341 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4401-12_0_4_load_178 | 114 | 0.0010147 | 0.00025431 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4401-12_0_4_load_75 | 115 | 0.00093608 | 0.0002346 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4401-12_0_4_load_77 | 116 | 0.0006396 | 0.0001603 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4401-12_0_4_load_79 | 117 | 0.0040385 | 0.0010121 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4401-12_0_4_load_86 | 118 | 0.002339 | 0.00058621 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4401-12_0_4_load_87 | 119 | 0.0021998 | 0.00055132 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4401-12_0_4_load_88 | 120 | 0.0020926 | 0.00052445 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4401-12_0_4_load_92 | 123 | 0.00095739 | 0.00023995 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4401-12_0_4_load_101 | 124 | 0.0022077 | 0.00055331 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4401-12_0_4_load_93 | 125 | 0.0014495 | 0.00036328 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4401-12_0_4_load_99 | 126 | 0.0027206 | 0.00068185 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4401-12_0_4_load_94 | 127 | 0.0036064 | 0.00090386 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4401-12_0_4_load_100 | 128 | 0.0023434 | 0.00058731 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4401-12_0_4_load_102 | 129 | 0.0054975 | 0.0013778 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4401-12_0_4_load_103 | 130 | 0.0028993 | 0.00072665 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_4401-12_0_4_load_111 | 131 | 0.0021887 | 0.00054853 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_4401-12_0_4_load_106 | 132 | 0.001761 | 0.00044134 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_4401-12_0_4_load_105 | 133 | 0.0042936 | 0.0010761 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_4401-12_0_4_load_107 | 134 | 0.0020661 | 0.00051781 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_4401-12_0_4_load_109 | 135 | 0.0019996 | 0.00050115 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_4401-12_0_4_load_112 | 136 | 0.0031891 | 0.00079927 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_4401-12_0_4_load_113 | 137 | 0.0021605 | 0.00054147 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_4401-12_0_4_load_114 | 138 | 0.0026585 | 0.00066627 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_4401-12_0_4_load_115 | 139 | 0.0013985 | 0.0003505 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_4401-12_0_4_load_116 | 140 | 0.0016915 | 0.00042394 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_4401-12_0_4_load_117 | 141 | 0.0026424 | 0.00066225 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_4401-12_0_4_load_123 | 145 | 0.0020323 | 0.00050935 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_4401-12_0_4_load_119 | 146 | 0.0041469 | 0.0010393 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_4401-12_0_4_load_144 | 147 | 0.0025504 | 0.0006392 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_4401-12_0_4_load_147 | 148 | 0.0018424 | 0.00046175 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_4401-12_0_4_load_120 | 149 | 0.0022777 | 0.00057084 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_4401-12_0_4_load_122 | 150 | 0.0084791 | 0.0021251 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_4401-12_0_4_load_150 | 151 | 0.0021009 | 0.00052654 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_4401-12_0_4_load_149 | 152 | 0.0019304 | 0.00048379 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_4401-12_0_4_load_128 | 153 | 6.1211e-05 | 1.5341e-05 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_4401-12_0_4_load_127 | 154 | 0.00010979 | 2.7516e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_4401-12_0_4_load_129 | 155 | 0.0037823 | 0.00094794 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_4401-12_0_4_load_131 | 156 | 0.0030032 | 0.00075267 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_4401-12_0_4_load_137 | 158 | 0.0016097 | 0.00040342 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_4401-12_0_4_load_136 | 159 | 0.001644 | 0.00041201 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_4401-12_0_4_load_142 | 160 | 0.0019127 | 0.00047936 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_4401-12_0_4_load_140 | 161 | 0.0019905 | 0.00049887 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_4401-12_0_4_load_141 | 162 | 0.001995 | 0.00049999 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_4401-12_0_4_load_145 | 163 | 0.0019729 | 0.00049446 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_4401-12_0_4_load_146 | 164 | 0.0018272 | 0.00045793 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_4401-12_0_4_load_151 | 165 | 0.0020772 | 0.0005206 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_4401-12_0_4_load_155 | 166 | 0.00099303 | 0.00024888 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_4401-12_0_4_load_156 | 167 | 0.0035992 | 0.00090205 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_4401-12_0_4_load_157 | 168 | 0.0017169 | 0.00043031 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_4401-12_0_4_load_158 | 169 | 0.0022116 | 0.00055429 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_4401-12_0_4_load_164 | 171 | 0.0022909 | 0.00057416 | 0 | 0 |  | 1 | TRUE | wye
127 | LV_4401-12_0_4_load_162 | 172 | 0.0033413 | 0.00083742 | 0 | 0 |  | 1 | TRUE | wye
128 | LV_4401-12_0_4_load_160 | 173 | 0.00057477 | 0.00014405 | 0 | 0 |  | 1 | TRUE | wye
129 | LV_4401-12_0_4_load_161 | 174 | 0.0039607 | 0.00099263 | 0 | 0 |  | 1 | TRUE | wye
130 | LV_4401-12_0_4_load_163 | 175 | 0.0012793 | 0.00032063 | 0 | 0 |  | 1 | TRUE | wye
131 | LV_4401-12_0_4_load_165 | 176 | 0.0051055 | 0.0012796 | 0 | 0 |  | 1 | TRUE | wye
132 | LV_4401-12_0_4_load_167 | 177 | 0.00070876 | 0.00017763 | 0 | 0 |  | 1 | TRUE | wye
133 | LV_4401-12_0_4_load_173 | 178 | 0.0046351 | 0.0011617 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 140 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4401-12_0_4_line_0 |  | 0 | 1 | 0.089758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4401-12_0_4_line_1 |  | 0 | 2 | 0.14791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4401-12_0_4_line_2 |  | 1 | 3 | 0.014883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4401-12_0_4_line_3 |  | 2 | 4 | 0.014467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4401-12_0_4_line_4 |  | 3 | 5 | 0.005458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4401-12_0_4_line_5 |  | 3 | 6 | 0.051462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4401-12_0_4_line_6 |  | 5 | 15 | 0.035236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4401-12_0_4_line_7 |  | 5 | 17 | 0.039915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4401-12_0_4_line_8 |  | 6 | 46 | 0.02957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4401-12_0_4_line_9 |  | 7 | 8 | 0.028799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4401-12_0_4_line_10 |  | 7 | 9 | 0.028975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4401-12_0_4_line_11 |  | 7 | 10 | 0.024725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4401-12_0_4_line_12 |  | 8 | 21 | 0.024608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4401-12_0_4_line_13 |  | 8 | 25 | 0.017791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4401-12_0_4_line_14 |  | 9 | 11 | 0.0085015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4401-12_0_4_line_15 |  | 9 | 12 | 0.039061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4401-12_0_4_line_16 |  | 9 | 13 | 0.015528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4401-12_0_4_line_17 |  | 10 | 47 | 0.030075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4401-12_0_4_line_18 |  | 11 | 48 | 0.017982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4401-12_0_4_line_19 |  | 12 | 49 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4401-12_0_4_line_20 |  | 13 | 50 | 0.015649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4401-12_0_4_line_21 |  | 14 | 15 | 0.01535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4401-12_0_4_line_22 |  | 14 | 16 | 0.011113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4401-12_0_4_line_23 |  | 17 | 18 | 0.032484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4401-12_0_4_line_24 |  | 18 | 48 | 0.018792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4401-12_0_4_line_25 |  | 19 | 20 | 0.011925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4401-12_0_4_line_26 |  | 19 | 21 | 0.033165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_4401-12_0_4_line_27 |  | 19 | 22 | 0.010261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_4401-12_0_4_line_28 |  | 20 | 23 | 0.024222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4401-12_0_4_line_29 |  | 20 | 24 | 0.00084618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4401-12_0_4_line_30 |  | 22 | 28 | 0.022185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_4401-12_0_4_line_31 |  | 22 | 51 | 0.026033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4401-12_0_4_line_32 |  | 23 | 29 | 0.033044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4401-12_0_4_line_33 |  | 23 | 30 | 0.011996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4401-12_0_4_line_34 |  | 25 | 52 | 0.009325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4401-12_0_4_line_35 |  | 26 | 27 | 0.023183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_4401-12_0_4_line_36 |  | 26 | 28 | 0.058526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_4401-12_0_4_line_37 |  | 27 | 53 | 0.013841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_4401-12_0_4_line_38 |  | 27 | 54 | 0.0010253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4401-12_0_4_line_39 |  | 29 | 55 | 0.019043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4401-12_0_4_line_40 |  | 29 | 56 | 0.052357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4401-12_0_4_line_41 |  | 29 | 57 | 0.011286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_4401-12_0_4_line_42 |  | 30 | 58 | 0.015596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4401-12_0_4_line_43 |  | 31 | 32 | 0.014577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4401-12_0_4_line_44 |  | 31 | 33 | 0.043335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4401-12_0_4_line_45 |  | 32 | 59 | 0.010843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4401-12_0_4_line_46 |  | 33 | 60 | 0.027203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4401-12_0_4_line_47 |  | 34 | 35 | 0.006268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_4401-12_0_4_line_48 |  | 34 | 36 | 0.011233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4401-12_0_4_line_49 |  | 35 | 37 | 0.056282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4401-12_0_4_line_50 |  | 36 | 61 | 0.0084286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4401-12_0_4_line_51 |  | 38 | 39 | 0.039692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4401-12_0_4_line_52 |  | 38 | 40 | 0.035167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_4401-12_0_4_line_53 |  | 39 | 64 | 0.023926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_4401-12_0_4_line_54 |  | 39 | 65 | 0.051224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4401-12_0_4_line_55 |  | 40 | 66 | 0.01217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4401-12_0_4_line_56 |  | 41 | 42 | 0.017305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4401-12_0_4_line_57 |  | 41 | 43 | 0.019345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4401-12_0_4_line_58 |  | 42 | 44 | 0.022231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4401-12_0_4_line_59 |  | 42 | 45 | 0.017387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4401-12_0_4_line_60 |  | 43 | 68 | 0.010701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4401-12_0_4_line_61 |  | 44 | 69 | 0.011266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4401-12_0_4_line_62 |  | 45 | 70 | 0.0053831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4401-12_0_4_line_63 |  | 46 | 60 | 0.032738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4401-12_0_4_line_64 |  | 47 | 115 | 0.0050527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4401-12_0_4_line_65 |  | 50 | 111 | 0.0031153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4401-12_0_4_line_66 |  | 50 | 112 | 0.014953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4401-12_0_4_line_67 |  | 51 | 127 | 0.008983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4401-12_0_4_line_68 |  | 52 | 116 | 0.011464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4401-12_0_4_line_69 |  | 53 | 131 | 0.02041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_4401-12_0_4_line_70 |  | 54 | 132 | 0.010072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4401-12_0_4_line_71 |  | 55 | 102 | 0.0082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4401-12_0_4_line_72 |  | 56 | 103 | 0.013139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4401-12_0_4_line_73 |  | 57 | 104 | 0.026843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4401-12_0_4_line_74 |  | 58 | 67 | 0.027695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4401-12_0_4_line_75 |  | 59 | 118 | 0.014064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4401-12_0_4_line_76 |  | 61 | 62 | 0.00785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4401-12_0_4_line_77 |  | 61 | 74 | 0.15325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4401-12_0_4_line_78 |  | 62 | 63 | 0.049346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4401-12_0_4_line_79 |  | 63 | 90 | 0.053917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4401-12_0_4_line_80 |  | 64 | 153 | 0.0076858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4401-12_0_4_line_81 |  | 65 | 124 | 0.01734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4401-12_0_4_line_82 |  | 65 | 121 | 0.009418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4401-12_0_4_line_83 |  | 69 | 94 | 0.010683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4401-12_0_4_line_84 |  | 70 | 79 | 0.024631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4401-12_0_4_line_85 |  | 70 | 80 | 0.11225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4401-12_0_4_line_86 |  | 71 | 72 | 0.024841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4401-12_0_4_line_87 |  | 72 | 73 | 0.004936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4401-12_0_4_line_88 |  | 73 | 76 | 0.041559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4401-12_0_4_line_89 |  | 73 | 77 | 0.019665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4401-12_0_4_line_90 |  | 74 | 75 | 0.005658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4401-12_0_4_line_91 |  | 75 | 78 | 0.029268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4401-12_0_4_line_92 |  | 77 | 78 | 0.021998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4401-12_0_4_line_93 |  | 79 | 84 | 0.026938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4401-12_0_4_line_94 |  | 79 | 85 | 0.02204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4401-12_0_4_line_95 |  | 80 | 81 | 0.18085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4401-12_0_4_line_96 |  | 81 | 86 | 0.016396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4401-12_0_4_line_97 |  | 81 | 87 | 0.037892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4401-12_0_4_line_98 |  | 82 | 83 | 0.0042172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4401-12_0_4_line_99 |  | 83 | 177 | 0.01201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4401-12_0_4_line_100 |  | 84 | 91 | 0.0235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4401-12_0_4_line_101 |  | 84 | 92 | 0.011193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4401-12_0_4_line_102 |  | 85 | 93 | 0.021483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4401-12_0_4_line_103 |  | 86 | 99 | 0.015253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4401-12_0_4_line_104 |  | 87 | 100 | 0.011683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4401-12_0_4_line_105 |  | 88 | 89 | 0.033255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4401-12_0_4_line_106 |  | 89 | 95 | 0.10971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4401-12_0_4_line_107 |  | 90 | 150 | 0.054205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4401-12_0_4_line_108 |  | 91 | 157 | 0.0029136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4401-12_0_4_line_109 |  | 92 | 158 | 0.016397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4401-12_0_4_line_110 |  | 95 | 96 | 0.014827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4401-12_0_4_line_111 |  | 95 | 97 | 0.052072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4401-12_0_4_line_112 |  | 96 | 98 | 0.0092338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4401-12_0_4_line_113 |  | 98 | 101 | 0.016776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_4401-12_0_4_line_114 |  | 99 | 178 | 0.017827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_4401-12_0_4_line_115 |  | 100 | 170 | 0.016047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_4401-12_0_4_line_116 |  | 101 | 108 | 0.0054748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_4401-12_0_4_line_117 |  | 102 | 108 | 0.0045784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_4401-12_0_4_line_118 |  | 103 | 109 | 6.9594e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_4401-12_0_4_line_119 |  | 104 | 105 | 0.020619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_4401-12_0_4_line_120 |  | 105 | 106 | 0.00019396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_4401-12_0_4_line_121 |  | 106 | 107 | 0.0023241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_4401-12_0_4_line_122 |  | 109 | 110 | 0.018149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_4401-12_0_4_line_123 |  | 111 | 113 | 0.01275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_4401-12_0_4_line_124 |  | 112 | 114 | 0.01893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_4401-12_0_4_line_125 |  | 116 | 117 | 0.00093784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_4401-12_0_4_line_126 |  | 119 | 120 | 0.0082084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_4401-12_0_4_line_127 |  | 119 | 121 | 0.0061629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_4401-12_0_4_line_128 |  | 120 | 122 | 0.0061654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_4401-12_0_4_line_129 |  | 122 | 123 | 0.02188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_4401-12_0_4_line_130 |  | 123 | 125 | 0.0038633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_4401-12_0_4_line_131 |  | 124 | 126 | 0.0030869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_4401-12_0_4_line_132 |  | 125 | 127 | 0.012409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_4401-12_0_4_line_133 |  | 126 | 128 | 0.023091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_4401-12_0_4_line_134 |  | 128 | 129 | 0.012863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_4401-12_0_4_line_135 |  | 129 | 130 | 0.013147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_4401-12_0_4_line_136 |  | 131 | 136 | 0.01872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
137 | LV_4401-12_0_4_line_137 |  | 132 | 133 | 0.010612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_4401-12_0_4_line_138 |  | 133 | 134 | 0.013259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_4401-12_0_4_line_139 |  | 134 | 135 | 0.0076804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_4401-12_0_4_line_140 |  | 136 | 137 | 0.030702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
141 | LV_4401-12_0_4_line_141 |  | 137 | 138 | 0.0043681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
142 | LV_4401-12_0_4_line_142 |  | 138 | 139 | 0.0072635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
143 | LV_4401-12_0_4_line_143 |  | 139 | 140 | 0.0066291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
144 | LV_4401-12_0_4_line_144 |  | 140 | 141 | 0.021717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
145 | LV_4401-12_0_4_line_145 |  | 141 | 142 | 0.01397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
146 | LV_4401-12_0_4_line_146 |  | 142 | 143 | 0.003676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_4401-12_0_4_line_147 |  | 142 | 144 | 0.021985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_4401-12_0_4_line_148 |  | 143 | 145 | 0.0088988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_4401-12_0_4_line_149 |  | 143 | 146 | 0.0089707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_4401-12_0_4_line_150 |  | 144 | 147 | 0.0081601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_4401-12_0_4_line_151 |  | 144 | 148 | 0.01165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_4401-12_0_4_line_152 |  | 145 | 151 | 0.016402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_4401-12_0_4_line_153 |  | 146 | 149 | 0.01574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_4401-12_0_4_line_154 |  | 147 | 157 | 0.017529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_4401-12_0_4_line_155 |  | 148 | 164 | 0.015632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
156 | LV_4401-12_0_4_line_156 |  | 149 | 150 | 0.028284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
157 | LV_4401-12_0_4_line_157 |  | 151 | 152 | 0.016009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
158 | LV_4401-12_0_4_line_158 |  | 152 | 165 | 0.00055296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
159 | LV_4401-12_0_4_line_159 |  | 153 | 154 | 0.029525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
160 | LV_4401-12_0_4_line_160 |  | 154 | 155 | 0.00035458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
161 | LV_4401-12_0_4_line_161 |  | 155 | 156 | 0.012027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
162 | LV_4401-12_0_4_line_162 |  | 157 | 160 | 0.011779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
163 | LV_4401-12_0_4_line_163 |  | 158 | 159 | 0.015935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
164 | LV_4401-12_0_4_line_164 |  | 160 | 162 | 0.016126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
165 | LV_4401-12_0_4_line_165 |  | 161 | 162 | 0.016066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
166 | LV_4401-12_0_4_line_166 |  | 163 | 164 | 0.016346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
167 | LV_4401-12_0_4_line_167 |  | 166 | 167 | 0.00055733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
168 | LV_4401-12_0_4_line_168 |  | 166 | 168 | 0.0013845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
169 | LV_4401-12_0_4_line_169 |  | 167 | 169 | 0.00013196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
170 | LV_4401-12_0_4_line_170 |  | 168 | 170 | 0.01448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
171 | LV_4401-12_0_4_line_171 |  | 169 | 171 | 0.005279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
172 | LV_4401-12_0_4_line_172 |  | 171 | 172 | 0.00049443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
173 | LV_4401-12_0_4_line_173 |  | 172 | 173 | 0.00026449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
174 | LV_4401-12_0_4_line_174 |  | 173 | 174 | 0.0045428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
175 | LV_4401-12_0_4_line_175 |  | 174 | 175 | 0.0037136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
176 | LV_4401-12_0_4_line_176 |  | 175 | 176 | 0.0054438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
177 | LV_4401-12_0_4_line_177 |  | 176 | 177 | 0.0083696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4401-12_0_4_trafo_116 | 0.63 MVA 20/0.4 kV | 179 | 140 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2748734.066 | 1265262.233 | 2748724.9219 | 1265272.3131 | 2748699.8697 | 1265300.489 | 2748683.9994 | 1265318.8862 | 2748676.6952 | 1265331.0036
1 | 2748577.1448 | 1265440.1328 | 2748648.2732 | 1265359.284 | 2748657.2218 | 1265352.4688 | 2748676.6952 | 1265331.0036
2 | 2748720.7471 | 1265255.5913 | 2748723.7155 | 1265257.0897 | 2748729.3411 | 1265259.8784 | 2748734.066 | 1265262.233
3 | 2748588.2879 | 1265449.4 | 2748577.1448 | 1265440.1328
4 | 2748715.8432 | 1265253.1655 | 2748720.7471 | 1265255.5913
5 | 2748720.7471 | 1265255.5913 | 2748719.5932 | 1265258.3317 | 2748717.3016 | 1265262.5672 | 2748713.7674 | 1265267.6834 | 2748708.3479 | 1265274.3649 | 2748693.5001 | 1265292.2428 | 2748689.8443 | 1265296.5006
6 | 2748715.8432 | 1265253.1655 | 2748713.2635 | 1265258.6728 | 2748709.7237 | 1265262.8101 | 2748696.8468 | 1265268.5365 | 2748692.4186 | 1265259.9994
7 | 2748715.8432 | 1265253.1655 | 2748715.9009 | 1265250.2751 | 2748715.1051 | 1265246.5736 | 2748713.9485 | 1265244.3312 | 2748711.4377 | 1265242.911 | 2748707.6081 | 1265242.1028 | 2748708.0199 | 1265236.8189 | 2748708.2742 | 1265233.5999 | 2748708.8192 | 1265226.6177 | 2748709.0334 | 1265223.798 | 2748709.4591 | 1265218.2587
8 | 2748689.8443 | 1265296.5006 | 2748670.5816 | 1265318.9354
9 | 2748618.6511 | 1265238.251 | 2748589.7657 | 1265238.225
10 | 2748618.6511 | 1265238.251 | 2748616.4739 | 1265232.2569 | 2748632.8133 | 1265231.7449 | 2748632.0503 | 1265225.5418
11 | 2748618.6511 | 1265238.251 | 2748627.0922 | 1265261.4901
12 | 2748589.7657 | 1265238.225 | 2748565.1573 | 1265238.2551
13 | 2748589.7657 | 1265238.225 | 2748595.4674 | 1265255.0775
14 | 2748632.0503 | 1265225.5418 | 2748640.5312 | 1265224.9513
15 | 2748632.0503 | 1265225.5418 | 2748601.5387 | 1265226.6648 | 2748593.0104 | 1265226.7828
16 | 2748632.0503 | 1265225.5418 | 2748631.3875 | 1265220.1419 | 2748629.0106 | 1265210.3385
17 | 2748627.0922 | 1265261.4901 | 2748637.3601 | 1265289.7582
18 | 2748658.458 | 1265223.5419 | 2748645.545 | 1265224.6023 | 2748640.5312 | 1265224.9513
19 | 2748572.638 | 1265227.0646 | 2748593.0104 | 1265226.7828
20 | 2748628.6903 | 1265194.693 | 2748629.0053 | 1265210.3166 | 2748629.0106 | 1265210.3385
21 | 2748684.0384 | 1265247.3041 | 2748688.0375 | 1265251.5534 | 2748692.4186 | 1265259.9994
22 | 2748684.0384 | 1265247.3041 | 2748672.9253 | 1265247.3886
23 | 2748709.4591 | 1265218.2587 | 2748693.2662 | 1265220.1311 | 2748677.1632 | 1265221.7431
24 | 2748677.1632 | 1265221.7431 | 2748662.5472 | 1265223.2062 | 2748658.458 | 1265223.5419
25 | 2748531.4703 | 1265226.3816 | 2748531.7274 | 1265232.3385 | 2748531.9919 | 1265238.2956
26 | 2748531.9919 | 1265238.2956 | 2748565.1573 | 1265238.2551
27 | 2748521.7001 | 1265238.3037 | 2748531.9919 | 1265238.2956
28 | 2748531.4703 | 1265226.3816 | 2748507.1856 | 1265227.0612
29 | 2748532.3162 | 1265226.4051 | 2748531.4703 | 1265226.3816
30 | 2748521.7001 | 1265238.3037 | 2748499.5153 | 1265238.3574
31 | 2748521.7001 | 1265238.3037 | 2748528.3509 | 1265259.9481 | 2748529.3462 | 1265263.1888
32 | 2748502.0877 | 1265194.8897 | 2748506.4804 | 1265205.6664 | 2748506.6331 | 1265213.6783 | 2748507.2086 | 1265226.1497 | 2748507.1856 | 1265227.0612
33 | 2748507.1856 | 1265227.0612 | 2748495.1916 | 1265227.2655
34 | 2748598.4559 | 1265263.9106 | 2748595.4674 | 1265255.0775
35 | 2748449.2139 | 1265260.183 | 2748440.9892 | 1265238.4992
36 | 2748440.9892 | 1265238.4992 | 2748499.5153 | 1265238.3574
37 | 2748449.2139 | 1265260.183 | 2748436.6623 | 1265266.0167
38 | 2748449.2139 | 1265260.183 | 2748449.5963 | 1265261.1343
39 | 2748502.0877 | 1265194.8897 | 2748493.5284 | 1265177.8782
40 | 2748502.0877 | 1265194.8897 | 2748459.4385 | 1265195.408 | 2748454.2926 | 1265194.211 | 2748451.1638 | 1265191.0868
41 | 2748502.0877 | 1265194.8897 | 2748513.3724 | 1265194.6879
42 | 2748495.1916 | 1265227.2655 | 2748479.5983 | 1265227.5312
43 | 2748602.33 | 1265396.4441 | 2748598.5032 | 1265382.3779
44 | 2748602.33 | 1265396.4441 | 2748631.0053 | 1265363.9531
45 | 2748598.5032 | 1265382.3779 | 2748595.6568 | 1265371.9156
46 | 2748649.0056 | 1265343.5575 | 2748631.0053 | 1265363.9531
47 | 2748481.5331 | 1265542.2779 | 2748476.6681 | 1265538.3072
48 | 2748481.5331 | 1265542.2779 | 2748474.0567 | 1265550.662
49 | 2748496.4431 | 1265495.5054 | 2748468.7906 | 1265524.7069 | 2748471.5874 | 1265532.7296 | 2748473.5604 | 1265535.76 | 2748476.6681 | 1265538.3072
50 | 2748468.4471 | 1265556.9529 | 2748474.0567 | 1265550.662
51 | 2748562.9609 | 1265378.3365 | 2748569.8219 | 1265408.0833 | 2748573.5514 | 1265416.4632
52 | 2748573.5514 | 1265416.4632 | 2748546.6422 | 1265439.1042
53 | 2748562.9609 | 1265378.3365 | 2748540.292 | 1265385.9904
54 | 2748562.9609 | 1265378.3365 | 2748557.4147 | 1265354.4176 | 2748549.5349 | 1265328.9273
55 | 2748537.3302 | 1265446.9392 | 2748546.6422 | 1265439.1042
56 | 2748370.3375 | 1265233.8544 | 2748382.681 | 1265233.753 | 2748382.3156 | 1265228.8055
57 | 2748382.3156 | 1265228.8055 | 2748381.3283 | 1265215.3228 | 2748386.5233 | 1265212.6851
58 | 2748370.3375 | 1265233.8544 | 2748379.8213 | 1265253.961
59 | 2748370.3375 | 1265233.8544 | 2748352.9507 | 1265233.9018
60 | 2748396.0648 | 1265207.8407 | 2748386.5233 | 1265212.6851
61 | 2748384.6275 | 1265264.1505 | 2748379.8213 | 1265253.961
62 | 2748347.5677 | 1265233.9164 | 2748352.9507 | 1265233.9018
63 | 2748670.5816 | 1265318.9354 | 2748665.0459 | 1265325.3827 | 2748649.0056 | 1265343.5575
64 | 2748637.3601 | 1265289.7582 | 2748639.0851 | 1265294.5073
65 | 2748628.6903 | 1265194.693 | 2748625.578 | 1265194.5557
66 | 2748628.6903 | 1265194.693 | 2748643.552 | 1265196.3459
67 | 2748529.3462 | 1265263.1888 | 2748531.9834 | 1265271.776
68 | 2748598.4559 | 1265263.9106 | 2748602.1301 | 1265274.7703
69 | 2748436.6623 | 1265266.0167 | 2748430.5295 | 1265268.867 | 2748422.8639 | 1265272.3003 | 2748425.0437 | 1265277.0738
70 | 2748449.5963 | 1265261.1343 | 2748453.3523 | 1265270.4799
71 | 2748489.8428 | 1265170.5532 | 2748493.5284 | 1265177.8782
72 | 2748451.1638 | 1265191.0868 | 2748450.1106 | 1265190.0351 | 2748444.8529 | 1265179.6387
73 | 2748513.3724 | 1265194.6879 | 2748518.889 | 1265194.5892 | 2748534.2609 | 1265193.908 | 2748540.0043 | 1265192.4001
74 | 2748451.9072 | 1265228.0007 | 2748452.3359 | 1265227.9957 | 2748479.5983 | 1265227.5312
75 | 2748591.9649 | 1265358.3453 | 2748595.6568 | 1265371.9156
76 | 2748468.4471 | 1265556.9529 | 2748466.6049 | 1265549.3211
77 | 2748366.5922 | 1265671.4553 | 2748386.6293 | 1265648.7576 | 2748412.0634 | 1265619.956 | 2748451.5765 | 1265576.2375 | 2748468.4471 | 1265556.9529
78 | 2748466.6049 | 1265549.3211 | 2748448.6608 | 1265503.3531
79 | 2748448.6608 | 1265503.3531 | 2748429.0547 | 1265453.127
80 | 2748533.01 | 1265388.449 | 2748540.292 | 1265385.9904
81 | 2748549.5349 | 1265328.9273 | 2748533.0915 | 1265334.4297
82 | 2748549.5349 | 1265328.9273 | 2748546.8235 | 1265319.9057
83 | 2748384.6275 | 1265264.1505 | 2748389.185 | 1265273.8128
84 | 2748347.5677 | 1265233.9164 | 2748348.5705 | 1265243.1842 | 2748354.9182 | 1265257.1242
85 | 2748236.2641 | 1265245.681 | 2748243.5757 | 1265244.0405 | 2748256.9714 | 1265241.04 | 2748276.6653 | 1265238.0531 | 2748303.2361 | 1265235.1388 | 2748330.6906 | 1265233.6372 | 2748347.5677 | 1265233.9164
86 | 2748321.9993 | 1265722.5099 | 2748336.1065 | 1265706.1363 | 2748338.2143 | 1265703.691
87 | 2748321.9993 | 1265722.5099 | 2748318.3231 | 1265719.2032
88 | 2748289.8061 | 1265689.0019 | 2748299.8021 | 1265701.3429 | 2748312.2224 | 1265713.7447 | 2748318.3231 | 1265719.2032
89 | 2748318.3231 | 1265719.2032 | 2748331.3196 | 1265704.4447
90 | 2748366.5922 | 1265671.4553 | 2748365.2006 | 1265665.9704
91 | 2748365.2006 | 1265665.9704 | 2748345.8575 | 1265687.9359
92 | 2748331.3196 | 1265704.4447 | 2748345.8575 | 1265687.9359
93 | 2748366.9165 | 1265281.2606 | 2748354.9182 | 1265257.1242
94 | 2748354.9182 | 1265257.1242 | 2748335.2973 | 1265267.1632
95 | 2748062.6425 | 1265295.7695 | 2748077.1035 | 1265292.0391 | 2748092.7148 | 1265288.4042 | 2748102.3766 | 1265285.877 | 2748119.3527 | 1265281.2977 | 2748125.7563 | 1265280.1125 | 2748140.0289 | 1265276.0883 | 2748171.8421 | 1265266.6093 | 2748195.6034 | 1265257.9518 | 2748210.4915 | 1265252.8198 | 2748236.2641 | 1265245.681
96 | 2748062.6425 | 1265295.7695 | 2748067.0134 | 1265311.5718
97 | 2748062.6425 | 1265295.7695 | 2748046.7226 | 1265299.9973 | 2748040.7081 | 1265301.5928 | 2748026.021 | 1265305.5007
98 | 2748018.7866 | 1265371.3373 | 2748017.4485 | 1265367.338
99 | 2748013.6378 | 1265355.9482 | 2748017.4485 | 1265367.338
100 | 2748366.9165 | 1265281.2606 | 2748377.5846 | 1265302.2001
101 | 2748366.9165 | 1265281.2606 | 2748356.8907 | 1265286.2371
102 | 2748316.1724 | 1265276.9485 | 2748335.2973 | 1265267.1632
103 | 2748067.0134 | 1265311.5718 | 2748068.2311 | 1265315.9742 | 2748071.8414 | 1265326.0306
104 | 2748014.7307 | 1265308.5048 | 2748026.021 | 1265305.5007
105 | 2748335.576 | 1265181.1633 | 2748365.5189 | 1265166.6959
106 | 2748466.9696 | 1265125.0933 | 2748386.6717 | 1265156.4756 | 2748365.5189 | 1265166.6959
107 | 2748409.3439 | 1265402.6331 | 2748429.0547 | 1265453.127
108 | 2748378.9072 | 1265304.7962 | 2748377.5846 | 1265302.2001
109 | 2748342.2039 | 1265293.5272 | 2748356.8907 | 1265286.2371
110 | 2748466.9696 | 1265125.0933 | 2748473.6339 | 1265138.3384
111 | 2748466.9696 | 1265125.0933 | 2748513.5953 | 1265101.9087
112 | 2748473.6339 | 1265138.3384 | 2748477.7842 | 1265146.5869
113 | 2748485.3242 | 1265161.5726 | 2748477.7842 | 1265146.5869
114 | 2748077.8649 | 1265342.809 | 2748071.8414 | 1265326.0306
115 | 2748014.7307 | 1265308.5048 | 2747999.4673 | 1265313.5945
116 | 2748487.7849 | 1265166.4633 | 2748485.3242 | 1265161.5726
117 | 2748489.8428 | 1265170.5532 | 2748487.7849 | 1265166.4633
118 | 2748444.8215 | 1265179.5766 | 2748444.8529 | 1265179.6387
119 | 2748540.0043 | 1265192.4001 | 2748545.3947 | 1265190.9848 | 2748559.2036 | 1265185.0092
120 | 2748559.3816 | 1265184.9321 | 2748559.2036 | 1265185.0092
121 | 2748561.5146 | 1265184.0091 | 2748559.3816 | 1265184.9321
122 | 2748436.6312 | 1265163.381 | 2748444.8215 | 1265179.5766
123 | 2748612.8408 | 1265193.9939 | 2748625.578 | 1265194.5557
124 | 2748643.552 | 1265196.3459 | 2748662.3659 | 1265198.4383
125 | 2748602.4306 | 1265275.6587 | 2748602.1301 | 1265274.7703
126 | 2748551.372 | 1265316.0939 | 2748551.7843 | 1265314.08 | 2748551.5114 | 1265312.0489 | 2748550.5779 | 1265310.2236 | 2748549.0916 | 1265308.8071
127 | 2748546.8235 | 1265319.9057 | 2748548.748 | 1265319.1755 | 2748550.3181 | 1265317.8581 | 2748551.372 | 1265316.0939
128 | 2748543.1839 | 1265308.247 | 2748545.1778 | 1265307.7522 | 2748547.2222 | 1265307.9482 | 2748549.0916 | 1265308.8071
129 | 2748543.1839 | 1265308.247 | 2748536.7605 | 1265287.3313
130 | 2748535.6263 | 1265283.6382 | 2748536.7605 | 1265287.3313
131 | 2748530.1642 | 1265335.4093 | 2748533.0915 | 1265334.4297
132 | 2748535.6263 | 1265283.6382 | 2748531.9834 | 1265271.776
133 | 2748530.1642 | 1265335.4093 | 2748508.2669 | 1265342.7366
134 | 2748496.0683 | 1265346.8186 | 2748508.2669 | 1265342.7366
135 | 2748496.0683 | 1265346.8186 | 2748483.6009 | 1265350.9905
136 | 2748425.0437 | 1265277.0738 | 2748432.8196 | 1265294.1029
137 | 2748457.3096 | 1265280.3262 | 2748453.3523 | 1265270.4799
138 | 2748457.3096 | 1265280.3262 | 2748462.2542 | 1265292.6291
139 | 2748465.1183 | 1265299.7554 | 2748462.2542 | 1265292.6291
140 | 2748432.8196 | 1265294.1029 | 2748445.5725 | 1265322.0314
141 | 2748444.2773 | 1265326.2031 | 2748445.5725 | 1265322.0314 | 2748445.5725 | 1265322.0314
142 | 2748444.2773 | 1265326.2031 | 2748444.2773 | 1265326.2031 | 2748437.7354 | 1265329.3595
143 | 2748437.7354 | 1265329.3595 | 2748431.765 | 1265332.2403
144 | 2748412.2056 | 1265341.6776 | 2748431.765 | 1265332.2403
145 | 2748399.6241 | 1265347.7482 | 2748412.2056 | 1265341.6776
146 | 2748399.6241 | 1265347.7482 | 2748398.9232 | 1265351.3564
147 | 2748399.6241 | 1265347.7482 | 2748390.0716 | 1265327.933
148 | 2748398.9232 | 1265351.3564 | 2748390.9976 | 1265355.4027
149 | 2748398.9232 | 1265351.3564 | 2748399.3981 | 1265360.3145
150 | 2748390.0716 | 1265327.933 | 2748386.5253 | 1265320.5838
151 | 2748390.0716 | 1265327.933 | 2748379.6376 | 1265333.1159
152 | 2748376.3892 | 1265362.8608 | 2748390.9976 | 1265355.4027
153 | 2748399.3981 | 1265360.3145 | 2748400.2313 | 1265376.0321
154 | 2748378.9072 | 1265304.7962 | 2748386.5253 | 1265320.5838
155 | 2748365.6376 | 1265340.0703 | 2748379.6376 | 1265333.1159
156 | 2748409.3439 | 1265402.6331 | 2748400.431 | 1265379.8006 | 2748400.2313 | 1265376.0321
157 | 2748362.131 | 1265370.1402 | 2748376.3892 | 1265362.8608
158 | 2748361.6385 | 1265370.3916 | 2748362.131 | 1265370.1402
159 | 2748505.0363 | 1265397.894 | 2748533.01 | 1265388.449
160 | 2748504.7003 | 1265398.0074 | 2748505.0363 | 1265397.894
161 | 2748493.3055 | 1265401.8547 | 2748504.7003 | 1265398.0074
162 | 2748378.9072 | 1265304.7962 | 2748368.3567 | 1265310.0328
163 | 2748327.9306 | 1265300.6121 | 2748342.2039 | 1265293.5272
164 | 2748353.9117 | 1265317.2022 | 2748368.3567 | 1265310.0328
165 | 2748339.5209 | 1265324.3448 | 2748353.9117 | 1265317.2022
166 | 2748350.9986 | 1265347.3421 | 2748365.6376 | 1265340.0703
167 | 2748004.5008 | 1265328.639 | 2748004.6776 | 1265329.1675
168 | 2748004.0615 | 1265327.3261 | 2748004.5008 | 1265328.639
169 | 2748004.6776 | 1265329.1675 | 2748004.7195 | 1265329.2927
170 | 2747999.4673 | 1265313.5945 | 2748004.0615 | 1265327.3261
171 | 2748006.3945 | 1265334.2989 | 2748004.7195 | 1265329.2927
172 | 2748006.3945 | 1265334.2989 | 2748006.5513 | 1265334.7678
173 | 2748006.5513 | 1265334.7678 | 2748006.6353 | 1265335.0186
174 | 2748006.6353 | 1265335.0186 | 2748008.0767 | 1265339.3267
175 | 2748009.2549 | 1265342.8484 | 2748008.0767 | 1265339.3267
176 | 2748009.2549 | 1265342.8484 | 2748010.9822 | 1265348.011
177 | 2748013.6378 | 1265355.9482 | 2748010.9822 | 1265348.011

## bus_geodata
| x | y | coords
0 | 2748676.6952 | 1265331.0036
1 | 2748734.066 | 1265262.233
2 | 2748577.1448 | 1265440.1328
3 | 2748720.7471 | 1265255.5913
4 | 2748588.2879 | 1265449.4
5 | 2748715.8432 | 1265253.1655
6 | 2748689.8443 | 1265296.5006
7 | 2748618.6511 | 1265238.251
8 | 2748589.7657 | 1265238.225
9 | 2748632.0503 | 1265225.5418
10 | 2748627.0922 | 1265261.4901
11 | 2748640.5312 | 1265224.9513
12 | 2748593.0104 | 1265226.7828
13 | 2748629.0106 | 1265210.3385
14 | 2748684.0384 | 1265247.3041
15 | 2748692.4186 | 1265259.9994
16 | 2748672.9253 | 1265247.3886
17 | 2748709.4591 | 1265218.2587
18 | 2748677.1632 | 1265221.7431
19 | 2748531.9919 | 1265238.2956
20 | 2748531.4703 | 1265226.3816
21 | 2748565.1573 | 1265238.2551
22 | 2748521.7001 | 1265238.3037
23 | 2748507.1856 | 1265227.0612
24 | 2748532.3162 | 1265226.4051
25 | 2748595.4674 | 1265255.0775
26 | 2748440.9892 | 1265238.4992
27 | 2748449.2139 | 1265260.183
28 | 2748499.5153 | 1265238.3574
29 | 2748502.0877 | 1265194.8897
30 | 2748495.1916 | 1265227.2655
31 | 2748602.33 | 1265396.4441
32 | 2748598.5032 | 1265382.3779
33 | 2748631.0053 | 1265363.9531
34 | 2748481.533 | 1265542.2779
35 | 2748476.6681 | 1265538.3072
36 | 2748474.0567 | 1265550.662
37 | 2748496.4431 | 1265495.5054
38 | 2748573.5514 | 1265416.4632
39 | 2748562.9609 | 1265378.3365
40 | 2748546.6422 | 1265439.1042
41 | 2748382.3156 | 1265228.8055
42 | 2748370.3375 | 1265233.8544
43 | 2748386.5233 | 1265212.6851
44 | 2748379.8213 | 1265253.961
45 | 2748352.9507 | 1265233.9018
46 | 2748670.5816 | 1265318.9354
47 | 2748637.3601 | 1265289.7582
48 | 2748658.458 | 1265223.5419
49 | 2748572.638 | 1265227.0646
50 | 2748628.6903 | 1265194.693
51 | 2748529.3462 | 1265263.1888
52 | 2748598.4559 | 1265263.9106
53 | 2748436.6623 | 1265266.0167
54 | 2748449.5963 | 1265261.1343
55 | 2748493.5284 | 1265177.8782
56 | 2748451.1638 | 1265191.0868
57 | 2748513.3724 | 1265194.6879
58 | 2748479.5983 | 1265227.5312
59 | 2748595.6568 | 1265371.9156
60 | 2748649.0056 | 1265343.5575
61 | 2748468.4471 | 1265556.9529
62 | 2748466.6049 | 1265549.3211
63 | 2748448.6608 | 1265503.3531
64 | 2748540.292 | 1265385.9904
65 | 2748549.5349 | 1265328.9273
66 | 2748537.3302 | 1265446.9392
67 | 2748451.9072 | 1265228.0007
68 | 2748396.0648 | 1265207.8407
69 | 2748384.6275 | 1265264.1505
70 | 2748347.5677 | 1265233.9164
71 | 2748338.2143 | 1265703.691
72 | 2748321.9993 | 1265722.5099
73 | 2748318.3231 | 1265719.2032
74 | 2748366.5922 | 1265671.4553
75 | 2748365.2006 | 1265665.9704
76 | 2748289.8061 | 1265689.0019
77 | 2748331.3196 | 1265704.4447
78 | 2748345.8575 | 1265687.9359
79 | 2748354.9182 | 1265257.1242
80 | 2748236.2641 | 1265245.681
81 | 2748062.6425 | 1265295.7695
82 | 2748018.7866 | 1265371.3373
83 | 2748017.4485 | 1265367.338
84 | 2748366.9165 | 1265281.2606
85 | 2748335.2973 | 1265267.1632
86 | 2748067.0134 | 1265311.5718
87 | 2748026.021 | 1265305.5007
88 | 2748335.576 | 1265181.1633
89 | 2748365.5189 | 1265166.6959
90 | 2748429.0547 | 1265453.127
91 | 2748377.5846 | 1265302.2001
92 | 2748356.8907 | 1265286.2371
93 | 2748316.1724 | 1265276.9485
94 | 2748389.185 | 1265273.8128
95 | 2748466.9696 | 1265125.0933
96 | 2748473.6339 | 1265138.3384
97 | 2748513.5953 | 1265101.9087
98 | 2748477.7842 | 1265146.5869
99 | 2748071.8414 | 1265326.0306
100 | 2748014.7307 | 1265308.5048
101 | 2748485.3242 | 1265161.5726
102 | 2748489.8428 | 1265170.5532
103 | 2748444.8529 | 1265179.6387
104 | 2748540.0043 | 1265192.4001
105 | 2748559.2036 | 1265185.0092
106 | 2748559.3816 | 1265184.9321
107 | 2748561.5146 | 1265184.0091
108 | 2748487.7849 | 1265166.4633
109 | 2748444.8215 | 1265179.5766
110 | 2748436.6312 | 1265163.381
111 | 2748625.578 | 1265194.5557
112 | 2748643.552 | 1265196.3459
113 | 2748612.8408 | 1265193.9939
114 | 2748662.3659 | 1265198.4383
115 | 2748639.0851 | 1265294.5073
116 | 2748602.1301 | 1265274.7703
117 | 2748602.4306 | 1265275.6587
118 | 2748591.9649 | 1265358.3453
119 | 2748551.372 | 1265316.0939
120 | 2748549.0916 | 1265308.8071
121 | 2748546.8235 | 1265319.9057
122 | 2748543.1839 | 1265308.247
123 | 2748536.7605 | 1265287.3313
124 | 2748533.0915 | 1265334.4297
125 | 2748535.6263 | 1265283.6382
126 | 2748530.1642 | 1265335.4093
127 | 2748531.9834 | 1265271.776
128 | 2748508.2669 | 1265342.7366
129 | 2748496.0683 | 1265346.8186
130 | 2748483.6009 | 1265350.9905
131 | 2748425.0437 | 1265277.0738
132 | 2748453.3523 | 1265270.4799
133 | 2748457.3096 | 1265280.3262
134 | 2748462.2542 | 1265292.6291
135 | 2748465.1183 | 1265299.7554
136 | 2748432.8196 | 1265294.1029
137 | 2748445.5725 | 1265322.0314
138 | 2748444.2773 | 1265326.2031
139 | 2748437.7354 | 1265329.3595
140 | 2748431.765 | 1265332.2403
141 | 2748412.2056 | 1265341.6776
142 | 2748399.6241 | 1265347.7482
143 | 2748398.9232 | 1265351.3564
144 | 2748390.0716 | 1265327.933
145 | 2748390.9976 | 1265355.4027
146 | 2748399.3981 | 1265360.3145
147 | 2748386.5253 | 1265320.5838
148 | 2748379.6376 | 1265333.1159
149 | 2748400.2313 | 1265376.0321
150 | 2748409.3439 | 1265402.6331
151 | 2748376.3892 | 1265362.8608
152 | 2748362.131 | 1265370.1402
153 | 2748533.01 | 1265388.449
154 | 2748505.0363 | 1265397.894
155 | 2748504.7003 | 1265398.0074
156 | 2748493.3055 | 1265401.8547
157 | 2748378.9072 | 1265304.7962
158 | 2748342.2039 | 1265293.5272
159 | 2748327.9306 | 1265300.6121
160 | 2748368.3567 | 1265310.0328
161 | 2748339.5209 | 1265324.3448
162 | 2748353.9117 | 1265317.2022
163 | 2748350.9986 | 1265347.3421
164 | 2748365.6376 | 1265340.0703
165 | 2748361.6385 | 1265370.3916
166 | 2748004.5008 | 1265328.639
167 | 2748004.6776 | 1265329.1675
168 | 2748004.0615 | 1265327.3261
169 | 2748004.7195 | 1265329.2927
170 | 2747999.4673 | 1265313.5945
171 | 2748006.3945 | 1265334.2989
172 | 2748006.5513 | 1265334.7678
173 | 2748006.6353 | 1265335.0186
174 | 2748008.0767 | 1265339.3267
175 | 2748009.2549 | 1265342.8484
176 | 2748010.9822 | 1265348.011
177 | 2748013.6378 | 1265355.9482
178 | 2748077.8649 | 1265342.809
179 | 2748399.6241 | 1265347.7482

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1