## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_4401-27_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_4401-27_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_4401-27_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_4401-27_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_4401-27_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_4401-27_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_4401-27_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_4401-27_0_4_node_9 | 0.4 | n |  | TRUE
8 | bus_LV_4401-27_0_4_node_73 | 0.4 | n |  | TRUE
9 | bus_LV_4401-27_0_4_node_71 | 0.4 | n |  | TRUE
10 | bus_LV_4401-27_0_4_node_67 | 0.4 | n |  | TRUE
11 | bus_LV_4401-27_0_4_node_66 | 0.4 | n |  | TRUE
12 | bus_LV_4401-27_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_4401-27_0_4_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_4401-27_0_4_node_76 | 0.4 | n |  | TRUE
15 | bus_LV_4401-27_0_4_node_68 | 0.4 | n |  | TRUE
16 | bus_LV_4401-27_0_4_node_65 | 0.4 | n |  | TRUE
17 | bus_LV_4401-27_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_4401-27_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_4401-27_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_4401-27_0_4_node_75 | 0.4 | n |  | TRUE
21 | bus_LV_4401-27_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_4401-27_0_4_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_4401-27_0_4_node_74 | 0.4 | n |  | TRUE
24 | bus_LV_4401-27_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_4401-27_0_4_node_78 | 0.4 | n |  | TRUE
26 | bus_LV_4401-27_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_4401-27_0_4_node_79 | 0.4 | n |  | TRUE
28 | bus_LV_4401-27_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_4401-27_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_4401-27_0_4_node_83 | 0.4 | n |  | TRUE
31 | bus_LV_4401-27_0_4_node_80 | 0.4 | n |  | TRUE
32 | bus_LV_4401-27_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_4401-27_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_4401-27_0_4_node_84 | 0.4 | n |  | TRUE
35 | bus_LV_4401-27_0_4_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_4401-27_0_4_node_20 | 0.4 | n |  | TRUE
37 | bus_LV_4401-27_0_4_node_21 | 0.4 | n |  | TRUE
38 | bus_LV_4401-27_0_4_node_45 | 0.4 | n |  | TRUE
39 | bus_LV_4401-27_0_4_node_52 | 0.4 | n |  | TRUE
40 | bus_LV_4401-27_0_4_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_4401-27_0_4_node_23 | 0.4 | n |  | TRUE
42 | bus_LV_4401-27_0_4_node_24 | 0.4 | n |  | TRUE
43 | bus_LV_4401-27_0_4_node_26 | 0.4 | n |  | TRUE
44 | bus_LV_4401-27_0_4_node_56 | 0.4 | n |  | TRUE
45 | bus_LV_4401-27_0_4_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_4401-27_0_4_node_53 | 0.4 | n |  | TRUE
47 | bus_LV_4401-27_0_4_node_54 | 0.4 | n |  | TRUE
48 | bus_LV_4401-27_0_4_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_4401-27_0_4_node_29 | 0.4 | n |  | TRUE
50 | bus_LV_4401-27_0_4_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_4401-27_0_4_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_4401-27_0_4_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_4401-27_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_4401-27_0_4_node_108 | 0.4 | n |  | TRUE
55 | bus_LV_4401-27_0_4_node_109 | 0.4 | n |  | TRUE
56 | bus_LV_4401-27_0_4_node_35 | 0.4 | n |  | TRUE
57 | bus_LV_4401-27_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_4401-27_0_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_4401-27_0_4_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_4401-27_0_4_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_4401-27_0_4_node_36 | 0.4 | n |  | TRUE
62 | bus_LV_4401-27_0_4_node_37 | 0.4 | n |  | TRUE
63 | bus_LV_4401-27_0_4_node_39 | 0.4 | n |  | TRUE
64 | bus_LV_4401-27_0_4_node_41 | 0.4 | n |  | TRUE
65 | bus_LV_4401-27_0_4_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_4401-27_0_4_node_111 | 0.4 | n |  | TRUE
67 | bus_LV_4401-27_0_4_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_4401-27_0_4_node_46 | 0.4 | n |  | TRUE
69 | bus_LV_4401-27_0_4_node_112 | 0.4 | n |  | TRUE
70 | bus_LV_4401-27_0_4_node_51 | 0.4 | n |  | TRUE
71 | bus_LV_4401-27_0_4_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_4401-27_0_4_node_58 | 0.4 | n |  | TRUE
73 | bus_LV_4401-27_0_4_node_47 | 0.4 | n |  | TRUE
74 | bus_LV_4401-27_0_4_node_49 | 0.4 | n |  | TRUE
75 | bus_LV_4401-27_0_4_node_115 | 0.4 | n |  | TRUE
76 | bus_LV_4401-27_0_4_node_116 | 0.4 | n |  | TRUE
77 | bus_LV_4401-27_0_4_node_59 | 0.4 | n |  | TRUE
78 | bus_LV_4401-27_0_4_node_60 | 0.4 | n |  | TRUE
79 | bus_LV_4401-27_0_4_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_4401-27_0_4_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_4401-27_0_4_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_4401-27_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_4401-27_0_4_node_69 | 0.4 | n |  | TRUE
84 | bus_LV_4401-27_0_4_node_119 | 0.4 | n |  | TRUE
85 | bus_LV_4401-27_0_4_node_77 | 0.4 | n |  | TRUE
86 | bus_LV_4401-27_0_4_node_90 | 0.4 | n |  | TRUE
87 | bus_LV_4401-27_0_4_node_91 | 0.4 | n |  | TRUE
88 | bus_LV_4401-27_0_4_node_81 | 0.4 | n |  | TRUE
89 | bus_LV_4401-27_0_4_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_4401-27_0_4_node_93 | 0.4 | n |  | TRUE
91 | bus_LV_4401-27_0_4_node_94 | 0.4 | n |  | TRUE
92 | bus_LV_4401-27_0_4_node_97 | 0.4 | n |  | TRUE
93 | bus_LV_4401-27_0_4_node_106 | 0.4 | n |  | TRUE
94 | bus_LV_4401-27_0_4_node_85 | 0.4 | n |  | TRUE
95 | bus_LV_4401-27_0_4_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_4401-27_0_4_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_4401-27_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_4401-27_0_4_node_92 | 0.4 | n |  | TRUE
99 | bus_LV_4401-27_0_4_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_4401-27_0_4_node_117 | 0.4 | n |  | TRUE
101 | bus_LV_4401-27_0_4_node_105 | 0.4 | n |  | TRUE
102 | bus_LV_4401-27_0_4_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_4401-27_0_4_node_100 | 0.4 | n |  | TRUE
104 | bus_LV_4401-27_0_4_node_107 | 0.4 | n |  | TRUE
105 | bus_LV_4401-27_0_4_node_101 | 0.4 | n |  | TRUE
106 | bus_LV_4401-27_0_4_node_102 | 0.4 | n |  | TRUE
107 | bus_LV_4401-27_0_4_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_4401-27_0_4_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_4401-27_0_4_node_110 | 0.4 | n |  | TRUE
110 | bus_LV_4401-27_0_4_node_120 | 0.4 | n |  | TRUE
111 | bus_LV_4401-27_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_4401-27_0_4_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_4401-27_0_4_node_118 | 0.4 | n |  | TRUE
114 | bus_LV_4401-27_0_4_node_121 | 0.4 | n |  | TRUE
115 | bus_MV_48_0_node_167 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_4401-27_0_4_load_0 | 0 | 0.0014203 | 0.00035595 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_4401-27_0_4_load_1 | 1 | 0.0014439 | 0.00036188 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_4401-27_0_4_load_3 | 3 | 0.00092299 | 0.00023132 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_4401-27_0_4_load_6 | 6 | 0.0010238 | 0.00025658 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_4401-27_0_4_load_73 | 8 | 0.0013918 | 0.00034881 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_4401-27_0_4_load_71 | 9 | 0.0016049 | 0.00040223 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_4401-27_0_4_load_67 | 10 | 0.00076928 | 0.0001928 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_4401-27_0_4_load_66 | 11 | 0.00024943 | 6.2512e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_4401-27_0_4_load_11 | 12 | 0.0011892 | 0.00029805 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_4401-27_0_4_load_7 | 13 | 0.0012964 | 0.00032491 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_4401-27_0_4_load_76 | 14 | 0.0023063 | 0.00057801 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_4401-27_0_4_load_65 | 16 | 0.00029164 | 7.3093e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_4401-27_0_4_load_8 | 17 | 0.00075209 | 0.00018849 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_4401-27_0_4_load_10 | 18 | 0.0015986 | 0.00040065 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_4401-27_0_4_load_75 | 20 | 0.0013545 | 0.00033946 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_4401-27_0_4_load_13 | 21 | 0.0014797 | 0.00037084 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_4401-27_0_4_load_14 | 22 | 0.0014724 | 0.00036903 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_4401-27_0_4_load_74 | 23 | 0.0020392 | 0.00051108 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_4401-27_0_4_load_15 | 24 | 0.0033278 | 0.00083401 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_4401-27_0_4_load_78 | 25 | 0.0073412 | 0.0018399 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_4401-27_0_4_load_79 | 27 | 0.0017851 | 0.00044739 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_4401-27_0_4_load_83 | 30 | 0.0035514 | 0.00089005 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_4401-27_0_4_load_80 | 31 | 0.0044212 | 0.0011081 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_4401-27_0_4_load_22 | 32 | 0.0036455 | 0.00091364 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_4401-27_0_4_load_19 | 33 | 0.0059761 | 0.0014977 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_4401-27_0_4_load_84 | 34 | 0.003877 | 0.00097168 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_4401-27_0_4_load_20 | 36 | 0.00624 | 0.0015639 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_4401-27_0_4_load_21 | 37 | 0.048902 | 0.012256 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_4401-27_0_4_load_27 | 40 | 0.003608 | 0.00090424 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_4401-27_0_4_load_23 | 41 | 0.0064238 | 0.0016099 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_4401-27_0_4_load_24 | 42 | 0.0064295 | 0.0016114 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_4401-27_0_4_load_26 | 43 | 0.0042298 | 0.0010601 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_4401-27_0_4_load_56 | 44 | 0.0063872 | 0.0016008 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_4401-27_0_4_load_55 | 45 | 0.0040534 | 0.0010159 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_4401-27_0_4_load_53 | 46 | 0.0054109 | 0.0013561 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_4401-27_0_4_load_54 | 47 | 0.016052 | 0.004023 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_4401-27_0_4_load_28 | 48 | 0.0029993 | 0.00075169 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_4401-27_0_4_load_30 | 50 | 0.0025501 | 0.00063911 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_4401-27_0_4_load_34 | 52 | 0.0023783 | 0.00059606 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_4401-27_0_4_load_40 | 53 | 0.002649 | 0.00066389 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_4401-27_0_4_load_108 | 54 | 0.0028094 | 0.0007041 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_4401-27_0_4_load_44 | 57 | 0.0031129 | 0.00078016 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_4401-27_0_4_load_43 | 58 | 0.0052598 | 0.0013182 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_4401-27_0_4_load_42 | 60 | 0.0039369 | 0.00098668 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_4401-27_0_4_load_36 | 61 | 0.0030261 | 0.00075842 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_4401-27_0_4_load_37 | 62 | 0.0061158 | 0.0015328 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_4401-27_0_4_load_39 | 63 | 0.0015192 | 0.00038074 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_4401-27_0_4_load_111 | 66 | 0.0020997 | 0.00052623 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_4401-27_0_4_load_50 | 67 | 0.0021428 | 0.00053704 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_4401-27_0_4_load_46 | 68 | 0.0062945 | 0.0015775 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_4401-27_0_4_load_112 | 69 | 0.0024514 | 0.00061437 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_4401-27_0_4_load_51 | 70 | 0.020989 | 0.0052603 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_4401-27_0_4_load_57 | 71 | 0.0031761 | 0.000796 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_4401-27_0_4_load_58 | 72 | 0.0015538 | 0.00038942 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_4401-27_0_4_load_47 | 73 | 0.0020357 | 0.00051021 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_4401-27_0_4_load_49 | 74 | 0.0057849 | 0.0014498 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_4401-27_0_4_load_115 | 75 | 0.0013927 | 0.00034904 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_4401-27_0_4_load_116 | 76 | 0.0020506 | 0.00051392 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_4401-27_0_4_load_59 | 77 | 0.0017594 | 0.00044095 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_4401-27_0_4_load_61 | 79 | 0.00021987 | 5.5104e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_4401-27_0_4_load_63 | 80 | 0.00035795 | 8.971e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_4401-27_0_4_load_64 | 81 | 0.00026568 | 6.6585e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_4401-27_0_4_load_72 | 82 | 0.0021512 | 0.00053914 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_4401-27_0_4_load_69 | 83 | 0.003319 | 0.00083183 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_4401-27_0_4_load_119 | 84 | 0.00254 | 0.00063659 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_4401-27_0_4_load_77 | 85 | 0.0020047 | 0.00050242 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_4401-27_0_4_load_90 | 86 | 0.0016585 | 0.00041565 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_4401-27_0_4_load_91 | 87 | 0.0070591 | 0.0017692 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_4401-27_0_4_load_81 | 88 | 0.017185 | 0.004307 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_4401-27_0_4_load_93 | 90 | 0.0049577 | 0.0012425 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_4401-27_0_4_load_94 | 91 | 0.0021881 | 0.00054839 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_4401-27_0_4_load_97 | 92 | 0.0028263 | 0.00070833 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_4401-27_0_4_load_85 | 94 | 0.0043367 | 0.0010869 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_4401-27_0_4_load_86 | 95 | 0.002733 | 0.00068495 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_4401-27_0_4_load_87 | 96 | 0.0044949 | 0.0011265 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_4401-27_0_4_load_88 | 97 | 0.0027327 | 0.00068487 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_4401-27_0_4_load_92 | 98 | 0.0035204 | 0.0008823 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_4401-27_0_4_load_95 | 99 | 0.015876 | 0.0039788 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_4401-27_0_4_load_117 | 100 | 0.0017379 | 0.00043555 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_4401-27_0_4_load_96 | 102 | 0.0044703 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_4401-27_0_4_load_100 | 103 | 0.0040213 | 0.0010078 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_4401-27_0_4_load_107 | 104 | 0.0017282 | 0.00043312 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_4401-27_0_4_load_101 | 105 | 0.0028303 | 0.00070935 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_4401-27_0_4_load_103 | 107 | 0.0015473 | 0.00038779 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_4401-27_0_4_load_104 | 108 | 0.0012735 | 0.00031917 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_4401-27_0_4_load_110 | 109 | 0.0033085 | 0.00082918 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_4401-27_0_4_load_120 | 110 | 0.0065767 | 0.0016483 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_4401-27_0_4_load_113 | 111 | 0.0033339 | 0.00083555 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_4401-27_0_4_load_114 | 112 | 0.0014301 | 0.00035843 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_4401-27_0_4_load_118 | 113 | 0.0011561 | 0.00028975 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_4401-27_0_4_load_121 | 114 | 0.0058192 | 0.0014584 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 35 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_4401-27_0_4_line_0 |  | 0 | 1 | 0.00067547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_4401-27_0_4_line_1 |  | 0 | 2 | 0.014123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_4401-27_0_4_line_2 |  | 1 | 3 | 0.011518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_4401-27_0_4_line_3 |  | 2 | 4 | 0.004755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_4401-27_0_4_line_4 |  | 2 | 5 | 0.01488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_4401-27_0_4_line_5 |  | 3 | 6 | 0.014122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_4401-27_0_4_line_6 |  | 4 | 7 | 0.013214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_4401-27_0_4_line_7 |  | 4 | 8 | 0.012182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_4401-27_0_4_line_8 |  | 5 | 9 | 0.026903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_4401-27_0_4_line_9 |  | 5 | 10 | 0.011948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_4401-27_0_4_line_10 |  | 6 | 11 | 0.0017754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_4401-27_0_4_line_11 |  | 7 | 12 | 0.011368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_4401-27_0_4_line_12 |  | 7 | 13 | 0.013089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_4401-27_0_4_line_13 |  | 9 | 14 | 0.018087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_4401-27_0_4_line_14 |  | 10 | 15 | 0.037468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_4401-27_0_4_line_15 |  | 11 | 16 | 0.00064363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_4401-27_0_4_line_16 |  | 12 | 20 | 0.00079378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_4401-27_0_4_line_17 |  | 13 | 17 | 0.014937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_4401-27_0_4_line_18 |  | 14 | 85 | 0.016265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_4401-27_0_4_line_19 |  | 15 | 83 | 0.059825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_4401-27_0_4_line_20 |  | 16 | 81 | 0.026448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_4401-27_0_4_line_21 |  | 17 | 18 | 0.0031295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_4401-27_0_4_line_22 |  | 18 | 19 | 0.0041821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_4401-27_0_4_line_23 |  | 19 | 21 | 0.015128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_4401-27_0_4_line_24 |  | 19 | 22 | 0.013549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_4401-27_0_4_line_25 |  | 20 | 23 | 0.0074854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_4401-27_0_4_line_26 |  | 21 | 24 | 0.020168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_4401-27_0_4_line_27 |  | 22 | 25 | 0.0081016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_4401-27_0_4_line_28 |  | 24 | 26 | 0.019742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_4401-27_0_4_line_29 |  | 25 | 27 | 0.024782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_4401-27_0_4_line_30 |  | 26 | 28 | 0.006477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_4401-27_0_4_line_31 |  | 26 | 29 | 0.006916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_4401-27_0_4_line_32 |  | 27 | 86 | 0.014746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_4401-27_0_4_line_33 |  | 28 | 30 | 0.018913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_4401-27_0_4_line_34 |  | 28 | 31 | 0.012193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_4401-27_0_4_line_35 |  | 29 | 32 | 0.024215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_4401-27_0_4_line_36 |  | 29 | 33 | 0.014247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_4401-27_0_4_line_37 |  | 30 | 34 | 0.010139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_4401-27_0_4_line_38 |  | 32 | 35 | 0.0034074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_4401-27_0_4_line_39 |  | 33 | 36 | 0.017645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_4401-27_0_4_line_40 |  | 34 | 94 | 0.018391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_4401-27_0_4_line_41 |  | 35 | 40 | 0.01097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_4401-27_0_4_line_42 |  | 35 | 41 | 0.010719 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_4401-27_0_4_line_43 |  | 37 | 38 | 0.032581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_4401-27_0_4_line_44 |  | 38 | 39 | 0.020067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_4401-27_0_4_line_45 |  | 39 | 46 | 0.013705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_4401-27_0_4_line_46 |  | 39 | 70 | 0.016652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_4401-27_0_4_line_47 |  | 40 | 45 | 0.015923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
48 | LV_4401-27_0_4_line_48 |  | 41 | 42 | 0.019443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_4401-27_0_4_line_49 |  | 42 | 43 | 0.0076916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_4401-27_0_4_line_50 |  | 43 | 44 | 0.018861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_4401-27_0_4_line_51 |  | 44 | 46 | 0.020242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_4401-27_0_4_line_52 |  | 45 | 47 | 0.0037791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
53 | LV_4401-27_0_4_line_53 |  | 47 | 74 | 0.016556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_4401-27_0_4_line_54 |  | 48 | 49 | 0.0010222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_4401-27_0_4_line_55 |  | 49 | 50 | 0.02141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_4401-27_0_4_line_56 |  | 49 | 51 | 0.023927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_4401-27_0_4_line_57 |  | 50 | 52 | 0.020714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_4401-27_0_4_line_58 |  | 51 | 53 | 0.0099531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_4401-27_0_4_line_59 |  | 53 | 59 | 0.037847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_4401-27_0_4_line_60 |  | 54 | 55 | 0.044161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_4401-27_0_4_line_61 |  | 55 | 109 | 0.026875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_4401-27_0_4_line_62 |  | 56 | 57 | 0.039449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_4401-27_0_4_line_63 |  | 56 | 58 | 0.016604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_4401-27_0_4_line_64 |  | 58 | 60 | 0.0010039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_4401-27_0_4_line_65 |  | 59 | 64 | 0.004204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_4401-27_0_4_line_66 |  | 59 | 61 | 0.013886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_4401-27_0_4_line_67 |  | 60 | 63 | 0.019074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_4401-27_0_4_line_68 |  | 61 | 62 | 0.0069962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_4401-27_0_4_line_69 |  | 62 | 63 | 0.009596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_4401-27_0_4_line_70 |  | 64 | 65 | 0.024185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_4401-27_0_4_line_71 |  | 64 | 66 | 0.013558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_4401-27_0_4_line_72 |  | 65 | 67 | 0.031385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_4401-27_0_4_line_73 |  | 65 | 68 | 0.013691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_4401-27_0_4_line_74 |  | 66 | 69 | 0.00021354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_4401-27_0_4_line_75 |  | 67 | 75 | 0.002288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_4401-27_0_4_line_76 |  | 68 | 73 | 0.010906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_4401-27_0_4_line_77 |  | 69 | 111 | 0.019126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_4401-27_0_4_line_78 |  | 71 | 72 | 0.023055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_4401-27_0_4_line_79 |  | 72 | 77 | 0.017199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_4401-27_0_4_line_80 |  | 73 | 74 | 0.014741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_4401-27_0_4_line_81 |  | 75 | 76 | 0.020494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_4401-27_0_4_line_82 |  | 76 | 100 | 0.0016089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_4401-27_0_4_line_83 |  | 77 | 78 | 0.025527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_4401-27_0_4_line_84 |  | 78 | 79 | 0.028899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_4401-27_0_4_line_85 |  | 79 | 80 | 1.1097e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_4401-27_0_4_line_86 |  | 80 | 81 | 0.00072126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_4401-27_0_4_line_87 |  | 82 | 83 | 0.023229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_4401-27_0_4_line_88 |  | 84 | 85 | 0.0073198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_4401-27_0_4_line_89 |  | 86 | 87 | 0.018921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_4401-27_0_4_line_90 |  | 87 | 98 | 0.010142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_4401-27_0_4_line_91 |  | 88 | 89 | 0.029382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_4401-27_0_4_line_92 |  | 89 | 90 | 0.018265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_4401-27_0_4_line_93 |  | 89 | 91 | 0.011809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_4401-27_0_4_line_94 |  | 90 | 92 | 0.030185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_4401-27_0_4_line_95 |  | 91 | 93 | 0.014128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_4401-27_0_4_line_96 |  | 92 | 99 | 0.01048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_4401-27_0_4_line_97 |  | 93 | 100 | 0.014126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_4401-27_0_4_line_98 |  | 93 | 101 | 0.014407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_4401-27_0_4_line_99 |  | 94 | 95 | 0.015738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_4401-27_0_4_line_100 |  | 95 | 96 | 0.0032218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_4401-27_0_4_line_101 |  | 96 | 97 | 0.016461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_4401-27_0_4_line_102 |  | 99 | 102 | 0.0081571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_4401-27_0_4_line_103 |  | 101 | 104 | 0.01125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_4401-27_0_4_line_104 |  | 101 | 103 | 0.032277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_4401-27_0_4_line_105 |  | 104 | 110 | 0.019499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_4401-27_0_4_line_106 |  | 105 | 106 | 0.011367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_4401-27_0_4_line_107 |  | 106 | 107 | 0.0015513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_4401-27_0_4_line_108 |  | 106 | 108 | 0.0072185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_4401-27_0_4_line_109 |  | 107 | 109 | 0.015295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_4401-27_0_4_line_110 |  | 108 | 110 | 0.017029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_4401-27_0_4_line_111 |  | 111 | 112 | 0.0050469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_4401-27_0_4_line_112 |  | 112 | 113 | 0.0059846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_4401-27_0_4_line_113 |  | 113 | 114 | 0.00047856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_4401-27_0_4_trafo_25 | 0.63 MVA 20/0.4 kV | 115 | 35 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2749874.1101 | 1264718.9331 | 2749874.109 | 1264718.2576
1 | 2749874.1326 | 1264733.0559 | 2749874.1101 | 1264718.9331
2 | 2749874.109 | 1264718.2576 | 2749874.0907 | 1264706.7398
3 | 2749874.1326 | 1264733.0559 | 2749869.3689 | 1264732.8238
4 | 2749874.1326 | 1264733.0559 | 2749889.0277 | 1264734.0011
5 | 2749874.0682 | 1264692.6178 | 2749874.0907 | 1264706.7398
6 | 2749856.1317 | 1264732.1654 | 2749869.3689 | 1264732.8238
7 | 2749869.3689 | 1264732.8238 | 2749869.4398 | 1264745.0052
8 | 2749889.0277 | 1264734.0011 | 2749888.6034 | 1264740.33 | 2749889.1443 | 1264745.4378 | 2749893.883 | 1264760.1157
9 | 2749889.0277 | 1264734.0011 | 2749900.9556 | 1264734.6884
10 | 2749874.0682 | 1264692.6178 | 2749874.0654 | 1264690.8425
11 | 2749856.1317 | 1264732.1654 | 2749856.2313 | 1264743.533
12 | 2749856.1317 | 1264732.1654 | 2749843.0585 | 1264731.5166
13 | 2749893.883 | 1264760.1157 | 2749899.4399 | 1264777.3276
14 | 2749938.3619 | 1264736.8437 | 2749900.9556 | 1264734.6884
15 | 2749874.0654 | 1264690.8425 | 2749874.0644 | 1264690.1988
16 | 2749856.2313 | 1264743.533 | 2749856.2382 | 1264744.3267
17 | 2749843.0585 | 1264731.5166 | 2749828.14 | 1264730.7762
18 | 2749904.4371 | 1264792.8062 | 2749899.4399 | 1264777.3276
19 | 2749938.3619 | 1264736.8437 | 2749935.6846 | 1264677.0789
20 | 2749874.0644 | 1264690.1988 | 2749874.0223 | 1264663.7513
21 | 2749825.0143 | 1264730.621 | 2749828.14 | 1264730.7762
22 | 2749820.8374 | 1264730.4137 | 2749825.0143 | 1264730.621
23 | 2749820.8374 | 1264730.4137 | 2749805.7261 | 1264729.7144
24 | 2749820.8374 | 1264730.4137 | 2749820.6226 | 1264737.9937 | 2749821.2696 | 1264743.9249
25 | 2749856.2382 | 1264744.3267 | 2749856.3038 | 1264751.8118 | 2749856.3038 | 1264751.8118
26 | 2749805.7261 | 1264729.7144 | 2749785.5792 | 1264728.782
27 | 2749821.2696 | 1264743.9249 | 2749822.1265 | 1264751.779 | 2749822.1768 | 1264751.9735
28 | 2749766.1446 | 1264729.4049 | 2749769.2688 | 1264728.0271 | 2749785.5792 | 1264728.782
29 | 2749829.2415 | 1264775.7012 | 2749825.9416 | 1264766.535 | 2749822.1768 | 1264751.9735
30 | 2749766.1446 | 1264729.4049 | 2749766.2441 | 1264735.8806
31 | 2749766.1446 | 1264729.4049 | 2749763.3637 | 1264727.3435 | 2749760.269 | 1264725.7747
32 | 2749834.2362 | 1264789.5752 | 2749829.2415 | 1264775.7012
33 | 2749766.2441 | 1264735.8806 | 2749772.6727 | 1264753.6679
34 | 2749766.2441 | 1264735.8806 | 2749759.4651 | 1264736.9767 | 2749754.1972 | 1264737.7589
35 | 2749760.269 | 1264725.7747 | 2749739.2031 | 1264713.8327
36 | 2749760.269 | 1264725.7747 | 2749761.4266 | 1264723.802 | 2749761.9726 | 1264720.9908 | 2749761.798 | 1264711.8967
37 | 2749776.1189 | 1264763.2033 | 2749772.6727 | 1264753.6679
38 | 2749736.2389 | 1264712.1524 | 2749739.2031 | 1264713.8327
39 | 2749761.4592 | 1264694.255 | 2749761.798 | 1264711.8967
40 | 2749776.1189 | 1264763.2033 | 2749782.3698 | 1264780.4989
41 | 2749736.2389 | 1264712.1524 | 2749726.8801 | 1264707.4106 | 2749726.4685 | 1264707.1668
42 | 2749736.2389 | 1264712.1524 | 2749738.0275 | 1264708.772 | 2749738.1884 | 1264701.8788
43 | 2749760.1069 | 1264623.69 | 2749760.297 | 1264633.7271 | 2749760.7297 | 1264656.2653
44 | 2749760.1069 | 1264623.69 | 2749740.0548 | 1264621.9582
45 | 2749740.0548 | 1264621.9582 | 2749739.7349 | 1264635.6594
46 | 2749740.0548 | 1264621.9582 | 2749723.4798 | 1264620.3595
47 | 2749712.7683 | 1264699.0523 | 2749726.4685 | 1264707.1668
48 | 2749738.6424 | 1264682.4407 | 2749738.1884 | 1264701.8788
49 | 2749738.6424 | 1264682.4407 | 2749738.822 | 1264674.7512
50 | 2749738.822 | 1264674.7512 | 2749739.2623 | 1264655.8957
51 | 2749739.2623 | 1264655.8957 | 2749739.7349 | 1264635.6594
52 | 2749709.5168 | 1264697.1265 | 2749712.7683 | 1264699.0523
53 | 2749694.7911 | 1264689.7505 | 2749699.8661 | 1264691.4105 | 2749709.5168 | 1264697.1265
54 | 2749581.8219 | 1264661.7265 | 2749581.7215 | 1264662.7438
55 | 2749581.8219 | 1264661.7265 | 2749582.5935 | 1264658.6318 | 2749583.3926 | 1264654.7481 | 2749584.8191 | 1264640.5645
56 | 2749580.3819 | 1264675.1481 | 2749580.2343 | 1264673.2424 | 2749579.4728 | 1264671.4769 | 2749578.1904 | 1264670.043 | 2749576.5265 | 1264669.1 | 2749574.6368 | 1264668.7407 | 2749574.9765 | 1264661.2751 | 2749581.8219 | 1264661.7265
57 | 2749584.3575 | 1264619.9436 | 2749583.9318 | 1264624.2311 | 2749584.0034 | 1264628.248 | 2749584.9014 | 1264634.4436 | 2749584.9536 | 1264639.2276 | 2749584.8191 | 1264640.5645
58 | 2749580.3819 | 1264675.1481 | 2749587.9321 | 1264675.7397 | 2749590.306 | 1264675.907
59 | 2749628.0594 | 1264678.5689 | 2749590.306 | 1264675.907
60 | 2749576.896 | 1264799.4183 | 2749576.1622 | 1264755.2638
61 | 2749576.896 | 1264799.4183 | 2749582.7198 | 1264797.9531 | 2749587.8157 | 1264796.6696 | 2749599.6226 | 1264795.189 | 2749603.2365 | 1264794.3256
62 | 2749637.2945 | 1264612.0468 | 2749676.5617 | 1264615.8341
63 | 2749637.2945 | 1264612.0468 | 2749635.0113 | 1264628.4933
64 | 2749635.0113 | 1264628.4933 | 2749634.8733 | 1264629.4876
65 | 2749632.2527 | 1264679.0088 | 2749628.0594 | 1264678.5689
66 | 2749628.0594 | 1264678.5689 | 2749629.9688 | 1264664.8153
67 | 2749632.2504 | 1264648.3807 | 2749634.8733 | 1264629.4876
68 | 2749629.9688 | 1264664.8153 | 2749630.9308 | 1264657.8855
69 | 2749632.2504 | 1264648.3807 | 2749630.9308 | 1264657.8855
70 | 2749632.2527 | 1264679.0088 | 2749656.3751 | 1264681.5663
71 | 2749632.2527 | 1264679.0088 | 2749633.263 | 1264689.1001 | 2749633.4039 | 1264692.5137
72 | 2749656.3751 | 1264681.5663 | 2749656.0547 | 1264687.0749 | 2749659.2028 | 1264707.9533 | 2749659.9012 | 1264712.6545
73 | 2749656.3751 | 1264681.5663 | 2749669.8895 | 1264683.7577
74 | 2749633.4128 | 1264692.7271 | 2749633.4039 | 1264692.5137
75 | 2749659.9012 | 1264712.6545 | 2749660.2374 | 1264714.9176
76 | 2749669.8895 | 1264683.7577 | 2749676.8614 | 1264684.8882 | 2749680.5832 | 1264685.8442
77 | 2749633.4128 | 1264692.7271 | 2749633.6786 | 1264699.1652 | 2749632.0693 | 1264704.3964 | 2749627.2115 | 1264709.0671 | 2749626.7455 | 1264709.1286
78 | 2749808.469 | 1264628.124 | 2749831.4274 | 1264630.229
79 | 2749831.4274 | 1264630.229 | 2749848.5545 | 1264631.7993
80 | 2749694.7911 | 1264689.7505 | 2749691.1301 | 1264688.5531 | 2749680.5832 | 1264685.8442
81 | 2749663.1904 | 1264735.1975 | 2749662.8333 | 1264732.3921 | 2749660.2374 | 1264714.9176
82 | 2749663.1904 | 1264735.1975 | 2749663.3936 | 1264736.7936
83 | 2749873.9752 | 1264634.13 | 2749848.5545 | 1264631.7993
84 | 2749873.9752 | 1264634.13 | 2749874.0211 | 1264663.0289
85 | 2749874.0211 | 1264663.03 | 2749874.0211 | 1264663.0289
86 | 2749874.0223 | 1264663.7513 | 2749874.0211 | 1264663.03
87 | 2749934.645 | 1264653.873 | 2749935.6846 | 1264677.0789
88 | 2749906.6859 | 1264799.772 | 2749904.4371 | 1264792.8062
89 | 2749834.2362 | 1264789.5752 | 2749840.6454 | 1264807.378
90 | 2749844.0806 | 1264816.9201 | 2749840.6454 | 1264807.378
91 | 2749691.2588 | 1264747.1042 | 2749720.322 | 1264742.7888
92 | 2749691.2588 | 1264747.1042 | 2749697.5742 | 1264764.2425
93 | 2749691.2588 | 1264747.1042 | 2749679.5698 | 1264748.7866
94 | 2749708.0114 | 1264792.566 | 2749697.5742 | 1264764.2425
95 | 2749665.5781 | 1264750.7467 | 2749672.2695 | 1264749.8374 | 2749679.5698 | 1264748.7866
96 | 2749711.6353 | 1264802.4 | 2749708.0114 | 1264792.566
97 | 2749665.5781 | 1264750.7467 | 2749664.0336 | 1264741.8208 | 2749663.3936 | 1264736.7936
98 | 2749665.5781 | 1264750.7467 | 2749668.2408 | 1264764.9061
99 | 2749782.3698 | 1264780.4989 | 2749787.7191 | 1264795.2998
100 | 2749787.7191 | 1264795.2998 | 2749788.8142 | 1264798.3298
101 | 2749788.8142 | 1264798.3298 | 2749794.4092 | 1264813.8106
102 | 2749711.6353 | 1264802.4 | 2749714.4558 | 1264810.054
103 | 2749668.2408 | 1264764.9061 | 2749657.5967 | 1264768.5483
104 | 2749668.2408 | 1264764.9061 | 2749679.3888 | 1264795.1967
105 | 2749657.5967 | 1264768.5483 | 2749641.8207 | 1264773.9465 | 2749639.421 | 1264775.4379
106 | 2749618.7737 | 1264788.1443 | 2749619.8009 | 1264799.4645
107 | 2749618.7737 | 1264788.1443 | 2749617.3987 | 1264788.8625
108 | 2749618.7737 | 1264788.1443 | 2749620.1025 | 1264787.4439 | 2749624.9577 | 1264784.4265
109 | 2749603.2365 | 1264794.3256 | 2749610.0612 | 1264792.6951 | 2749617.3987 | 1264788.8625
110 | 2749624.9577 | 1264784.4265 | 2749639.421 | 1264775.4379
111 | 2749626.7455 | 1264709.1286 | 2749621.742 | 1264709.789
112 | 2749621.742 | 1264709.789 | 2749615.8089 | 1264710.5721
113 | 2749615.3344 | 1264710.6348 | 2749615.8089 | 1264710.5721

## bus_geodata
| x | y | coords
0 | 2749874.1101 | 1264718.9331
1 | 2749874.109 | 1264718.2576
2 | 2749874.1326 | 1264733.0559
3 | 2749874.0907 | 1264706.7398
4 | 2749869.3689 | 1264732.8238
5 | 2749889.0277 | 1264734.0011
6 | 2749874.0682 | 1264692.6178
7 | 2749856.1317 | 1264732.1654
8 | 2749869.4398 | 1264745.0052
9 | 2749893.883 | 1264760.1157
10 | 2749900.9556 | 1264734.6884
11 | 2749874.0654 | 1264690.8425
12 | 2749856.2313 | 1264743.533
13 | 2749843.0585 | 1264731.5166
14 | 2749899.4399 | 1264777.3276
15 | 2749938.3619 | 1264736.8437
16 | 2749874.0644 | 1264690.1988
17 | 2749828.14 | 1264730.7762
18 | 2749825.0143 | 1264730.621
19 | 2749820.8374 | 1264730.4137
20 | 2749856.2382 | 1264744.3267
21 | 2749805.7261 | 1264729.7144
22 | 2749821.2696 | 1264743.9249
23 | 2749856.3038 | 1264751.8118
24 | 2749785.5792 | 1264728.782
25 | 2749822.1768 | 1264751.9735
26 | 2749766.1446 | 1264729.4049
27 | 2749829.2415 | 1264775.7012
28 | 2749766.2441 | 1264735.8806
29 | 2749760.269 | 1264725.7747
30 | 2749772.6727 | 1264753.6679
31 | 2749754.1972 | 1264737.7589
32 | 2749739.2031 | 1264713.8327
33 | 2749761.798 | 1264711.8967
34 | 2749776.1189 | 1264763.2033
35 | 2749736.2389 | 1264712.1524
36 | 2749761.4592 | 1264694.255
37 | 2749760.7297 | 1264656.2653
38 | 2749760.1069 | 1264623.69
39 | 2749740.0548 | 1264621.9582
40 | 2749726.4685 | 1264707.1668
41 | 2749738.1884 | 1264701.8788
42 | 2749738.6424 | 1264682.4407
43 | 2749738.822 | 1264674.7512
44 | 2749739.2623 | 1264655.8957
45 | 2749712.7683 | 1264699.0523
46 | 2749739.7349 | 1264635.6594
47 | 2749709.5168 | 1264697.1265
48 | 2749581.7215 | 1264662.7438
49 | 2749581.8219 | 1264661.7265
50 | 2749584.8191 | 1264640.5645
51 | 2749580.3819 | 1264675.1481
52 | 2749584.3575 | 1264619.9436
53 | 2749590.306 | 1264675.907
54 | 2749576.1622 | 1264755.2638
55 | 2749576.896 | 1264799.4183
56 | 2749637.2945 | 1264612.0468
57 | 2749676.5617 | 1264615.8341
58 | 2749635.0113 | 1264628.4933
59 | 2749628.0594 | 1264678.5689
60 | 2749634.8733 | 1264629.4876
61 | 2749629.9688 | 1264664.8153
62 | 2749630.9308 | 1264657.8855
63 | 2749632.2504 | 1264648.3807
64 | 2749632.2527 | 1264679.0088
65 | 2749656.3751 | 1264681.5663
66 | 2749633.4039 | 1264692.5137
67 | 2749659.9012 | 1264712.6545
68 | 2749669.8895 | 1264683.7577
69 | 2749633.4128 | 1264692.7271
70 | 2749723.4798 | 1264620.3595
71 | 2749808.469 | 1264628.124
72 | 2749831.4274 | 1264630.229
73 | 2749680.5832 | 1264685.8442
74 | 2749694.7911 | 1264689.7505
75 | 2749660.2374 | 1264714.9176
76 | 2749663.1904 | 1264735.1975
77 | 2749848.5545 | 1264631.7993
78 | 2749873.9752 | 1264634.13
79 | 2749874.0211 | 1264663.0289
80 | 2749874.0211 | 1264663.03
81 | 2749874.0223 | 1264663.7513
82 | 2749934.645 | 1264653.873
83 | 2749935.6846 | 1264677.0789
84 | 2749906.6859 | 1264799.772
85 | 2749904.4371 | 1264792.8062
86 | 2749834.2362 | 1264789.5752
87 | 2749840.6454 | 1264807.378
88 | 2749720.322 | 1264742.7888
89 | 2749691.2588 | 1264747.1042
90 | 2749697.5742 | 1264764.2425
91 | 2749679.5698 | 1264748.7866
92 | 2749708.0114 | 1264792.566
93 | 2749665.5781 | 1264750.7467
94 | 2749782.3698 | 1264780.4989
95 | 2749787.7191 | 1264795.2998
96 | 2749788.8142 | 1264798.3298
97 | 2749794.4092 | 1264813.8106
98 | 2749844.0806 | 1264816.9201
99 | 2749711.6353 | 1264802.4
100 | 2749663.3936 | 1264736.7936
101 | 2749668.2408 | 1264764.9061
102 | 2749714.4558 | 1264810.054
103 | 2749679.3888 | 1264795.1967
104 | 2749657.5967 | 1264768.5483
105 | 2749619.8009 | 1264799.4645
106 | 2749618.7737 | 1264788.1443
107 | 2749617.3987 | 1264788.8625
108 | 2749624.9577 | 1264784.4265
109 | 2749603.2365 | 1264794.3256
110 | 2749639.421 | 1264775.4379
111 | 2749626.7455 | 1264709.1286
112 | 2749621.742 | 1264709.789
113 | 2749615.8089 | 1264710.5721
114 | 2749615.3344 | 1264710.6348
115 | 2749760.269 | 1264725.7747

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1